## Read Me
SK-3X1 Rev 14 gas power campus: cable schedule and cable bill of materials
Conceptual, derived from the SK-3X1 3D model. Not engineered, not for construction or procurement.
How it was built
1. Every powered item of the model (BTM data-centre option excluded) is matched to an equipment class that gives its power circuits (voltage, typical rating, source bus) and its field devices (motors, MOVs, analog and discrete instruments, solenoids, thermocouples, RTDs; typical counts for the class). Each device has its own cable to its MCC or to a local junction box; junction boxes home-run on 24-pair / 12-triad / 25-conductor cables. Device-to-JB cables are grouped per JB (Sets = number of device cables). Ratings are typical unless the drawing states one.
2. Lengths follow the model's electrical routes (trays, duct banks, buried / surface cable, trenches) as a graph: shortest path source to load, plus drops and vertical transitions. 230 kV circuits, overhead conductors and the ground grid are measured directly from the model.
3. Sizes: ampacity at 125 % of full-load current (NEC 310.16 75 C Cu for 600 V; typical ICEA values for MV-105), 3 % voltage drop at 480 V, parallel sets above 500 kcmil (LV) / 1000 kcmil (MV).
4. Products are typical Southwire families for each application; confirm constructions, sizes and listings against current Southwire specifications.
5. 0 of 5695 runs could not follow a modelled route (Route type 'Estimated'): L-shaped length between the items plus 40 ft.
Inputs (blue, yellow cells; every length and quantity recalculates)
Routing slack (training, sag, cutting) | 10% | Source: typical industry allowance (assumption)
Termination allowance per run end (ft) | 10 | Source: typical (assumption)
BOM waste / cut allowance | 5% | Source: typical (assumption)
Sheets
Cable Schedule: one row per cable run (from / to, service, product, size, sets, length)
Cable BOM: totals per product and size, waste, order length, reels (SUMIFS on the schedule)
Accessories: terminations, glands, lugs, splices (from the schedule)
Summary: cable length by zone and voltage class
Load List: the equipment, assumed ratings and sources behind the power circuits
Excluded from the cable BOM (bus duct, by others)
RICE PCM to MOD-EH bus tie: 13.8 kV, ~6,300 A
MOD-EH to T-MOD-1 LV side: 13.8 kV, ~5,000 A
MOD-EH to T-MOD-2 LV side: 13.8 kV, ~5,000 A
Generator terminals to GSU / UAT / ET (isolated-phase bus): 21 kV, as modelled (IPB routes)
T-R4-1..4 secondaries to the ACC VFD lineups: 480 V, ~4,500 A each

## Audit
Check | Result | Count | Notes / examples
Every powered item has a power circuit (VFD lineups: bus duct; BESS blocks: per container) | PASS | 0
Every instrumented item has instrument cables | PASS | 0
No lump feeder where motors are fed individually (double count) | PASS | 0
Ampacity >= 125 % of full-load current (recomputed) | PASS | 0
480 V voltage drop <= 3 % (recomputed) | CHECK | 3 | EDG-1 480 V output to EMCC 3.1%; EDG-2 480 V output to EMCC 3.3%; Fuel-cell AC cabinet to MOD-LV 5.7%
Class I Div 2 loads on ARMOR-X / IS cable | PASS | 0
Runs that follow a modelled route | INFO | 5695 | 0 estimated (build-out bays D4-D6 and utilities without drawn trench / bank)
Copper runs > 3,000 ft | INFO | 114 | Control; Motor 1 of 6: control / local ; Motor 2 of 6: control / local ; Motor 3 of 6: control / local
Feeders with >= 6 parallel sets (bus-duct candidates) | INFO | 15 | EDG-1 480 V output to EMCC x13; EDG-2 480 V output to EMCC x13; Site / road lighting: 120 pole x120; Black-start genset output x10
Excluded as bus duct | INFO | 5 | RICE PCM to MOD-EH bus tie; MOD-EH to T-MOD-1 LV side; MOD-EH to T-MOD-2 LV side; Generator terminals to GSU / UAT / ET (isolated-phase bus); T-R4-1..4 secondaries to the ACC VFD lineups

## Cable Schedule
Cable No. | Zone | Area | Service / circuit | From (tag) | From (description) | To (tag) | To (description) | Class | Product | Product key | Conductors | Size (AWG/kcmil) | Sets | Cables / set | Voltage (V) | Load (kW) | Current (A) | Route type | Route (ft) | Drops + vertical (ft) | Run length (ft) | Total cable (ft) | MV term. kits | Glands / connectors | Notes | Cables (count)
A-L-0001 | A | Power block | Lighting, receptacles and small power branch circuits (allowance) | CEMS-1 | CEMS shelter, HRSG 1 | CEMS-1 | CEMS shelter, HRSG 1 | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | THHN¦1/C¦12 | 1/C | 12 | 1 | 1 | 277 |  |  | Conduit | 358 | 0 |  |  |  |  | allowance: 1.6 ft of conductor per ft2 of floor
A-L-0002 | A | Power block | Lighting, receptacles and small power branch circuits (allowance) | CEMS-2 | CEMS shelter, HRSG 2 | CEMS-2 | CEMS shelter, HRSG 2 | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | THHN¦1/C¦12 | 1/C | 12 | 1 | 1 | 277 |  |  | Conduit | 358 | 0 |  |  |  |  | allowance: 1.6 ft of conductor per ft2 of floor
A-L-0003 | A | Power block | Lighting, receptacles and small power branch circuits (allowance) | CEMS-3 | CEMS shelter, HRSG 3 | CEMS-3 | CEMS shelter, HRSG 3 | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | THHN¦1/C¦12 | 1/C | 12 | 1 | 1 | 277 |  |  | Conduit | 358 | 0 |  |  |  |  | allowance: 1.6 ft of conductor per ft2 of floor
A-L-0004 | A | Power block | Lighting, receptacles and small power branch circuits (allowance) | FH-1 | FH-1: GT inlet filter house on its own frame | FH-1 | FH-1: GT inlet filter house on its own frame | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | THHN¦1/C¦12 | 1/C | 12 | 1 | 1 | 277 |  |  | Conduit | 4973 | 0 |  |  |  |  | allowance: 1.6 ft of conductor per ft2 of floor
A-L-0005 | A | Power block | Lighting, receptacles and small power branch circuits (allowance) | FH-2 | FH-2: GT inlet filter house on its own frame | FH-2 | FH-2: GT inlet filter house on its own frame | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | THHN¦1/C¦12 | 1/C | 12 | 1 | 1 | 277 |  |  | Conduit | 4973 | 0 |  |  |  |  | allowance: 1.6 ft of conductor per ft2 of floor
A-L-0006 | A | Power block | Lighting, receptacles and small power branch circuits (allowance) | FH-3 | FH-3: GT inlet filter house on its own frame | FH-3 | FH-3: GT inlet filter house on its own frame | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | THHN¦1/C¦12 | 1/C | 12 | 1 | 1 | 277 |  |  | Conduit | 4973 | 0 |  |  |  |  | allowance: 1.6 ft of conductor per ft2 of floor
A-L-0007 | A | Power block | Lighting, receptacles and small power branch circuits (allowance) | R1 | R1: main electrical building (64 x 180 ft) | R1 | R1: main electrical building (64 x 180 ft) | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | THHN¦1/C¦12 | 1/C | 12 | 1 | 1 | 277 |  |  | Conduit | 18432 | 0 |  |  |  |  | allowance: 1.6 ft of conductor per ft2 of floor
A-L-0008 | A | Power block | Lighting, receptacles and small power branch circuits (allowance) | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | THHN¦1/C¦12 | 1/C | 12 | 1 | 1 | 277 |  |  | Conduit | 2048 | 0 |  |  |  |  | allowance: 1.6 ft of conductor per ft2 of floor
A-L-0009 | A | Power block | Lighting, receptacles and small power branch circuits (allowance) | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | THHN¦1/C¦12 | 1/C | 12 | 1 | 1 | 277 |  |  | Conduit | 2048 | 0 |  |  |  |  | allowance: 1.6 ft of conductor per ft2 of floor
A-L-0010 | A | Power block | Lighting, receptacles and small power branch circuits (allowance) | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | THHN¦1/C¦12 | 1/C | 12 | 1 | 1 | 277 |  |  | Conduit | 2048 | 0 |  |  |  |  | allowance: 1.6 ft of conductor per ft2 of floor
A-L-0011 | A | Power block | Lighting, receptacles and small power branch circuits (allowance) | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | THHN¦1/C¦12 | 1/C | 12 | 1 | 1 | 277 |  |  | Conduit | 4160 | 0 |  |  |  |  | allowance: 1.6 ft of conductor per ft2 of floor
A-C-0001 | A | Power block | Motor 1 of 3: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | AC-A/B/C | Air compressors AC-A/B/C | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 88 | 84
A-C-0002 | A | Power block | Motor 2 of 3: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | AC-A/B/C | Air compressors AC-A/B/C | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 88 | 84
A-C-0003 | A | Power block | Motor 3 of 3: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | AC-A/B/C | Air compressors AC-A/B/C | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 88 | 84
A-C-0004 | A | Power block | Motor 1 of 4: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | BFP-1 | BFP-1A/B: boiler feed pumps (13.8 kV DOL) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 481 | 84
A-C-0005 | A | Power block | Motor 2 of 4: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | BFP-1 | BFP-1A/B: boiler feed pumps (13.8 kV DOL) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 481 | 84
A-C-0006 | A | Power block | Motor 3 of 4: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | BFP-1 | BFP-1A/B: boiler feed pumps (13.8 kV DOL) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 481 | 84
A-C-0007 | A | Power block | Motor 4 of 4: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | BFP-1 | BFP-1A/B: boiler feed pumps (13.8 kV DOL) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 481 | 84
A-C-0008 | A | Power block | Motor 1 of 4: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | BFP-2 | BFP-2A/B: boiler feed pumps (13.8 kV DOL) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 479 | 84
A-C-0009 | A | Power block | Motor 2 of 4: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | BFP-2 | BFP-2A/B: boiler feed pumps (13.8 kV DOL) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 479 | 84
A-C-0010 | A | Power block | Motor 3 of 4: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | BFP-2 | BFP-2A/B: boiler feed pumps (13.8 kV DOL) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 479 | 84
A-C-0011 | A | Power block | Motor 4 of 4: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | BFP-2 | BFP-2A/B: boiler feed pumps (13.8 kV DOL) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 479 | 84
A-C-0012 | A | Power block | Motor 1 of 4: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | BFP-3 | BFP-3A/B: boiler feed pumps (13.8 kV DOL) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 481 | 84
A-C-0013 | A | Power block | Motor 2 of 4: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | BFP-3 | BFP-3A/B: boiler feed pumps (13.8 kV DOL) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 481 | 84
A-C-0014 | A | Power block | Motor 3 of 4: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | BFP-3 | BFP-3A/B: boiler feed pumps (13.8 kV DOL) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 481 | 84
A-C-0015 | A | Power block | Motor 4 of 4: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | BFP-3 | BFP-3A/B: boiler feed pumps (13.8 kV DOL) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 481 | 84
A-C-0016 | A | Power block | Motor 1 of 2: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | CEMS-1 | CEMS shelter, HRSG 1 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 277 | 97
A-C-0017 | A | Power block | Motor 2 of 2: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | CEMS-1 | CEMS shelter, HRSG 1 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 277 | 97
A-C-0018 | A | Power block | Motor 1 of 2: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | CEMS-2 | CEMS shelter, HRSG 2 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 273 | 93
A-C-0019 | A | Power block | Motor 2 of 2: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | CEMS-2 | CEMS shelter, HRSG 2 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 273 | 93
A-C-0020 | A | Power block | Motor 1 of 2: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | CEMS-3 | CEMS shelter, HRSG 3 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 277 | 97
A-C-0021 | A | Power block | Motor 2 of 2: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | CEMS-3 | CEMS shelter, HRSG 3 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 277 | 97
A-C-0022 | A | Power block | Motor 1 of 6: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | Chem feed | Chemical feed | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 258 | 35
A-C-0023 | A | Power block | Motor 2 of 6: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | Chem feed | Chemical feed | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 258 | 35
A-C-0024 | A | Power block | Motor 3 of 6: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | Chem feed | Chemical feed | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 258 | 35
A-C-0025 | A | Power block | Motor 4 of 6: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | Chem feed | Chemical feed | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 258 | 35
A-C-0026 | A | Power block | Motor 5 of 6: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | Chem feed | Chemical feed | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 258 | 35
A-C-0027 | A | Power block | Motor 6 of 6: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | Chem feed | Chemical feed | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 258 | 35
A-C-0028 | A | Power block | Control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HALL | Common turbine hall | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 1069 | 184
A-C-0029 | A | Power block | Motor 1 of 2: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | EHC-ST | EHC-ST: ST electro-hydraulic control power unit | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 67 | 89
A-C-0030 | A | Power block | Motor 2 of 2: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | EHC-ST | EHC-ST: ST electro-hydraulic control power unit | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 67 | 89
A-C-0031 | A | Power block | Solenoid to JB JB-EHC-ST-SOL01: 10 x 2/C (field cables) | EHC-ST | EHC-ST: ST electro-hydraulic control power unit | JB-EHC-ST-SOL01 | EHC-ST: ST electro-hydraulic control power unit | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0032 | A | Power block | Home run JB-EHC-ST-SOL01 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-EHC-ST-SOL01 | EHC-ST: ST electro-hydraulic control power unit | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 67 | 89
A-C-0033 | A | Power block | Control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | ET-1 | ET-1: excitation transformer (dry type, GTG-1 terminals) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 403 | 119
A-C-0034 | A | Power block | Control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | ET-1 | ET-1: excitation transformer (dry type, GTG-1 terminals) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 403 | 119
A-C-0035 | A | Power block | CT / VT | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | ET-1 | ET-1: excitation transformer (dry type, GTG-1 terminals) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 403 | 119
A-C-0036 | A | Power block | CT / VT | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | ET-1 | ET-1: excitation transformer (dry type, GTG-1 terminals) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 403 | 119
A-C-0037 | A | Power block | Control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | ET-2 | ET-2: excitation transformer (dry type, GTG-2 terminals) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 1277 | 209
A-C-0038 | A | Power block | Control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | ET-2 | ET-2: excitation transformer (dry type, GTG-2 terminals) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 1277 | 209
A-C-0039 | A | Power block | CT / VT | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | ET-2 | ET-2: excitation transformer (dry type, GTG-2 terminals) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 1277 | 209
A-C-0040 | A | Power block | CT / VT | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | ET-2 | ET-2: excitation transformer (dry type, GTG-2 terminals) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 1277 | 209
A-C-0041 | A | Power block | Control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | ET-3 | ET-3: excitation transformer (dry type, GTG-3 terminals) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1214 | 102
A-C-0042 | A | Power block | Control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | ET-3 | ET-3: excitation transformer (dry type, GTG-3 terminals) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 1214 | 102
A-C-0043 | A | Power block | CT / VT | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | ET-3 | ET-3: excitation transformer (dry type, GTG-3 terminals) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Duct bank | 1214 | 102
A-C-0044 | A | Power block | CT / VT | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | ET-3 | ET-3: excitation transformer (dry type, GTG-3 terminals) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Duct bank | 1214 | 102
A-C-0045 | A | Power block | Motor 1 of 2: control / local station | MCC-GT1 | R1 MCC-GT1 | FH-1 | FH-1: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 451 | 157
A-C-0046 | A | Power block | Motor 2 of 2: control / local station | MCC-GT1 | R1 MCC-GT1 | FH-1 | FH-1: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 451 | 157
A-C-0047 | A | Power block | Solenoid to JB JB-FH-1-SOL01: 10 x 2/C (field cables) | FH-1 | FH-1: GT inlet filter house on its own frame | JB-FH-1-SOL01 | FH-1: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 140 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0048 | A | Power block | Home run JB-FH-1-SOL01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-FH-1-SOL01 | FH-1: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 373 | 106
A-C-0049 | A | Power block | Solenoid to JB JB-FH-1-SOL02: 10 x 2/C (field cables) | FH-1 | FH-1: GT inlet filter house on its own frame | JB-FH-1-SOL02 | FH-1: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 140 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0050 | A | Power block | Home run JB-FH-1-SOL02 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-FH-1-SOL02 | FH-1: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 373 | 106
A-C-0051 | A | Power block | Solenoid to JB JB-FH-1-SOL03: 10 x 2/C (field cables) | FH-1 | FH-1: GT inlet filter house on its own frame | JB-FH-1-SOL03 | FH-1: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 140 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0052 | A | Power block | Home run JB-FH-1-SOL03 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-FH-1-SOL03 | FH-1: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 373 | 106
A-C-0053 | A | Power block | Solenoid to JB JB-FH-1-SOL04: 10 x 2/C (field cables) | FH-1 | FH-1: GT inlet filter house on its own frame | JB-FH-1-SOL04 | FH-1: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 140 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0054 | A | Power block | Home run JB-FH-1-SOL04 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-FH-1-SOL04 | FH-1: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 373 | 106
A-C-0055 | A | Power block | Solenoid to JB JB-FH-1-SOL05: 10 x 2/C (field cables) | FH-1 | FH-1: GT inlet filter house on its own frame | JB-FH-1-SOL05 | FH-1: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 140 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0056 | A | Power block | Home run JB-FH-1-SOL05 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-FH-1-SOL05 | FH-1: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 373 | 106
A-C-0057 | A | Power block | Solenoid to JB JB-FH-1-SOL06: 10 x 2/C (field cables) | FH-1 | FH-1: GT inlet filter house on its own frame | JB-FH-1-SOL06 | FH-1: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 140 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0058 | A | Power block | Home run JB-FH-1-SOL06 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-FH-1-SOL06 | FH-1: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 373 | 106
A-C-0059 | A | Power block | Motor 1 of 2: control / local station | MCC-GT2 | R1 MCC-GT2 | FH-2 | FH-2: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 631 | 137
A-C-0060 | A | Power block | Motor 2 of 2: control / local station | MCC-GT2 | R1 MCC-GT2 | FH-2 | FH-2: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 631 | 137
A-C-0061 | A | Power block | Solenoid to JB JB-FH-2-SOL01: 10 x 2/C (field cables) | FH-2 | FH-2: GT inlet filter house on its own frame | JB-FH-2-SOL01 | FH-2: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 140 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0062 | A | Power block | Home run JB-FH-2-SOL01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-FH-2-SOL01 | FH-2: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 1247 | 196
A-C-0063 | A | Power block | Solenoid to JB JB-FH-2-SOL02: 10 x 2/C (field cables) | FH-2 | FH-2: GT inlet filter house on its own frame | JB-FH-2-SOL02 | FH-2: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 140 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0064 | A | Power block | Home run JB-FH-2-SOL02 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-FH-2-SOL02 | FH-2: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 1247 | 196
A-C-0065 | A | Power block | Solenoid to JB JB-FH-2-SOL03: 10 x 2/C (field cables) | FH-2 | FH-2: GT inlet filter house on its own frame | JB-FH-2-SOL03 | FH-2: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 140 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0066 | A | Power block | Home run JB-FH-2-SOL03 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-FH-2-SOL03 | FH-2: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 1247 | 196
A-C-0067 | A | Power block | Solenoid to JB JB-FH-2-SOL04: 10 x 2/C (field cables) | FH-2 | FH-2: GT inlet filter house on its own frame | JB-FH-2-SOL04 | FH-2: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 140 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0068 | A | Power block | Home run JB-FH-2-SOL04 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-FH-2-SOL04 | FH-2: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 1247 | 196
A-C-0069 | A | Power block | Solenoid to JB JB-FH-2-SOL05: 10 x 2/C (field cables) | FH-2 | FH-2: GT inlet filter house on its own frame | JB-FH-2-SOL05 | FH-2: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 140 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0070 | A | Power block | Home run JB-FH-2-SOL05 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-FH-2-SOL05 | FH-2: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 1247 | 196
A-C-0071 | A | Power block | Solenoid to JB JB-FH-2-SOL06: 10 x 2/C (field cables) | FH-2 | FH-2: GT inlet filter house on its own frame | JB-FH-2-SOL06 | FH-2: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 140 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0072 | A | Power block | Home run JB-FH-2-SOL06 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-FH-2-SOL06 | FH-2: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 1247 | 196
A-C-0073 | A | Power block | Motor 1 of 2: control / local station | MCC-GT3 | R1 MCC-GT3 | FH-3 | FH-3: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 799 | 145
A-C-0074 | A | Power block | Motor 2 of 2: control / local station | MCC-GT3 | R1 MCC-GT3 | FH-3 | FH-3: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 799 | 145
A-C-0075 | A | Power block | Solenoid to JB JB-FH-3-SOL01: 10 x 2/C (field cables) | FH-3 | FH-3: GT inlet filter house on its own frame | JB-FH-3-SOL01 | FH-3: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 140 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0076 | A | Power block | Home run JB-FH-3-SOL01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-FH-3-SOL01 | FH-3: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 1193 | 96
A-C-0077 | A | Power block | Solenoid to JB JB-FH-3-SOL02: 10 x 2/C (field cables) | FH-3 | FH-3: GT inlet filter house on its own frame | JB-FH-3-SOL02 | FH-3: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 140 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0078 | A | Power block | Home run JB-FH-3-SOL02 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-FH-3-SOL02 | FH-3: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 1193 | 96
A-C-0079 | A | Power block | Solenoid to JB JB-FH-3-SOL03: 10 x 2/C (field cables) | FH-3 | FH-3: GT inlet filter house on its own frame | JB-FH-3-SOL03 | FH-3: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 140 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0080 | A | Power block | Home run JB-FH-3-SOL03 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-FH-3-SOL03 | FH-3: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 1193 | 96
A-C-0081 | A | Power block | Solenoid to JB JB-FH-3-SOL04: 10 x 2/C (field cables) | FH-3 | FH-3: GT inlet filter house on its own frame | JB-FH-3-SOL04 | FH-3: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 140 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0082 | A | Power block | Home run JB-FH-3-SOL04 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-FH-3-SOL04 | FH-3: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 1193 | 96
A-C-0083 | A | Power block | Solenoid to JB JB-FH-3-SOL05: 10 x 2/C (field cables) | FH-3 | FH-3: GT inlet filter house on its own frame | JB-FH-3-SOL05 | FH-3: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 140 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0084 | A | Power block | Home run JB-FH-3-SOL05 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-FH-3-SOL05 | FH-3: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 1193 | 96
A-C-0085 | A | Power block | Solenoid to JB JB-FH-3-SOL06: 10 x 2/C (field cables) | FH-3 | FH-3: GT inlet filter house on its own frame | JB-FH-3-SOL06 | FH-3: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 140 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0086 | A | Power block | Home run JB-FH-3-SOL06 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-FH-3-SOL06 | FH-3: GT inlet filter house on its own frame | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 1193 | 96
A-C-0087 | A | Power block | Solenoid to JB JB-FS-GT1-SOL01: 8 x 2/C (field cables) | FS-GT1 | FS-GT1: CO2 fire-suppression skid | JB-FS-GT1-SOL01 | FS-GT1: CO2 fire-suppression skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦2/C¦14 | 2/C | 14 | 8 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0088 | A | Power block | Home run JB-FS-GT1-SOL01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-FS-GT1-SOL01 | FS-GT1: CO2 fire-suppression skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 210 | 104
A-C-0089 | A | Power block | Solenoid to JB JB-FS-GT2-SOL01: 8 x 2/C (field cables) | FS-GT2 | FS-GT2: CO2 fire-suppression skid | JB-FS-GT2-SOL01 | FS-GT2: CO2 fire-suppression skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦2/C¦14 | 2/C | 14 | 8 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0090 | A | Power block | Home run JB-FS-GT2-SOL01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-FS-GT2-SOL01 | FS-GT2: CO2 fire-suppression skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 1102 | 198
A-C-0091 | A | Power block | Solenoid to JB JB-FS-GT3-SOL01: 8 x 2/C (field cables) | FS-GT3 | FS-GT3: CO2 fire-suppression skid | JB-FS-GT3-SOL01 | FS-GT3: CO2 fire-suppression skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦2/C¦14 | 2/C | 14 | 8 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0092 | A | Power block | Home run JB-FS-GT3-SOL01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-FS-GT3-SOL01 | FS-GT3: CO2 fire-suppression skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 908 | 238
A-C-0093 | A | Power block | Control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | GCB-1 | GCB-1: generator circuit breaker | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 373 | 118
A-C-0094 | A | Power block | Control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | GCB-1 | GCB-1: generator circuit breaker | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 373 | 118
A-C-0095 | A | Power block | Control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | GCB-1 | GCB-1: generator circuit breaker | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 373 | 118
A-C-0096 | A | Power block | CT / VT | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | GCB-1 | GCB-1: generator circuit breaker | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 373 | 118
A-C-0097 | A | Power block | CT / VT | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | GCB-1 | GCB-1: generator circuit breaker | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 373 | 118
A-C-0098 | A | Power block | CT / VT | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | GCB-1 | GCB-1: generator circuit breaker | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 373 | 118
A-C-0099 | A | Power block | CT / VT | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | GCB-1 | GCB-1: generator circuit breaker | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 373 | 118
A-C-0100 | A | Power block | Control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | GCB-2 | GCB-2: generator circuit breaker | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 1247 | 208
A-C-0101 | A | Power block | Control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | GCB-2 | GCB-2: generator circuit breaker | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 1247 | 208
A-C-0102 | A | Power block | Control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | GCB-2 | GCB-2: generator circuit breaker | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 1247 | 208
A-C-0103 | A | Power block | CT / VT | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | GCB-2 | GCB-2: generator circuit breaker | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 1247 | 208
A-C-0104 | A | Power block | CT / VT | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | GCB-2 | GCB-2: generator circuit breaker | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 1247 | 208
A-C-0105 | A | Power block | CT / VT | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | GCB-2 | GCB-2: generator circuit breaker | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 1247 | 208
A-C-0106 | A | Power block | CT / VT | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | GCB-2 | GCB-2: generator circuit breaker | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 1247 | 208
A-C-0107 | A | Power block | Control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | GCB-3 | GCB-3: generator circuit breaker | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 1193 | 97
A-C-0108 | A | Power block | Control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | GCB-3 | GCB-3: generator circuit breaker | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 1193 | 97
A-C-0109 | A | Power block | Control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | GCB-3 | GCB-3: generator circuit breaker | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 1193 | 97
A-C-0110 | A | Power block | CT / VT | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | GCB-3 | GCB-3: generator circuit breaker | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Duct bank | 1193 | 97
A-C-0111 | A | Power block | CT / VT | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | GCB-3 | GCB-3: generator circuit breaker | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Duct bank | 1193 | 97
A-C-0112 | A | Power block | CT / VT | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | GCB-3 | GCB-3: generator circuit breaker | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Duct bank | 1193 | 97
A-C-0113 | A | Power block | CT / VT | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | GCB-3 | GCB-3: generator circuit breaker | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Duct bank | 1193 | 97
A-C-0114 | A | Power block | Control | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | GCB-ST | GCB-ST | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 366 | 111
A-C-0115 | A | Power block | Control | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | GCB-ST | GCB-ST | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 366 | 111
A-C-0116 | A | Power block | Control | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | GCB-ST | GCB-ST | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 366 | 111
A-C-0117 | A | Power block | CT / VT | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | GCB-ST | GCB-ST | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 366 | 111
A-C-0118 | A | Power block | CT / VT | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | GCB-ST | GCB-ST | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 366 | 111
A-C-0119 | A | Power block | CT / VT | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | GCB-ST | GCB-ST | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 366 | 111
A-C-0120 | A | Power block | CT / VT | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | GCB-ST | GCB-ST | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 366 | 111
A-C-0121 | A | Power block | Solenoid to JB JB-GFM-1-SOL01: 6 x 2/C (field cables) | GFM-1 | GFM-1: GT1 gas fuel module (stop / control valves, final strainer) | JB-GFM-1-SOL01 | GFM-1: GT1 gas fuel module (stop / control valves, final strainer) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 6 | 1 |  |  |  | Tray / conduit | 70 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0122 | A | Power block | Home run JB-GFM-1-SOL01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GFM-1-SOL01 | GFM-1: GT1 gas fuel module (stop / control valves, final strainer) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 220 | 94
A-C-0123 | A | Power block | Solenoid to JB JB-GFM-2-SOL01: 6 x 2/C (field cables) | GFM-2 | GFM-2: GT2 gas fuel module (stop / control valves, final strainer) | JB-GFM-2-SOL01 | GFM-2: GT2 gas fuel module (stop / control valves, final strainer) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 6 | 1 |  |  |  | Tray / conduit | 70 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0124 | A | Power block | Home run JB-GFM-2-SOL01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GFM-2-SOL01 | GFM-2: GT2 gas fuel module (stop / control valves, final strainer) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 1124 | 188
A-C-0125 | A | Power block | Solenoid to JB JB-GFM-3-SOL01: 6 x 2/C (field cables) | GFM-3 | GFM-3: GT3 gas fuel module (stop / control valves, final strainer) | JB-GFM-3-SOL01 | GFM-3: GT3 gas fuel module (stop / control valves, final strainer) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 6 | 1 |  |  |  | Tray / conduit | 70 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0126 | A | Power block | Home run JB-GFM-3-SOL01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GFM-3-SOL01 | GFM-3: GT3 gas fuel module (stop / control valves, final strainer) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 896 | 212
A-C-0127 | A | Power block | Motor 1 of 2: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | GSC-ST | GSC-ST: gland-steam condenser and exhausters | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 72 | 139
A-C-0128 | A | Power block | Motor 2 of 2: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | GSC-ST | GSC-ST: gland-steam condenser and exhausters | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 72 | 139
A-C-0129 | A | Power block | Motor 1 of 6: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-1 firewall | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 416 | 181
A-C-0130 | A | Power block | Motor 2 of 6: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-1 firewall | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 416 | 181
A-C-0131 | A | Power block | Motor 3 of 6: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-1 firewall | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 416 | 181
A-C-0132 | A | Power block | Motor 4 of 6: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-1 firewall | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 416 | 181
A-C-0133 | A | Power block | Motor 5 of 6: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-1 firewall | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 416 | 181
A-C-0134 | A | Power block | Motor 6 of 6: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-1 firewall | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 416 | 181
A-C-0135 | A | Power block | Motor 1 of 6: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | GSU-1 | GSU-1: 21/230 kV generator step-up transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 419 | 179
A-C-0136 | A | Power block | Motor 2 of 6: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | GSU-1 | GSU-1: 21/230 kV generator step-up transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 419 | 179
A-C-0137 | A | Power block | Motor 3 of 6: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | GSU-1 | GSU-1: 21/230 kV generator step-up transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 419 | 179
A-C-0138 | A | Power block | Motor 4 of 6: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | GSU-1 | GSU-1: 21/230 kV generator step-up transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 419 | 179
A-C-0139 | A | Power block | Motor 5 of 6: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | GSU-1 | GSU-1: 21/230 kV generator step-up transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 419 | 179
A-C-0140 | A | Power block | Motor 6 of 6: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | GSU-1 | GSU-1: 21/230 kV generator step-up transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 419 | 179
A-C-0141 | A | Power block | Control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | GSU-1 | GSU-1: 21/230 kV generator step-up transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 419 | 179
A-C-0142 | A | Power block | Control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | GSU-1 | GSU-1: 21/230 kV generator step-up transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 419 | 179
A-C-0143 | A | Power block | CT / VT | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | GSU-1 | GSU-1: 21/230 kV generator step-up transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 419 | 179
A-C-0144 | A | Power block | CT / VT | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | GSU-1 | GSU-1: 21/230 kV generator step-up transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 419 | 179
A-C-0145 | A | Power block | Motor 1 of 6: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-2 firewall | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 1290 | 271
A-C-0146 | A | Power block | Motor 2 of 6: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-2 firewall | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 1290 | 271
A-C-0147 | A | Power block | Motor 3 of 6: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-2 firewall | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 1290 | 271
A-C-0148 | A | Power block | Motor 4 of 6: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-2 firewall | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 1290 | 271
A-C-0149 | A | Power block | Motor 5 of 6: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-2 firewall | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 1290 | 271
A-C-0150 | A | Power block | Motor 6 of 6: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-2 firewall | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 1290 | 271
A-C-0151 | A | Power block | Motor 1 of 6: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | GSU-2 | GSU-2: 21/230 kV generator step-up transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1423 | 113
A-C-0152 | A | Power block | Motor 2 of 6: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | GSU-2 | GSU-2: 21/230 kV generator step-up transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1423 | 113
A-C-0153 | A | Power block | Motor 3 of 6: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | GSU-2 | GSU-2: 21/230 kV generator step-up transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1423 | 113
A-C-0154 | A | Power block | Motor 4 of 6: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | GSU-2 | GSU-2: 21/230 kV generator step-up transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1423 | 113
A-C-0155 | A | Power block | Motor 5 of 6: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | GSU-2 | GSU-2: 21/230 kV generator step-up transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1423 | 113
A-C-0156 | A | Power block | Motor 6 of 6: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | GSU-2 | GSU-2: 21/230 kV generator step-up transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1423 | 113
A-C-0157 | A | Power block | Control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | GSU-2 | GSU-2: 21/230 kV generator step-up transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1423 | 113
A-C-0158 | A | Power block | Control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | GSU-2 | GSU-2: 21/230 kV generator step-up transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 1423 | 113
A-C-0159 | A | Power block | CT / VT | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | GSU-2 | GSU-2: 21/230 kV generator step-up transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Duct bank | 1423 | 113
A-C-0160 | A | Power block | CT / VT | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | GSU-2 | GSU-2: 21/230 kV generator step-up transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Duct bank | 1423 | 113
A-C-0161 | A | Power block | Motor 1 of 6: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-3 firewall | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1140 | 110
A-C-0162 | A | Power block | Motor 2 of 6: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-3 firewall | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1140 | 110
A-C-0163 | A | Power block | Motor 3 of 6: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-3 firewall | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1140 | 110
A-C-0164 | A | Power block | Motor 4 of 6: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-3 firewall | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1140 | 110
A-C-0165 | A | Power block | Motor 5 of 6: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-3 firewall | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1140 | 110
A-C-0166 | A | Power block | Motor 6 of 6: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-3 firewall | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1140 | 110
A-C-0167 | A | Power block | Motor 1 of 6: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | GSU-3 | GSU-3: 21/230 kV generator step-up transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1103 | 113
A-C-0168 | A | Power block | Motor 2 of 6: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | GSU-3 | GSU-3: 21/230 kV generator step-up transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1103 | 113
A-C-0169 | A | Power block | Motor 3 of 6: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | GSU-3 | GSU-3: 21/230 kV generator step-up transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1103 | 113
A-C-0170 | A | Power block | Motor 4 of 6: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | GSU-3 | GSU-3: 21/230 kV generator step-up transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1103 | 113
A-C-0171 | A | Power block | Motor 5 of 6: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | GSU-3 | GSU-3: 21/230 kV generator step-up transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1103 | 113
A-C-0172 | A | Power block | Motor 6 of 6: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | GSU-3 | GSU-3: 21/230 kV generator step-up transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1103 | 113
A-C-0173 | A | Power block | Control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | GSU-3 | GSU-3: 21/230 kV generator step-up transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1103 | 113
A-C-0174 | A | Power block | Control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | GSU-3 | GSU-3: 21/230 kV generator step-up transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 1103 | 113
A-C-0175 | A | Power block | CT / VT | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | GSU-3 | GSU-3: 21/230 kV generator step-up transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Duct bank | 1103 | 113
A-C-0176 | A | Power block | CT / VT | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | GSU-3 | GSU-3: 21/230 kV generator step-up transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Duct bank | 1103 | 113
A-C-0177 | A | Power block | Motor 1 of 6: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) |  | GSU-ST firewall | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 463 | 35
A-C-0178 | A | Power block | Motor 2 of 6: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) |  | GSU-ST firewall | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 463 | 35
A-C-0179 | A | Power block | Motor 3 of 6: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) |  | GSU-ST firewall | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 463 | 35
A-C-0180 | A | Power block | Motor 4 of 6: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) |  | GSU-ST firewall | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 463 | 35
A-C-0181 | A | Power block | Motor 5 of 6: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) |  | GSU-ST firewall | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 463 | 35
A-C-0182 | A | Power block | Motor 6 of 6: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) |  | GSU-ST firewall | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 463 | 35
A-C-0183 | A | Power block | Motor 1 of 6: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | GSU-ST | GSU-ST: 21/230 kV (one ST GSU, baseline) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 408 | 32
A-C-0184 | A | Power block | Motor 2 of 6: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | GSU-ST | GSU-ST: 21/230 kV (one ST GSU, baseline) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 408 | 32
A-C-0185 | A | Power block | Motor 3 of 6: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | GSU-ST | GSU-ST: 21/230 kV (one ST GSU, baseline) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 408 | 32
A-C-0186 | A | Power block | Motor 4 of 6: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | GSU-ST | GSU-ST: 21/230 kV (one ST GSU, baseline) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 408 | 32
A-C-0187 | A | Power block | Motor 5 of 6: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | GSU-ST | GSU-ST: 21/230 kV (one ST GSU, baseline) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 408 | 32
A-C-0188 | A | Power block | Motor 6 of 6: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | GSU-ST | GSU-ST: 21/230 kV (one ST GSU, baseline) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 408 | 32
A-C-0189 | A | Power block | Control | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | GSU-ST | GSU-ST: 21/230 kV (one ST GSU, baseline) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 408 | 32
A-C-0190 | A | Power block | Control | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | GSU-ST | GSU-ST: 21/230 kV (one ST GSU, baseline) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 408 | 32
A-C-0191 | A | Power block | CT / VT | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | GSU-ST | GSU-ST: 21/230 kV (one ST GSU, baseline) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Duct bank | 408 | 32
A-C-0192 | A | Power block | CT / VT | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | GSU-ST | GSU-ST: 21/230 kV (one ST GSU, baseline) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Duct bank | 408 | 32
A-C-0193 | A | Power block | Motor 1 of 12: control / local station | MCC-GT1 | R1 MCC-GT1 | GT1 aux | GT1 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 302 | 170
A-C-0194 | A | Power block | Motor 2 of 12: control / local station | MCC-GT1 | R1 MCC-GT1 | GT1 aux | GT1 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 302 | 170
A-C-0195 | A | Power block | Motor 3 of 12: control / local station | MCC-GT1 | R1 MCC-GT1 | GT1 aux | GT1 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 302 | 170
A-C-0196 | A | Power block | Motor 4 of 12: control / local station | MCC-GT1 | R1 MCC-GT1 | GT1 aux | GT1 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 302 | 170
A-C-0197 | A | Power block | Motor 5 of 12: control / local station | MCC-GT1 | R1 MCC-GT1 | GT1 aux | GT1 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 302 | 170
A-C-0198 | A | Power block | Motor 6 of 12: control / local station | MCC-GT1 | R1 MCC-GT1 | GT1 aux | GT1 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 302 | 170
A-C-0199 | A | Power block | Motor 7 of 12: control / local station | MCC-GT1 | R1 MCC-GT1 | GT1 aux | GT1 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 302 | 170
A-C-0200 | A | Power block | Motor 8 of 12: control / local station | MCC-GT1 | R1 MCC-GT1 | GT1 aux | GT1 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 302 | 170
A-C-0201 | A | Power block | Motor 9 of 12: control / local station | MCC-GT1 | R1 MCC-GT1 | GT1 aux | GT1 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 302 | 170
A-C-0202 | A | Power block | Motor 10 of 12: control / local station | MCC-GT1 | R1 MCC-GT1 | GT1 aux | GT1 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 302 | 170
A-C-0203 | A | Power block | Motor 11 of 12: control / local station | MCC-GT1 | R1 MCC-GT1 | GT1 aux | GT1 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 302 | 170
A-C-0204 | A | Power block | Motor 12 of 12: control / local station | MCC-GT1 | R1 MCC-GT1 | GT1 aux | GT1 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 302 | 170
A-C-0205 | A | Power block | Solenoid to JB JB-GT1 aux-SOL01: 10 x 2/C (field cables) | GT1 aux | GT1 aux: lube oil, hydraulics, enclosure fans | JB-GT1 aux-SOL01 | GT1 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 62 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0206 | A | Power block | Home run JB-GT1 aux-SOL01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT1 aux-SOL01 | GT1 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 224 | 119
A-C-0207 | A | Power block | Solenoid to JB JB-GT1-SOL01: 10 x 2/C (field cables) | GT1 | GT1: H-class gas turbine (60 Hz) | JB-GT1-SOL01 | GT1: H-class gas turbine (60 Hz) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0208 | A | Power block | Home run JB-GT1-SOL01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT1-SOL01 | GT1: H-class gas turbine (60 Hz) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 154 | 103
A-C-0209 | A | Power block | Solenoid to JB JB-GT1-SOL02: 10 x 2/C (field cables) | GT1 | GT1: H-class gas turbine (60 Hz) | JB-GT1-SOL02 | GT1: H-class gas turbine (60 Hz) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0210 | A | Power block | Home run JB-GT1-SOL02 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT1-SOL02 | GT1: H-class gas turbine (60 Hz) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 154 | 103
A-C-0211 | A | Power block | Solenoid to JB JB-GT1-SOL03: 10 x 2/C (field cables) | GT1 | GT1: H-class gas turbine (60 Hz) | JB-GT1-SOL03 | GT1: H-class gas turbine (60 Hz) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0212 | A | Power block | Home run JB-GT1-SOL03 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT1-SOL03 | GT1: H-class gas turbine (60 Hz) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 154 | 103
A-C-0213 | A | Power block | Motor 1 of 12: control / local station | MCC-GT2 | R1 MCC-GT2 | GT2 aux | GT2 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 482 | 150
A-C-0214 | A | Power block | Motor 2 of 12: control / local station | MCC-GT2 | R1 MCC-GT2 | GT2 aux | GT2 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 482 | 150
A-C-0215 | A | Power block | Motor 3 of 12: control / local station | MCC-GT2 | R1 MCC-GT2 | GT2 aux | GT2 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 482 | 150
A-C-0216 | A | Power block | Motor 4 of 12: control / local station | MCC-GT2 | R1 MCC-GT2 | GT2 aux | GT2 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 482 | 150
A-C-0217 | A | Power block | Motor 5 of 12: control / local station | MCC-GT2 | R1 MCC-GT2 | GT2 aux | GT2 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 482 | 150
A-C-0218 | A | Power block | Motor 6 of 12: control / local station | MCC-GT2 | R1 MCC-GT2 | GT2 aux | GT2 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 482 | 150
A-C-0219 | A | Power block | Motor 7 of 12: control / local station | MCC-GT2 | R1 MCC-GT2 | GT2 aux | GT2 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 482 | 150
A-C-0220 | A | Power block | Motor 8 of 12: control / local station | MCC-GT2 | R1 MCC-GT2 | GT2 aux | GT2 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 482 | 150
A-C-0221 | A | Power block | Motor 9 of 12: control / local station | MCC-GT2 | R1 MCC-GT2 | GT2 aux | GT2 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 482 | 150
A-C-0222 | A | Power block | Motor 10 of 12: control / local station | MCC-GT2 | R1 MCC-GT2 | GT2 aux | GT2 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 482 | 150
A-C-0223 | A | Power block | Motor 11 of 12: control / local station | MCC-GT2 | R1 MCC-GT2 | GT2 aux | GT2 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 482 | 150
A-C-0224 | A | Power block | Motor 12 of 12: control / local station | MCC-GT2 | R1 MCC-GT2 | GT2 aux | GT2 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 482 | 150
A-C-0225 | A | Power block | Solenoid to JB JB-GT2 aux-SOL01: 10 x 2/C (field cables) | GT2 aux | GT2 aux: lube oil, hydraulics, enclosure fans | JB-GT2 aux-SOL01 | GT2 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 62 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0226 | A | Power block | Home run JB-GT2 aux-SOL01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT2 aux-SOL01 | GT2 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 1116 | 213
A-C-0227 | A | Power block | Solenoid to JB JB-GT2-SOL01: 10 x 2/C (field cables) | GT2 | GT2: H-class gas turbine (60 Hz) | JB-GT2-SOL01 | GT2: H-class gas turbine (60 Hz) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0228 | A | Power block | Home run JB-GT2-SOL01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT2-SOL01 | GT2: H-class gas turbine (60 Hz) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 1046 | 197
A-C-0229 | A | Power block | Solenoid to JB JB-GT2-SOL02: 10 x 2/C (field cables) | GT2 | GT2: H-class gas turbine (60 Hz) | JB-GT2-SOL02 | GT2: H-class gas turbine (60 Hz) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0230 | A | Power block | Home run JB-GT2-SOL02 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT2-SOL02 | GT2: H-class gas turbine (60 Hz) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 1046 | 197
A-C-0231 | A | Power block | Solenoid to JB JB-GT2-SOL03: 10 x 2/C (field cables) | GT2 | GT2: H-class gas turbine (60 Hz) | JB-GT2-SOL03 | GT2: H-class gas turbine (60 Hz) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0232 | A | Power block | Home run JB-GT2-SOL03 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT2-SOL03 | GT2: H-class gas turbine (60 Hz) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 1046 | 197
A-C-0233 | A | Power block | Motor 1 of 12: control / local station | MCC-GT3 | R1 MCC-GT3 | GT3 aux | GT3 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 693 | 149
A-C-0234 | A | Power block | Motor 2 of 12: control / local station | MCC-GT3 | R1 MCC-GT3 | GT3 aux | GT3 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 693 | 149
A-C-0235 | A | Power block | Motor 3 of 12: control / local station | MCC-GT3 | R1 MCC-GT3 | GT3 aux | GT3 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 693 | 149
A-C-0236 | A | Power block | Motor 4 of 12: control / local station | MCC-GT3 | R1 MCC-GT3 | GT3 aux | GT3 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 693 | 149
A-C-0237 | A | Power block | Motor 5 of 12: control / local station | MCC-GT3 | R1 MCC-GT3 | GT3 aux | GT3 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 693 | 149
A-C-0238 | A | Power block | Motor 6 of 12: control / local station | MCC-GT3 | R1 MCC-GT3 | GT3 aux | GT3 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 693 | 149
A-C-0239 | A | Power block | Motor 7 of 12: control / local station | MCC-GT3 | R1 MCC-GT3 | GT3 aux | GT3 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 693 | 149
A-C-0240 | A | Power block | Motor 8 of 12: control / local station | MCC-GT3 | R1 MCC-GT3 | GT3 aux | GT3 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 693 | 149
A-C-0241 | A | Power block | Motor 9 of 12: control / local station | MCC-GT3 | R1 MCC-GT3 | GT3 aux | GT3 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 693 | 149
A-C-0242 | A | Power block | Motor 10 of 12: control / local station | MCC-GT3 | R1 MCC-GT3 | GT3 aux | GT3 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 693 | 149
A-C-0243 | A | Power block | Motor 11 of 12: control / local station | MCC-GT3 | R1 MCC-GT3 | GT3 aux | GT3 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 693 | 149
A-C-0244 | A | Power block | Motor 12 of 12: control / local station | MCC-GT3 | R1 MCC-GT3 | GT3 aux | GT3 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 693 | 149
A-C-0245 | A | Power block | Solenoid to JB JB-GT3 aux-SOL01: 10 x 2/C (field cables) | GT3 aux | GT3 aux: lube oil, hydraulics, enclosure fans | JB-GT3 aux-SOL01 | GT3 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 62 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0246 | A | Power block | Home run JB-GT3 aux-SOL01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT3 aux-SOL01 | GT3 aux: lube oil, hydraulics, enclosure fans | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 926 | 248
A-C-0247 | A | Power block | Solenoid to JB JB-GT3-SOL01: 10 x 2/C (field cables) | GT3 | GT3: H-class gas turbine (60 Hz) | JB-GT3-SOL01 | GT3: H-class gas turbine (60 Hz) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0248 | A | Power block | Home run JB-GT3-SOL01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT3-SOL01 | GT3: H-class gas turbine (60 Hz) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 986 | 249
A-C-0249 | A | Power block | Solenoid to JB JB-GT3-SOL02: 10 x 2/C (field cables) | GT3 | GT3: H-class gas turbine (60 Hz) | JB-GT3-SOL02 | GT3: H-class gas turbine (60 Hz) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0250 | A | Power block | Home run JB-GT3-SOL02 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT3-SOL02 | GT3: H-class gas turbine (60 Hz) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 986 | 249
A-C-0251 | A | Power block | Solenoid to JB JB-GT3-SOL03: 10 x 2/C (field cables) | GT3 | GT3: H-class gas turbine (60 Hz) | JB-GT3-SOL03 | GT3: H-class gas turbine (60 Hz) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0252 | A | Power block | Home run JB-GT3-SOL03 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT3-SOL03 | GT3: H-class gas turbine (60 Hz) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 986 | 249
A-C-0253 | A | Power block | Motor 1 of 4: control / local station | MCC-GT1 | R1 MCC-GT1 | GTG-1 | GTG-1: GT generator | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 445 | 178
A-C-0254 | A | Power block | Motor 2 of 4: control / local station | MCC-GT1 | R1 MCC-GT1 | GTG-1 | GTG-1: GT generator | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 445 | 178
A-C-0255 | A | Power block | Motor 3 of 4: control / local station | MCC-GT1 | R1 MCC-GT1 | GTG-1 | GTG-1: GT generator | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 445 | 178
A-C-0256 | A | Power block | Motor 4 of 4: control / local station | MCC-GT1 | R1 MCC-GT1 | GTG-1 | GTG-1: GT generator | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 445 | 178
A-C-0257 | A | Power block | Motor 1 of 4: control / local station | MCC-GT2 | R1 MCC-GT2 | GTG-2 | GTG-2: GT generator | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 625 | 158
A-C-0258 | A | Power block | Motor 2 of 4: control / local station | MCC-GT2 | R1 MCC-GT2 | GTG-2 | GTG-2: GT generator | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 625 | 158
A-C-0259 | A | Power block | Motor 3 of 4: control / local station | MCC-GT2 | R1 MCC-GT2 | GTG-2 | GTG-2: GT generator | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 625 | 158
A-C-0260 | A | Power block | Motor 4 of 4: control / local station | MCC-GT2 | R1 MCC-GT2 | GTG-2 | GTG-2: GT generator | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 625 | 158
A-C-0261 | A | Power block | Motor 1 of 4: control / local station | MCC-GT3 | R1 MCC-GT3 | GTG-3 | GTG-3: GT generator | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 793 | 166
A-C-0262 | A | Power block | Motor 2 of 4: control / local station | MCC-GT3 | R1 MCC-GT3 | GTG-3 | GTG-3: GT generator | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 793 | 166
A-C-0263 | A | Power block | Motor 3 of 4: control / local station | MCC-GT3 | R1 MCC-GT3 | GTG-3 | GTG-3: GT generator | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 793 | 166
A-C-0264 | A | Power block | Motor 4 of 4: control / local station | MCC-GT3 | R1 MCC-GT3 | GTG-3 | GTG-3: GT generator | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 793 | 166
A-C-0265 | A | Power block | Motor 1 of 4: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0266 | A | Power block | Motor 2 of 4: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0267 | A | Power block | Motor 3 of 4: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0268 | A | Power block | Motor 4 of 4: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0269 | A | Power block | MOV 1: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0270 | A | Power block | MOV 2: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0271 | A | Power block | MOV 3: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0272 | A | Power block | MOV 4: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0273 | A | Power block | MOV 5: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0274 | A | Power block | MOV 6: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0275 | A | Power block | MOV 7: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0276 | A | Power block | MOV 8: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0277 | A | Power block | MOV 9: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0278 | A | Power block | MOV 10: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0279 | A | Power block | MOV 11: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0280 | A | Power block | MOV 12: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0281 | A | Power block | MOV 13: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0282 | A | Power block | MOV 14: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0283 | A | Power block | MOV 15: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0284 | A | Power block | MOV 16: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0285 | A | Power block | MOV 17: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0286 | A | Power block | MOV 18: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0287 | A | Power block | MOV 19: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0288 | A | Power block | MOV 20: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0289 | A | Power block | MOV 21: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0290 | A | Power block | MOV 22: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0291 | A | Power block | MOV 23: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0292 | A | Power block | MOV 24: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0293 | A | Power block | MOV 25: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0294 | A | Power block | MOV 26: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0295 | A | Power block | MOV 27: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0296 | A | Power block | MOV 28: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0297 | A | Power block | MOV 29: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0298 | A | Power block | MOV 30: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0299 | A | Power block | MOV 31: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0300 | A | Power block | MOV 32: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0301 | A | Power block | MOV 33: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0302 | A | Power block | MOV 34: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0303 | A | Power block | MOV 35: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0304 | A | Power block | MOV 36: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0305 | A | Power block | MOV 37: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0306 | A | Power block | MOV 38: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0307 | A | Power block | MOV 39: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0308 | A | Power block | MOV 40: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0309 | A | Power block | MOV 41: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0310 | A | Power block | MOV 42: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0311 | A | Power block | MOV 43: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0312 | A | Power block | MOV 44: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0313 | A | Power block | MOV 45: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0314 | A | Power block | Solenoid to JB JB-HRSG-1-SOL01: 10 x 2/C (field cables) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | JB-HRSG-1-SOL01 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0315 | A | Power block | Home run JB-HRSG-1-SOL01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-1-SOL01 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0316 | A | Power block | Solenoid to JB JB-HRSG-1-SOL02: 10 x 2/C (field cables) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | JB-HRSG-1-SOL02 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0317 | A | Power block | Home run JB-HRSG-1-SOL02 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-1-SOL02 | HRSG 1 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0318 | A | Power block | MOV 1: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 1 blowdown tank (continuous / intermittent) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 38 | 86
A-C-0319 | A | Power block | MOV 2: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 1 blowdown tank (continuous / intermittent) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 38 | 86
A-C-0320 | A | Power block | MOV 3: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 1 blowdown tank (continuous / intermittent) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 38 | 86
A-C-0321 | A | Power block | MOV 4: control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 1 blowdown tank (continuous / intermittent) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 38 | 86
A-C-0322 | A | Power block | Motor 1 of 6: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 1 chemical feed skid (phosphate / amine) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 404 | 108
A-C-0323 | A | Power block | Motor 2 of 6: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 1 chemical feed skid (phosphate / amine) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 404 | 108
A-C-0324 | A | Power block | Motor 3 of 6: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 1 chemical feed skid (phosphate / amine) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 404 | 108
A-C-0325 | A | Power block | Motor 4 of 6: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 1 chemical feed skid (phosphate / amine) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 404 | 108
A-C-0326 | A | Power block | Motor 5 of 6: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 1 chemical feed skid (phosphate / amine) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 404 | 108
A-C-0327 | A | Power block | Motor 6 of 6: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 1 chemical feed skid (phosphate / amine) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 404 | 108
A-C-0328 | A | Power block | Motor 1 of 4: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0329 | A | Power block | Motor 2 of 4: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0330 | A | Power block | Motor 3 of 4: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0331 | A | Power block | Motor 4 of 4: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0332 | A | Power block | MOV 1: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0333 | A | Power block | MOV 2: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0334 | A | Power block | MOV 3: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0335 | A | Power block | MOV 4: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0336 | A | Power block | MOV 5: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0337 | A | Power block | MOV 6: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0338 | A | Power block | MOV 7: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0339 | A | Power block | MOV 8: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0340 | A | Power block | MOV 9: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0341 | A | Power block | MOV 10: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0342 | A | Power block | MOV 11: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0343 | A | Power block | MOV 12: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0344 | A | Power block | MOV 13: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0345 | A | Power block | MOV 14: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0346 | A | Power block | MOV 15: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0347 | A | Power block | MOV 16: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0348 | A | Power block | MOV 17: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0349 | A | Power block | MOV 18: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0350 | A | Power block | MOV 19: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0351 | A | Power block | MOV 20: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0352 | A | Power block | MOV 21: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0353 | A | Power block | MOV 22: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0354 | A | Power block | MOV 23: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0355 | A | Power block | MOV 24: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0356 | A | Power block | MOV 25: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0357 | A | Power block | MOV 26: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0358 | A | Power block | MOV 27: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0359 | A | Power block | MOV 28: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0360 | A | Power block | MOV 29: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0361 | A | Power block | MOV 30: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0362 | A | Power block | MOV 31: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0363 | A | Power block | MOV 32: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0364 | A | Power block | MOV 33: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0365 | A | Power block | MOV 34: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0366 | A | Power block | MOV 35: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0367 | A | Power block | MOV 36: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0368 | A | Power block | MOV 37: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0369 | A | Power block | MOV 38: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0370 | A | Power block | MOV 39: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0371 | A | Power block | MOV 40: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0372 | A | Power block | MOV 41: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0373 | A | Power block | MOV 42: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0374 | A | Power block | MOV 43: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0375 | A | Power block | MOV 44: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0376 | A | Power block | MOV 45: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0377 | A | Power block | Solenoid to JB JB-HRSG-2-SOL01: 10 x 2/C (field cables) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | JB-HRSG-2-SOL01 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0378 | A | Power block | Home run JB-HRSG-2-SOL01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-2-SOL01 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0379 | A | Power block | Solenoid to JB JB-HRSG-2-SOL02: 10 x 2/C (field cables) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | JB-HRSG-2-SOL02 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0380 | A | Power block | Home run JB-HRSG-2-SOL02 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-2-SOL02 | HRSG 2 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 53 | 96
A-C-0381 | A | Power block | MOV 1: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 2 blowdown tank (continuous / intermittent) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 38 | 86
A-C-0382 | A | Power block | MOV 2: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 2 blowdown tank (continuous / intermittent) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 38 | 86
A-C-0383 | A | Power block | MOV 3: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 2 blowdown tank (continuous / intermittent) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 38 | 86
A-C-0384 | A | Power block | MOV 4: control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 2 blowdown tank (continuous / intermittent) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 38 | 86
A-C-0385 | A | Power block | Motor 1 of 6: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 2 chemical feed skid (phosphate / amine) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 404 | 108
A-C-0386 | A | Power block | Motor 2 of 6: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 2 chemical feed skid (phosphate / amine) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 404 | 108
A-C-0387 | A | Power block | Motor 3 of 6: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 2 chemical feed skid (phosphate / amine) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 404 | 108
A-C-0388 | A | Power block | Motor 4 of 6: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 2 chemical feed skid (phosphate / amine) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 404 | 108
A-C-0389 | A | Power block | Motor 5 of 6: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 2 chemical feed skid (phosphate / amine) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 404 | 108
A-C-0390 | A | Power block | Motor 6 of 6: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 2 chemical feed skid (phosphate / amine) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 404 | 108
A-C-0391 | A | Power block | Motor 1 of 4: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0392 | A | Power block | Motor 2 of 4: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0393 | A | Power block | Motor 3 of 4: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0394 | A | Power block | Motor 4 of 4: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0395 | A | Power block | MOV 1: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0396 | A | Power block | MOV 2: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0397 | A | Power block | MOV 3: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0398 | A | Power block | MOV 4: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0399 | A | Power block | MOV 5: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0400 | A | Power block | MOV 6: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0401 | A | Power block | MOV 7: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0402 | A | Power block | MOV 8: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0403 | A | Power block | MOV 9: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0404 | A | Power block | MOV 10: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0405 | A | Power block | MOV 11: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0406 | A | Power block | MOV 12: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0407 | A | Power block | MOV 13: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0408 | A | Power block | MOV 14: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0409 | A | Power block | MOV 15: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0410 | A | Power block | MOV 16: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0411 | A | Power block | MOV 17: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0412 | A | Power block | MOV 18: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0413 | A | Power block | MOV 19: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0414 | A | Power block | MOV 20: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0415 | A | Power block | MOV 21: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0416 | A | Power block | MOV 22: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0417 | A | Power block | MOV 23: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0418 | A | Power block | MOV 24: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0419 | A | Power block | MOV 25: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0420 | A | Power block | MOV 26: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0421 | A | Power block | MOV 27: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0422 | A | Power block | MOV 28: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0423 | A | Power block | MOV 29: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0424 | A | Power block | MOV 30: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0425 | A | Power block | MOV 31: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0426 | A | Power block | MOV 32: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0427 | A | Power block | MOV 33: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0428 | A | Power block | MOV 34: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0429 | A | Power block | MOV 35: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0430 | A | Power block | MOV 36: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0431 | A | Power block | MOV 37: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0432 | A | Power block | MOV 38: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0433 | A | Power block | MOV 39: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0434 | A | Power block | MOV 40: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0435 | A | Power block | MOV 41: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0436 | A | Power block | MOV 42: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0437 | A | Power block | MOV 43: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0438 | A | Power block | MOV 44: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0439 | A | Power block | MOV 45: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0440 | A | Power block | Solenoid to JB JB-HRSG-3-SOL01: 10 x 2/C (field cables) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | JB-HRSG-3-SOL01 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0441 | A | Power block | Home run JB-HRSG-3-SOL01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-3-SOL01 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0442 | A | Power block | Solenoid to JB JB-HRSG-3-SOL02: 10 x 2/C (field cables) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | JB-HRSG-3-SOL02 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0443 | A | Power block | Home run JB-HRSG-3-SOL02 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-3-SOL02 | HRSG 3 + SCR (3P reheat, horizontal) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 87
A-C-0444 | A | Power block | MOV 1: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 3 blowdown tank (continuous / intermittent) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 38 | 86
A-C-0445 | A | Power block | MOV 2: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 3 blowdown tank (continuous / intermittent) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 38 | 86
A-C-0446 | A | Power block | MOV 3: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 3 blowdown tank (continuous / intermittent) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 38 | 86
A-C-0447 | A | Power block | MOV 4: control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 3 blowdown tank (continuous / intermittent) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 38 | 86
A-C-0448 | A | Power block | Motor 1 of 6: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 3 chemical feed skid (phosphate / amine) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 404 | 108
A-C-0449 | A | Power block | Motor 2 of 6: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 3 chemical feed skid (phosphate / amine) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 404 | 108
A-C-0450 | A | Power block | Motor 3 of 6: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 3 chemical feed skid (phosphate / amine) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 404 | 108
A-C-0451 | A | Power block | Motor 4 of 6: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 3 chemical feed skid (phosphate / amine) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 404 | 108
A-C-0452 | A | Power block | Motor 5 of 6: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 3 chemical feed skid (phosphate / amine) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 404 | 108
A-C-0453 | A | Power block | Motor 6 of 6: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 3 chemical feed skid (phosphate / amine) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 404 | 108
A-C-0454 | A | Power block | Control | R1 | R1: main electrical building (64 x 180 ft) | HTP-1 | HTP-1: heat-trace panel (rack) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 829 | 218
A-C-0455 | A | Power block | Motor 1 of 6: control / local station | LC-480-B | R1 LC-480-B (480 V switchgear) | LCT-A | LCT-A: 13.8/0.48 kV load-centre transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 51 | 41
A-C-0456 | A | Power block | Motor 2 of 6: control / local station | LC-480-B | R1 LC-480-B (480 V switchgear) | LCT-A | LCT-A: 13.8/0.48 kV load-centre transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 51 | 41
A-C-0457 | A | Power block | Motor 3 of 6: control / local station | LC-480-B | R1 LC-480-B (480 V switchgear) | LCT-A | LCT-A: 13.8/0.48 kV load-centre transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 51 | 41
A-C-0458 | A | Power block | Motor 4 of 6: control / local station | LC-480-B | R1 LC-480-B (480 V switchgear) | LCT-A | LCT-A: 13.8/0.48 kV load-centre transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 51 | 41
A-C-0459 | A | Power block | Motor 5 of 6: control / local station | LC-480-B | R1 LC-480-B (480 V switchgear) | LCT-A | LCT-A: 13.8/0.48 kV load-centre transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 51 | 41
A-C-0460 | A | Power block | Motor 6 of 6: control / local station | LC-480-B | R1 LC-480-B (480 V switchgear) | LCT-A | LCT-A: 13.8/0.48 kV load-centre transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 51 | 41
A-C-0461 | A | Power block | Control | R1 | R1: main electrical building (64 x 180 ft) | LCT-A | LCT-A: 13.8/0.48 kV load-centre transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 718 | 124
A-C-0462 | A | Power block | Control | R1 | R1: main electrical building (64 x 180 ft) | LCT-A | LCT-A: 13.8/0.48 kV load-centre transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 718 | 124
A-C-0463 | A | Power block | CT / VT | R1 | R1: main electrical building (64 x 180 ft) | LCT-A | LCT-A: 13.8/0.48 kV load-centre transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 718 | 124
A-C-0464 | A | Power block | CT / VT | R1 | R1: main electrical building (64 x 180 ft) | LCT-A | LCT-A: 13.8/0.48 kV load-centre transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 718 | 124
A-C-0465 | A | Power block | Motor 1 of 6: control / local station | LC-480-B | R1 LC-480-B (480 V switchgear) | LCT-B | LCT-B: 13.8/0.48 kV load-centre transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 51 | 63
A-C-0466 | A | Power block | Motor 2 of 6: control / local station | LC-480-B | R1 LC-480-B (480 V switchgear) | LCT-B | LCT-B: 13.8/0.48 kV load-centre transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 51 | 63
A-C-0467 | A | Power block | Motor 3 of 6: control / local station | LC-480-B | R1 LC-480-B (480 V switchgear) | LCT-B | LCT-B: 13.8/0.48 kV load-centre transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 51 | 63
A-C-0468 | A | Power block | Motor 4 of 6: control / local station | LC-480-B | R1 LC-480-B (480 V switchgear) | LCT-B | LCT-B: 13.8/0.48 kV load-centre transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 51 | 63
A-C-0469 | A | Power block | Motor 5 of 6: control / local station | LC-480-B | R1 LC-480-B (480 V switchgear) | LCT-B | LCT-B: 13.8/0.48 kV load-centre transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 51 | 63
A-C-0470 | A | Power block | Motor 6 of 6: control / local station | LC-480-B | R1 LC-480-B (480 V switchgear) | LCT-B | LCT-B: 13.8/0.48 kV load-centre transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 51 | 63
A-C-0471 | A | Power block | Control | R1 | R1: main electrical building (64 x 180 ft) | LCT-B | LCT-B: 13.8/0.48 kV load-centre transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 718 | 146
A-C-0472 | A | Power block | Control | R1 | R1: main electrical building (64 x 180 ft) | LCT-B | LCT-B: 13.8/0.48 kV load-centre transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 718 | 146
A-C-0473 | A | Power block | CT / VT | R1 | R1: main electrical building (64 x 180 ft) | LCT-B | LCT-B: 13.8/0.48 kV load-centre transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 718 | 146
A-C-0474 | A | Power block | CT / VT | R1 | R1: main electrical building (64 x 180 ft) | LCT-B | LCT-B: 13.8/0.48 kV load-centre transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 718 | 146
A-C-0475 | A | Power block | Control | R1 | R1: main electrical building (64 x 180 ft) | TX-LCI-1 | R1 TX-LCI-1 dry-type input transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 73
A-C-0476 | A | Power block | Control | R1 | R1: main electrical building (64 x 180 ft) | TX-LCI-1 | R1 TX-LCI-1 dry-type input transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 73
A-C-0477 | A | Power block | CT / VT | R1 | R1: main electrical building (64 x 180 ft) | TX-LCI-1 | R1 TX-LCI-1 dry-type input transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 0 | 73
A-C-0478 | A | Power block | CT / VT | R1 | R1: main electrical building (64 x 180 ft) | TX-LCI-1 | R1 TX-LCI-1 dry-type input transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 0 | 73
A-C-0479 | A | Power block | Control | R1 | R1: main electrical building (64 x 180 ft) | TX-LCI-2 | R1 TX-LCI-2 dry-type input transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 109
A-C-0480 | A | Power block | Control | R1 | R1: main electrical building (64 x 180 ft) | TX-LCI-2 | R1 TX-LCI-2 dry-type input transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 109
A-C-0481 | A | Power block | CT / VT | R1 | R1: main electrical building (64 x 180 ft) | TX-LCI-2 | R1 TX-LCI-2 dry-type input transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 0 | 109
A-C-0482 | A | Power block | CT / VT | R1 | R1: main electrical building (64 x 180 ft) | TX-LCI-2 | R1 TX-LCI-2 dry-type input transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 0 | 109
A-C-0483 | A | Power block | Control | R1 | R1: main electrical building (64 x 180 ft) | TX-LCI-3 | R1 TX-LCI-3 dry-type input transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 667 | 144
A-C-0484 | A | Power block | Control | R1 | R1: main electrical building (64 x 180 ft) | TX-LCI-3 | R1 TX-LCI-3 dry-type input transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 667 | 144
A-C-0485 | A | Power block | CT / VT | R1 | R1: main electrical building (64 x 180 ft) | TX-LCI-3 | R1 TX-LCI-3 dry-type input transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 667 | 144
A-C-0486 | A | Power block | CT / VT | R1 | R1: main electrical building (64 x 180 ft) | TX-LCI-3 | R1 TX-LCI-3 dry-type input transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 667 | 144
A-C-0487 | A | Power block | Control | R1 | R1: main electrical building (64 x 180 ft) | R1 | R1: main electrical building (64 x 180 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 32
A-C-0488 | A | Power block | Control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 72
A-C-0489 | A | Power block | Control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 72
A-C-0490 | A | Power block | Control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 72
A-C-0491 | A | Power block | Control | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 32
A-C-0492 | A | Power block | Motor 1 of 2: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | SCRB-1 | SCRB-1A/B: SCR dilution-air blowers | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 404 | 72
A-C-0493 | A | Power block | Motor 2 of 2: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | SCRB-1 | SCRB-1A/B: SCR dilution-air blowers | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 404 | 72
A-C-0494 | A | Power block | Motor 1 of 2: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | SCRB-2 | SCRB-2A/B: SCR dilution-air blowers | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 404 | 72
A-C-0495 | A | Power block | Motor 2 of 2: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | SCRB-2 | SCRB-2A/B: SCR dilution-air blowers | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 404 | 72
A-C-0496 | A | Power block | Motor 1 of 2: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | SCRB-3 | SCRB-3A/B: SCR dilution-air blowers | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 404 | 72
A-C-0497 | A | Power block | Motor 2 of 2: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | SCRB-3 | SCRB-3A/B: SCR dilution-air blowers | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 404 | 72
A-C-0498 | A | Power block | Control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | SFC-1 | SFC-1: GT1 static starter (LCI) and isolation transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 359 | 147
A-C-0499 | A | Power block | Control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | SFC-1 | SFC-1: GT1 static starter (LCI) and isolation transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 359 | 147
A-C-0500 | A | Power block | CT / VT | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | SFC-1 | SFC-1: GT1 static starter (LCI) and isolation transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 359 | 147
A-C-0501 | A | Power block | CT / VT | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | SFC-1 | SFC-1: GT1 static starter (LCI) and isolation transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 359 | 147
A-C-0502 | A | Power block | Control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | SFC-2 | SFC-2: GT2 static starter (LCI) and isolation transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 1233 | 237
A-C-0503 | A | Power block | Control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | SFC-2 | SFC-2: GT2 static starter (LCI) and isolation transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 1233 | 237
A-C-0504 | A | Power block | CT / VT | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | SFC-2 | SFC-2: GT2 static starter (LCI) and isolation transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 1233 | 237
A-C-0505 | A | Power block | CT / VT | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | SFC-2 | SFC-2: GT2 static starter (LCI) and isolation transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 1233 | 237
A-C-0506 | A | Power block | Control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | SFC-3 | SFC-3: GT3 static starter (LCI) and isolation transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 987 | 184
A-C-0507 | A | Power block | Control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | SFC-3 | SFC-3: GT3 static starter (LCI) and isolation transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 987 | 184
A-C-0508 | A | Power block | CT / VT | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | SFC-3 | SFC-3: GT3 static starter (LCI) and isolation transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 987 | 184
A-C-0509 | A | Power block | CT / VT | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | SFC-3 | SFC-3: GT3 static starter (LCI) and isolation transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 987 | 184
A-C-0510 | A | Power block | Motor 1 of 3: control / local station | MCC-GT1 | R1 MCC-GT1 | SOS-1 | SOS-1: GTG-1 seal-oil and H2 / CO2 gas-control skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 481 | 189
A-C-0511 | A | Power block | Motor 2 of 3: control / local station | MCC-GT1 | R1 MCC-GT1 | SOS-1 | SOS-1: GTG-1 seal-oil and H2 / CO2 gas-control skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 481 | 189
A-C-0512 | A | Power block | Motor 3 of 3: control / local station | MCC-GT1 | R1 MCC-GT1 | SOS-1 | SOS-1: GTG-1 seal-oil and H2 / CO2 gas-control skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 481 | 189
A-C-0513 | A | Power block | Solenoid to JB JB-SOS-1-SOL01: 4 x 2/C (field cables) | SOS-1 | SOS-1: GTG-1 seal-oil and H2 / CO2 gas-control skid | JB-SOS-1-SOL01 | SOS-1: GTG-1 seal-oil and H2 / CO2 gas-control skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 4 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0514 | A | Power block | Home run JB-SOS-1-SOL01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-SOS-1-SOL01 | SOS-1: GTG-1 seal-oil and H2 / CO2 gas-control skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 403 | 138
A-C-0515 | A | Power block | Motor 1 of 3: control / local station | MCC-GT2 | R1 MCC-GT2 | SOS-2 | SOS-2: GTG-2 seal-oil and H2 / CO2 gas-control skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 661 | 169
A-C-0516 | A | Power block | Motor 2 of 3: control / local station | MCC-GT2 | R1 MCC-GT2 | SOS-2 | SOS-2: GTG-2 seal-oil and H2 / CO2 gas-control skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 661 | 169
A-C-0517 | A | Power block | Motor 3 of 3: control / local station | MCC-GT2 | R1 MCC-GT2 | SOS-2 | SOS-2: GTG-2 seal-oil and H2 / CO2 gas-control skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 661 | 169
A-C-0518 | A | Power block | Solenoid to JB JB-SOS-2-SOL01: 4 x 2/C (field cables) | SOS-2 | SOS-2: GTG-2 seal-oil and H2 / CO2 gas-control skid | JB-SOS-2-SOL01 | SOS-2: GTG-2 seal-oil and H2 / CO2 gas-control skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 4 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0519 | A | Power block | Home run JB-SOS-2-SOL01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-SOS-2-SOL01 | SOS-2: GTG-2 seal-oil and H2 / CO2 gas-control skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 1277 | 228
A-C-0520 | A | Power block | Motor 1 of 3: control / local station | MCC-GT3 | R1 MCC-GT3 | SOS-3 | SOS-3: GTG-3 seal-oil and H2 / CO2 gas-control skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 829 | 177
A-C-0521 | A | Power block | Motor 2 of 3: control / local station | MCC-GT3 | R1 MCC-GT3 | SOS-3 | SOS-3: GTG-3 seal-oil and H2 / CO2 gas-control skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 829 | 177
A-C-0522 | A | Power block | Motor 3 of 3: control / local station | MCC-GT3 | R1 MCC-GT3 | SOS-3 | SOS-3: GTG-3 seal-oil and H2 / CO2 gas-control skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 829 | 177
A-C-0523 | A | Power block | Solenoid to JB JB-SOS-3-SOL01: 4 x 2/C (field cables) | SOS-3 | SOS-3: GTG-3 seal-oil and H2 / CO2 gas-control skid | JB-SOS-3-SOL01 | SOS-3: GTG-3 seal-oil and H2 / CO2 gas-control skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 4 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0524 | A | Power block | Home run JB-SOS-3-SOL01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-SOS-3-SOL01 | SOS-3: GTG-3 seal-oil and H2 / CO2 gas-control skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 1214 | 126
A-C-0525 | A | Power block | Motor 1 of 10: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST aux | ST aux: lube oil, turning gear, EHC | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 67 | 84
A-C-0526 | A | Power block | Motor 2 of 10: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST aux | ST aux: lube oil, turning gear, EHC | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 67 | 84
A-C-0527 | A | Power block | Motor 3 of 10: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST aux | ST aux: lube oil, turning gear, EHC | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 67 | 84
A-C-0528 | A | Power block | Motor 4 of 10: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST aux | ST aux: lube oil, turning gear, EHC | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 67 | 84
A-C-0529 | A | Power block | Motor 5 of 10: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST aux | ST aux: lube oil, turning gear, EHC | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 67 | 84
A-C-0530 | A | Power block | Motor 6 of 10: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST aux | ST aux: lube oil, turning gear, EHC | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 67 | 84
A-C-0531 | A | Power block | Motor 7 of 10: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST aux | ST aux: lube oil, turning gear, EHC | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 67 | 84
A-C-0532 | A | Power block | Motor 8 of 10: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST aux | ST aux: lube oil, turning gear, EHC | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 67 | 84
A-C-0533 | A | Power block | Motor 9 of 10: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST aux | ST aux: lube oil, turning gear, EHC | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 67 | 84
A-C-0534 | A | Power block | Motor 10 of 10: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST aux | ST aux: lube oil, turning gear, EHC | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 67 | 84
A-C-0535 | A | Power block | MOV 1: control | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-C-0536 | A | Power block | MOV 2: control | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-C-0537 | A | Power block | MOV 3: control | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-C-0538 | A | Power block | MOV 4: control | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-C-0539 | A | Power block | MOV 5: control | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-C-0540 | A | Power block | MOV 6: control | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-C-0541 | A | Power block | MOV 7: control | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-C-0542 | A | Power block | MOV 8: control | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-C-0543 | A | Power block | MOV 9: control | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-C-0544 | A | Power block | MOV 10: control | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-C-0545 | A | Power block | MOV 11: control | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-C-0546 | A | Power block | MOV 12: control | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-C-0547 | A | Power block | MOV 13: control | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-C-0548 | A | Power block | MOV 14: control | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-C-0549 | A | Power block | MOV 15: control | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-C-0550 | A | Power block | MOV 16: control | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-C-0551 | A | Power block | MOV 17: control | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-C-0552 | A | Power block | MOV 18: control | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-C-0553 | A | Power block | MOV 19: control | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-C-0554 | A | Power block | MOV 20: control | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-C-0555 | A | Power block | Solenoid to JB JB-ST-SOL01: 10 x 2/C (field cables) | ST | ST: steam turbine (HP/IP + LP), ACC plant | JB-ST-SOL01 | ST: steam turbine (HP/IP + LP), ACC plant | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 119 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0556 | A | Power block | Home run JB-ST-SOL01 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-ST-SOL01 | ST: steam turbine (HP/IP + LP), ACC plant | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-C-0557 | A | Power block | Solenoid to JB JB-ST-SOL02: 10 x 2/C (field cables) | ST | ST: steam turbine (HP/IP + LP), ACC plant | JB-ST-SOL02 | ST: steam turbine (HP/IP + LP), ACC plant | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦2/C¦14 | 2/C | 14 | 10 | 1 |  |  |  | Tray / conduit | 119 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0558 | A | Power block | Home run JB-ST-SOL02 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-ST-SOL02 | ST: steam turbine (HP/IP + LP), ACC plant | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-C-0559 | A | Power block | Motor 1 of 4: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | STG | STG: steam-turbine generator | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 517 | 35
A-C-0560 | A | Power block | Motor 2 of 4: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | STG | STG: steam-turbine generator | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 517 | 35
A-C-0561 | A | Power block | Motor 3 of 4: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | STG | STG: steam-turbine generator | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 517 | 35
A-C-0562 | A | Power block | Motor 4 of 4: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | STG | STG: steam-turbine generator | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 517 | 35
A-C-0563 | A | Power block | Motor 1 of 6: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2A: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 86
A-C-0564 | A | Power block | Motor 2 of 6: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2A: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 86
A-C-0565 | A | Power block | Motor 3 of 6: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2A: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 86
A-C-0566 | A | Power block | Motor 4 of 6: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2A: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 86
A-C-0567 | A | Power block | Motor 5 of 6: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2A: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 86
A-C-0568 | A | Power block | Motor 6 of 6: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2A: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 86
A-C-0569 | A | Power block | Motor 1 of 6: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2B: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 97
A-C-0570 | A | Power block | Motor 2 of 6: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2B: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 97
A-C-0571 | A | Power block | Motor 3 of 6: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2B: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 97
A-C-0572 | A | Power block | Motor 4 of 6: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2B: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 97
A-C-0573 | A | Power block | Motor 5 of 6: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2B: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 97
A-C-0574 | A | Power block | Motor 6 of 6: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2B: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 97
A-C-0575 | A | Power block | Motor 1 of 6: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2C: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 97
A-C-0576 | A | Power block | Motor 2 of 6: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2C: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 97
A-C-0577 | A | Power block | Motor 3 of 6: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2C: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 97
A-C-0578 | A | Power block | Motor 4 of 6: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2C: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 97
A-C-0579 | A | Power block | Motor 5 of 6: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2C: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 97
A-C-0580 | A | Power block | Motor 6 of 6: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2C: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 97
A-C-0581 | A | Power block | Motor 1 of 6: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) |  | T-R3: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 0 | 71
A-C-0582 | A | Power block | Motor 2 of 6: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) |  | T-R3: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 0 | 71
A-C-0583 | A | Power block | Motor 3 of 6: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) |  | T-R3: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 0 | 71
A-C-0584 | A | Power block | Motor 4 of 6: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) |  | T-R3: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 0 | 71
A-C-0585 | A | Power block | Motor 5 of 6: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) |  | T-R3: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 0 | 71
A-C-0586 | A | Power block | Motor 6 of 6: control / local station | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) |  | T-R3: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 0 | 71
A-C-0587 | A | Power block | Motor 1 of 6: control / local station | LC-480-B | R1 LC-480-B (480 V switchgear) | T4-A | T4-A: 13.8/4.16 kV station transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 63 | 41
A-C-0588 | A | Power block | Motor 2 of 6: control / local station | LC-480-B | R1 LC-480-B (480 V switchgear) | T4-A | T4-A: 13.8/4.16 kV station transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 63 | 41
A-C-0589 | A | Power block | Motor 3 of 6: control / local station | LC-480-B | R1 LC-480-B (480 V switchgear) | T4-A | T4-A: 13.8/4.16 kV station transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 63 | 41
A-C-0590 | A | Power block | Motor 4 of 6: control / local station | LC-480-B | R1 LC-480-B (480 V switchgear) | T4-A | T4-A: 13.8/4.16 kV station transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 63 | 41
A-C-0591 | A | Power block | Motor 5 of 6: control / local station | LC-480-B | R1 LC-480-B (480 V switchgear) | T4-A | T4-A: 13.8/4.16 kV station transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 63 | 41
A-C-0592 | A | Power block | Motor 6 of 6: control / local station | LC-480-B | R1 LC-480-B (480 V switchgear) | T4-A | T4-A: 13.8/4.16 kV station transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 63 | 41
A-C-0593 | A | Power block | Control | R1 | R1: main electrical building (64 x 180 ft) | T4-A | T4-A: 13.8/4.16 kV station transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 730 | 124
A-C-0594 | A | Power block | Control | R1 | R1: main electrical building (64 x 180 ft) | T4-A | T4-A: 13.8/4.16 kV station transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 730 | 124
A-C-0595 | A | Power block | CT / VT | R1 | R1: main electrical building (64 x 180 ft) | T4-A | T4-A: 13.8/4.16 kV station transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 730 | 124
A-C-0596 | A | Power block | CT / VT | R1 | R1: main electrical building (64 x 180 ft) | T4-A | T4-A: 13.8/4.16 kV station transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 730 | 124
A-C-0597 | A | Power block | Motor 1 of 6: control / local station | LC-480-B | R1 LC-480-B (480 V switchgear) | T4-B | T4-B: 13.8/4.16 kV station transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 85 | 41
A-C-0598 | A | Power block | Motor 2 of 6: control / local station | LC-480-B | R1 LC-480-B (480 V switchgear) | T4-B | T4-B: 13.8/4.16 kV station transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 85 | 41
A-C-0599 | A | Power block | Motor 3 of 6: control / local station | LC-480-B | R1 LC-480-B (480 V switchgear) | T4-B | T4-B: 13.8/4.16 kV station transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 85 | 41
A-C-0600 | A | Power block | Motor 4 of 6: control / local station | LC-480-B | R1 LC-480-B (480 V switchgear) | T4-B | T4-B: 13.8/4.16 kV station transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 85 | 41
A-C-0601 | A | Power block | Motor 5 of 6: control / local station | LC-480-B | R1 LC-480-B (480 V switchgear) | T4-B | T4-B: 13.8/4.16 kV station transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 85 | 41
A-C-0602 | A | Power block | Motor 6 of 6: control / local station | LC-480-B | R1 LC-480-B (480 V switchgear) | T4-B | T4-B: 13.8/4.16 kV station transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 85 | 41
A-C-0603 | A | Power block | Control | R1 | R1: main electrical building (64 x 180 ft) | T4-B | T4-B: 13.8/4.16 kV station transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 752 | 124
A-C-0604 | A | Power block | Control | R1 | R1: main electrical building (64 x 180 ft) | T4-B | T4-B: 13.8/4.16 kV station transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 752 | 124
A-C-0605 | A | Power block | CT / VT | R1 | R1: main electrical building (64 x 180 ft) | T4-B | T4-B: 13.8/4.16 kV station transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 752 | 124
A-C-0606 | A | Power block | CT / VT | R1 | R1: main electrical building (64 x 180 ft) | T4-B | T4-B: 13.8/4.16 kV station transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 752 | 124
A-C-0607 | A | Power block | Control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | TCP-1 | TCP-1: GT1 turbine control and protection cabinets | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 178 | 94
A-C-0608 | A | Power block | Control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | TCP-2 | TCP-2: GT2 turbine control and protection cabinets | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 1069 | 184
A-C-0609 | A | Power block | Control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | TCP-3 | TCP-3: GT3 turbine control and protection cabinets | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 1024 | 240
A-C-0610 | A | Power block | Control | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | TCP-ST | TCP-ST: ST turbine control and protection cabinets | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 408 | 183
A-C-0611 | A | Power block | Motor 1 of 6: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | UAT-1 | UAT-1: 21/13.8 kV unit auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 566 | 158
A-C-0612 | A | Power block | Motor 2 of 6: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | UAT-1 | UAT-1: 21/13.8 kV unit auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 566 | 158
A-C-0613 | A | Power block | Motor 3 of 6: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | UAT-1 | UAT-1: 21/13.8 kV unit auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 566 | 158
A-C-0614 | A | Power block | Motor 4 of 6: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | UAT-1 | UAT-1: 21/13.8 kV unit auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 566 | 158
A-C-0615 | A | Power block | Motor 5 of 6: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | UAT-1 | UAT-1: 21/13.8 kV unit auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 566 | 158
A-C-0616 | A | Power block | Motor 6 of 6: control / local station | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | UAT-1 | UAT-1: 21/13.8 kV unit auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 566 | 158
A-C-0617 | A | Power block | Control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | UAT-1 | UAT-1: 21/13.8 kV unit auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 566 | 158
A-C-0618 | A | Power block | Control | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | UAT-1 | UAT-1: 21/13.8 kV unit auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 566 | 158
A-C-0619 | A | Power block | CT / VT | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | UAT-1 | UAT-1: 21/13.8 kV unit auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 566 | 158
A-C-0620 | A | Power block | CT / VT | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | UAT-1 | UAT-1: 21/13.8 kV unit auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 566 | 158
A-C-0621 | A | Power block | Motor 1 of 6: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | UAT-2 | UAT-2: 21/13.8 kV unit auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1423 | 96
A-C-0622 | A | Power block | Motor 2 of 6: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | UAT-2 | UAT-2: 21/13.8 kV unit auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1423 | 96
A-C-0623 | A | Power block | Motor 3 of 6: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | UAT-2 | UAT-2: 21/13.8 kV unit auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1423 | 96
A-C-0624 | A | Power block | Motor 4 of 6: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | UAT-2 | UAT-2: 21/13.8 kV unit auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1423 | 96
A-C-0625 | A | Power block | Motor 5 of 6: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | UAT-2 | UAT-2: 21/13.8 kV unit auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1423 | 96
A-C-0626 | A | Power block | Motor 6 of 6: control / local station | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | UAT-2 | UAT-2: 21/13.8 kV unit auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1423 | 96
A-C-0627 | A | Power block | Control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | UAT-2 | UAT-2: 21/13.8 kV unit auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1423 | 96
A-C-0628 | A | Power block | Control | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | UAT-2 | UAT-2: 21/13.8 kV unit auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 1423 | 96
A-C-0629 | A | Power block | CT / VT | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | UAT-2 | UAT-2: 21/13.8 kV unit auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Duct bank | 1423 | 96
A-C-0630 | A | Power block | CT / VT | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | UAT-2 | UAT-2: 21/13.8 kV unit auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Duct bank | 1423 | 96
A-C-0631 | A | Power block | Motor 1 of 6: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | UAT-3 | UAT-3: 21/13.8 kV unit auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1103 | 96
A-C-0632 | A | Power block | Motor 2 of 6: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | UAT-3 | UAT-3: 21/13.8 kV unit auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1103 | 96
A-C-0633 | A | Power block | Motor 3 of 6: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | UAT-3 | UAT-3: 21/13.8 kV unit auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1103 | 96
A-C-0634 | A | Power block | Motor 4 of 6: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | UAT-3 | UAT-3: 21/13.8 kV unit auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1103 | 96
A-C-0635 | A | Power block | Motor 5 of 6: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | UAT-3 | UAT-3: 21/13.8 kV unit auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1103 | 96
A-C-0636 | A | Power block | Motor 6 of 6: control / local station | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | UAT-3 | UAT-3: 21/13.8 kV unit auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1103 | 96
A-C-0637 | A | Power block | Control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | UAT-3 | UAT-3: 21/13.8 kV unit auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1103 | 96
A-C-0638 | A | Power block | Control | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | UAT-3 | UAT-3: 21/13.8 kV unit auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 1103 | 96
A-C-0639 | A | Power block | CT / VT | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | UAT-3 | UAT-3: 21/13.8 kV unit auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Duct bank | 1103 | 96
A-C-0640 | A | Power block | CT / VT | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | UAT-3 | UAT-3: 21/13.8 kV unit auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Duct bank | 1103 | 96
A-C-0641 | A | Power block | Motor 1 of 2: control / local station | MCC-GT1 | R1 MCC-GT1 | WASH-GT1 | WASH-GT1: compressor water-wash skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 261 | 145
A-C-0642 | A | Power block | Motor 2 of 2: control / local station | MCC-GT1 | R1 MCC-GT1 | WASH-GT1 | WASH-GT1: compressor water-wash skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 261 | 145
A-C-0643 | A | Power block | Solenoid to JB JB-WASH-GT1-SOL01: 4 x 2/C (field cables) | WASH-GT1 | WASH-GT1: compressor water-wash skid | JB-WASH-GT1-SOL01 | WASH-GT1: compressor water-wash skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 4 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0644 | A | Power block | Home run JB-WASH-GT1-SOL01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-WASH-GT1-SOL01 | WASH-GT1: compressor water-wash skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 183 | 94
A-C-0645 | A | Power block | Motor 1 of 2: control / local station | MCC-GT2 | R1 MCC-GT2 | WASH-GT2 | WASH-GT2: compressor water-wash skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 441 | 125
A-C-0646 | A | Power block | Motor 2 of 2: control / local station | MCC-GT2 | R1 MCC-GT2 | WASH-GT2 | WASH-GT2: compressor water-wash skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 441 | 125
A-C-0647 | A | Power block | Solenoid to JB JB-WASH-GT2-SOL01: 4 x 2/C (field cables) | WASH-GT2 | WASH-GT2: compressor water-wash skid | JB-WASH-GT2-SOL01 | WASH-GT2: compressor water-wash skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 4 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0648 | A | Power block | Home run JB-WASH-GT2-SOL01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-WASH-GT2-SOL01 | WASH-GT2: compressor water-wash skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 1075 | 188
A-C-0649 | A | Power block | Motor 1 of 2: control / local station | MCC-GT3 | R1 MCC-GT3 | WASH-GT3 | WASH-GT3: compressor water-wash skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 609 | 133
A-C-0650 | A | Power block | Motor 2 of 2: control / local station | MCC-GT3 | R1 MCC-GT3 | WASH-GT3 | WASH-GT3: compressor water-wash skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 609 | 133
A-C-0651 | A | Power block | Solenoid to JB JB-WASH-GT3-SOL01: 4 x 2/C (field cables) | WASH-GT3 | WASH-GT3: compressor water-wash skid | JB-WASH-GT3-SOL01 | WASH-GT3: compressor water-wash skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 4 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-C-0652 | A | Power block | Home run JB-WASH-GT3-SOL01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-WASH-GT3-SOL01 | WASH-GT3: compressor water-wash skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 1024 | 267
A-F-0001 | A | Power block | Plant network / DCS fibre | CR | Control / admin building (main control room) | CEMS-1 | CEMS shelter, HRSG 1 | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Tray | 1311 | 225
A-F-0002 | A | Power block | Plant network / DCS fibre | CR | Control / admin building (main control room) | CEMS-2 | CEMS shelter, HRSG 2 | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Tray | 1467 | 221
A-F-0003 | A | Power block | Plant network / DCS fibre | CR | Control / admin building (main control room) | CEMS-3 | CEMS shelter, HRSG 3 | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Tray | 1631 | 225
A-F-0004 | A | Power block | Plant network / DCS fibre | CR | Control / admin building (main control room) | EXC-1 | EXC-1: static excitation cubicles (GTG-1) | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Duct bank | 906 | 124
A-F-0005 | A | Power block | Plant network / DCS fibre | CR | Control / admin building (main control room) | EXC-2 | EXC-2: static excitation cubicles (GTG-2) | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Tray | 1066 | 124
A-F-0006 | A | Power block | Plant network / DCS fibre | CR | Control / admin building (main control room) | EXC-3 | EXC-3: static excitation cubicles (GTG-3) | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Tray | 1226 | 124
A-F-0007 | A | Power block | Plant network / DCS fibre | CR | Control / admin building (main control room) | EXC-ST | EXC-ST: static excitation cubicles (STG) | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Tray | 1289 | 140
A-F-0008 | A | Power block | Plant network / DCS fibre | CR | Control / admin building (main control room) | NGT-1 | NGT-1: neutral grounding cubicle (GTG-1) | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Duct bank | 899 | 138
A-F-0009 | A | Power block | Plant network / DCS fibre | CR | Control / admin building (main control room) | NGT-2 | NGT-2: neutral grounding cubicle (GTG-2) | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Tray | 1059 | 138
A-F-0010 | A | Power block | Plant network / DCS fibre | CR | Control / admin building (main control room) | NGT-3 | NGT-3: neutral grounding cubicle (GTG-3) | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Tray | 1219 | 138
A-F-0011 | A | Power block | Plant network / DCS fibre | CR | Control / admin building (main control room) | NGT-ST | NGT-ST: neutral grounding cubicle (STG) | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Tray | 1289 | 124
A-F-0012 | A | Power block | Plant network / DCS fibre | CR | Control / admin building (main control room) | R1 | R1: main electrical building (64 x 180 ft) | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Duct bank | 371 | 32
A-F-0013 | A | Power block | Plant network / DCS fibre | CR | Control / admin building (main control room) | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Duct bank | 546 | 96
A-F-0014 | A | Power block | Plant network / DCS fibre | CR | Control / admin building (main control room) | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Tray | 1566 | 200
A-F-0015 | A | Power block | Plant network / DCS fibre | CR | Control / admin building (main control room) | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Tray | 1726 | 200
A-F-0016 | A | Power block | Plant network / DCS fibre | CR | Control / admin building (main control room) | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Tray | 1302 | 188
A-F-0017 | A | Power block | Plant network / DCS fibre | CR | Control / admin building (main control room) | SPC-1 | SPC-1: surge-protection and VT cubicle on the IPB (GTG-1) | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Duct bank | 964 | 44
A-F-0018 | A | Power block | Plant network / DCS fibre | CR | Control / admin building (main control room) | SPC-2 | SPC-2: surge-protection and VT cubicle on the IPB (GTG-2) | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Duct bank | 1124 | 44
A-F-0019 | A | Power block | Plant network / DCS fibre | CR | Control / admin building (main control room) | SPC-3 | SPC-3: surge-protection and VT cubicle on the IPB (GTG-3) | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Duct bank | 1284 | 44
A-FA-0001 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | CEMS-1 | CEMS shelter, HRSG 1 | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 277 | 97
A-FA-0002 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | CEMS-2 | CEMS shelter, HRSG 2 | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 273 | 93
A-FA-0003 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | CEMS-3 | CEMS shelter, HRSG 3 | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 277 | 97
A-FA-0004 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HALL | Common turbine hall | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 1069 | 184
A-FA-0005 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | EXC-1 | EXC-1: static excitation cubicles (GTG-1) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 366 | 106
A-FA-0006 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | EXC-2 | EXC-2: static excitation cubicles (GTG-2) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 1240 | 196
A-FA-0007 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | EXC-3 | EXC-3: static excitation cubicles (GTG-3) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 1260 | 148
A-FA-0008 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | EXC-ST | EXC-ST: static excitation cubicles (STG) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 392 | 96
A-FA-0009 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | GT1 | GT1: H-class gas turbine (60 Hz) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 154 | 103
A-FA-0010 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | GT2 | GT2: H-class gas turbine (60 Hz) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 1046 | 197
A-FA-0011 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | GT3 | GT3: H-class gas turbine (60 Hz) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 986 | 249
A-FA-0012 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | NGT-1 | NGT-1: neutral grounding cubicle (GTG-1) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 359 | 120
A-FA-0013 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | NGT-2 | NGT-2: neutral grounding cubicle (GTG-2) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 1233 | 210
A-FA-0014 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | NGT-3 | NGT-3: neutral grounding cubicle (GTG-3) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 1229 | 198
A-FA-0015 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | NGT-ST | NGT-ST: neutral grounding cubicle (STG) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 392 | 105
A-FA-0016 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R1 | R1: main electrical building (64 x 180 ft) | EMCC | R1 EMCC (emergency MCC) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 635 | 144
A-FA-0017 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R1 | R1: main electrical building (64 x 180 ft) | LC-480-A | R1 LC-480-A (480 V switchgear) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 624 | 155
A-FA-0018 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R1 | R1: main electrical building (64 x 180 ft) | LC-480-B | R1 LC-480-B (480 V switchgear) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 624 | 144
A-FA-0019 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R1 | R1: main electrical building (64 x 180 ft) | MCC-C1 | R1 MCC-C1 | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 624 | 181
A-FA-0020 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R1 | R1: main electrical building (64 x 180 ft) | MCC-C2 | R1 MCC-C2 | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 624 | 165
A-FA-0021 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | MCC-GT1 | R1 MCC-GT1 | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 90 | 123
A-FA-0022 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | MCC-GT2 | R1 MCC-GT2 | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 1114 | 223
A-FA-0023 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | MCC-GT3 | R1 MCC-GT3 | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 726 | 181
A-FA-0024 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R1 | R1: main electrical building (64 x 180 ft) | SWGR-13.8-1 | R1 SWGR-13.8-1 (11 x 36 in cubicles, 15 kV metal-clad) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 66 | 54
A-FA-0025 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R1 | R1: main electrical building (64 x 180 ft) | SWGR-13.8-2 | R1 SWGR-13.8-2 (11 x 36 in cubicles, 15 kV metal-clad) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 86 | 71
A-FA-0026 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R1 | R1: main electrical building (64 x 180 ft) | SWGR-13.8-3 | R1 SWGR-13.8-3 (11 x 36 in cubicles, 15 kV metal-clad) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 624 | 128
A-FA-0027 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R1 | R1: main electrical building (64 x 180 ft) | SWGR-4.16-A | R1 SWGR-4.16-A (9 x 36 in cubicles, 5 kV metal-clad) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 66 | 70
A-FA-0028 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R1 | R1: main electrical building (64 x 180 ft) | R1 | R1: main electrical building (64 x 180 ft) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 32
A-FA-0029 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 72
A-FA-0030 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 72
A-FA-0031 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 72
A-FA-0032 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 32
A-FA-0033 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | SOS-1 | SOS-1: GTG-1 seal-oil and H2 / CO2 gas-control skid | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 403 | 138
A-FA-0034 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | SOS-2 | SOS-2: GTG-2 seal-oil and H2 / CO2 gas-control skid | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 1277 | 228
A-FA-0035 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | SOS-3 | SOS-3: GTG-3 seal-oil and H2 / CO2 gas-control skid | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 1214 | 126
A-FA-0036 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | SPC-1 | SPC-1: surge-protection and VT cubicle on the IPB (GTG-1) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 395 | 124
A-FA-0037 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | SPC-2 | SPC-2: surge-protection and VT cubicle on the IPB (GTG-2) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 1269 | 214
A-FA-0038 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | SPC-3 | SPC-3: surge-protection and VT cubicle on the IPB (GTG-3) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 1193 | 114
A-FA-0039 | A | Power block | Fire alarm / F&G loop (to the local FACP / F&G node) | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | Turbine hall exterior electrical: MC-cable risers, roof exhausters, wa | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 1069 | 184
A-I-0001 | A | Power block | Analog instrument to JB JB-AC-A/B/C-AI01: 15 x 1 pr (field cables) | AC-A/B/C | Air compressors AC-A/B/C | JB-AC-A/B/C-AI01 | Air compressors AC-A/B/C | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 15 | 1 |  |  |  | Tray / conduit | 88 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0002 | A | Power block | Home run JB-AC-A/B/C-AI01 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-AC-A/B/C-AI01 | Air compressors AC-A/B/C | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 88 | 84
A-I-0003 | A | Power block | Discrete device to JB JB-AC-A/B/C-DI01: 15 x 1 pr (field cables) | AC-A/B/C | Air compressors AC-A/B/C | JB-AC-A/B/C-DI01 | Air compressors AC-A/B/C | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 15 | 1 |  |  |  | Tray / conduit | 88 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0004 | A | Power block | Home run JB-AC-A/B/C-DI01 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-AC-A/B/C-DI01 | Air compressors AC-A/B/C | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 88 | 84
A-I-0005 | A | Power block | Analog instrument to JB JB-BFP-1-AI01: 20 x 1 pr (field cables) | BFP-1 | BFP-1A/B: boiler feed pumps (13.8 kV DOL) | JB-BFP-1-AI01 | BFP-1A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 68 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0006 | A | Power block | Home run JB-BFP-1-AI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-BFP-1-AI01 | BFP-1A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 481 | 84
A-I-0007 | A | Power block | Analog instrument to JB JB-BFP-1-AI02: 10 x 1 pr (field cables) | BFP-1 | BFP-1A/B: boiler feed pumps (13.8 kV DOL) | JB-BFP-1-AI02 | BFP-1A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 68 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0008 | A | Power block | Home run JB-BFP-1-AI02 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-BFP-1-AI02 | BFP-1A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 481 | 84
A-I-0009 | A | Power block | Discrete device to JB JB-BFP-1-DI01: 20 x 1 pr (field cables) | BFP-1 | BFP-1A/B: boiler feed pumps (13.8 kV DOL) | JB-BFP-1-DI01 | BFP-1A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 68 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0010 | A | Power block | Home run JB-BFP-1-DI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-BFP-1-DI01 | BFP-1A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 481 | 84
A-I-0011 | A | Power block | RTD to JB JB-BFP-1-RTD01: 10 x 1 tri (field cables) | BFP-1 | BFP-1A/B: boiler feed pumps (13.8 kV DOL) | JB-BFP-1-RTD01 | BFP-1A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 68 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0012 | A | Power block | Home run JB-BFP-1-RTD01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-BFP-1-RTD01 | BFP-1A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Tray | 481 | 84
A-I-0013 | A | Power block | RTD to JB JB-BFP-1-RTD02: 10 x 1 tri (field cables) | BFP-1 | BFP-1A/B: boiler feed pumps (13.8 kV DOL) | JB-BFP-1-RTD02 | BFP-1A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 68 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0014 | A | Power block | Home run JB-BFP-1-RTD02 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-BFP-1-RTD02 | BFP-1A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Tray | 481 | 84
A-I-0015 | A | Power block | RTD to JB JB-BFP-1-RTD03: 4 x 1 tri (field cables) | BFP-1 | BFP-1A/B: boiler feed pumps (13.8 kV DOL) | JB-BFP-1-RTD03 | BFP-1A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 4 | 1 |  |  |  | Tray / conduit | 68 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0016 | A | Power block | Home run JB-BFP-1-RTD03 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-BFP-1-RTD03 | BFP-1A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Tray | 481 | 84
A-I-0017 | A | Power block | Analog instrument to JB JB-BFP-2-AI01: 20 x 1 pr (field cables) | BFP-2 | BFP-2A/B: boiler feed pumps (13.8 kV DOL) | JB-BFP-2-AI01 | BFP-2A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 68 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0018 | A | Power block | Home run JB-BFP-2-AI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-BFP-2-AI01 | BFP-2A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 479 | 84
A-I-0019 | A | Power block | Analog instrument to JB JB-BFP-2-AI02: 10 x 1 pr (field cables) | BFP-2 | BFP-2A/B: boiler feed pumps (13.8 kV DOL) | JB-BFP-2-AI02 | BFP-2A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 68 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0020 | A | Power block | Home run JB-BFP-2-AI02 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-BFP-2-AI02 | BFP-2A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 479 | 84
A-I-0021 | A | Power block | Discrete device to JB JB-BFP-2-DI01: 20 x 1 pr (field cables) | BFP-2 | BFP-2A/B: boiler feed pumps (13.8 kV DOL) | JB-BFP-2-DI01 | BFP-2A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 68 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0022 | A | Power block | Home run JB-BFP-2-DI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-BFP-2-DI01 | BFP-2A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 479 | 84
A-I-0023 | A | Power block | RTD to JB JB-BFP-2-RTD01: 10 x 1 tri (field cables) | BFP-2 | BFP-2A/B: boiler feed pumps (13.8 kV DOL) | JB-BFP-2-RTD01 | BFP-2A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 68 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0024 | A | Power block | Home run JB-BFP-2-RTD01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-BFP-2-RTD01 | BFP-2A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Tray | 479 | 84
A-I-0025 | A | Power block | RTD to JB JB-BFP-2-RTD02: 10 x 1 tri (field cables) | BFP-2 | BFP-2A/B: boiler feed pumps (13.8 kV DOL) | JB-BFP-2-RTD02 | BFP-2A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 68 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0026 | A | Power block | Home run JB-BFP-2-RTD02 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-BFP-2-RTD02 | BFP-2A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Tray | 479 | 84
A-I-0027 | A | Power block | RTD to JB JB-BFP-2-RTD03: 4 x 1 tri (field cables) | BFP-2 | BFP-2A/B: boiler feed pumps (13.8 kV DOL) | JB-BFP-2-RTD03 | BFP-2A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 4 | 1 |  |  |  | Tray / conduit | 68 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0028 | A | Power block | Home run JB-BFP-2-RTD03 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-BFP-2-RTD03 | BFP-2A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Tray | 479 | 84
A-I-0029 | A | Power block | Analog instrument to JB JB-BFP-3-AI01: 20 x 1 pr (field cables) | BFP-3 | BFP-3A/B: boiler feed pumps (13.8 kV DOL) | JB-BFP-3-AI01 | BFP-3A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 68 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0030 | A | Power block | Home run JB-BFP-3-AI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-BFP-3-AI01 | BFP-3A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 481 | 84
A-I-0031 | A | Power block | Analog instrument to JB JB-BFP-3-AI02: 10 x 1 pr (field cables) | BFP-3 | BFP-3A/B: boiler feed pumps (13.8 kV DOL) | JB-BFP-3-AI02 | BFP-3A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 68 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0032 | A | Power block | Home run JB-BFP-3-AI02 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-BFP-3-AI02 | BFP-3A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 481 | 84
A-I-0033 | A | Power block | Discrete device to JB JB-BFP-3-DI01: 20 x 1 pr (field cables) | BFP-3 | BFP-3A/B: boiler feed pumps (13.8 kV DOL) | JB-BFP-3-DI01 | BFP-3A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 68 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0034 | A | Power block | Home run JB-BFP-3-DI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-BFP-3-DI01 | BFP-3A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 481 | 84
A-I-0035 | A | Power block | RTD to JB JB-BFP-3-RTD01: 10 x 1 tri (field cables) | BFP-3 | BFP-3A/B: boiler feed pumps (13.8 kV DOL) | JB-BFP-3-RTD01 | BFP-3A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 68 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0036 | A | Power block | Home run JB-BFP-3-RTD01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-BFP-3-RTD01 | BFP-3A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Tray | 481 | 84
A-I-0037 | A | Power block | RTD to JB JB-BFP-3-RTD02: 10 x 1 tri (field cables) | BFP-3 | BFP-3A/B: boiler feed pumps (13.8 kV DOL) | JB-BFP-3-RTD02 | BFP-3A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 68 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0038 | A | Power block | Home run JB-BFP-3-RTD02 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-BFP-3-RTD02 | BFP-3A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Tray | 481 | 84
A-I-0039 | A | Power block | RTD to JB JB-BFP-3-RTD03: 4 x 1 tri (field cables) | BFP-3 | BFP-3A/B: boiler feed pumps (13.8 kV DOL) | JB-BFP-3-RTD03 | BFP-3A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 4 | 1 |  |  |  | Tray / conduit | 68 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0040 | A | Power block | Home run JB-BFP-3-RTD03 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-BFP-3-RTD03 | BFP-3A/B: boiler feed pumps (13.8 kV DOL) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Tray | 481 | 84
A-I-0041 | A | Power block | Analog instrument to JB JB-CEMS-1-AI01: 12 x 1 pr (field cables) | CEMS-1 | CEMS shelter, HRSG 1 | JB-CEMS-1-AI01 | CEMS shelter, HRSG 1 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0042 | A | Power block | Home run JB-CEMS-1-AI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-CEMS-1-AI01 | CEMS shelter, HRSG 1 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 277 | 97
A-I-0043 | A | Power block | Discrete device to JB JB-CEMS-1-DI01: 10 x 1 pr (field cables) | CEMS-1 | CEMS shelter, HRSG 1 | JB-CEMS-1-DI01 | CEMS shelter, HRSG 1 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0044 | A | Power block | Home run JB-CEMS-1-DI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-CEMS-1-DI01 | CEMS shelter, HRSG 1 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 277 | 97
A-I-0045 | A | Power block | Analog instrument to JB JB-CEMS-2-AI01: 12 x 1 pr (field cables) | CEMS-2 | CEMS shelter, HRSG 2 | JB-CEMS-2-AI01 | CEMS shelter, HRSG 2 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0046 | A | Power block | Home run JB-CEMS-2-AI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-CEMS-2-AI01 | CEMS shelter, HRSG 2 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 273 | 93
A-I-0047 | A | Power block | Discrete device to JB JB-CEMS-2-DI01: 10 x 1 pr (field cables) | CEMS-2 | CEMS shelter, HRSG 2 | JB-CEMS-2-DI01 | CEMS shelter, HRSG 2 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0048 | A | Power block | Home run JB-CEMS-2-DI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-CEMS-2-DI01 | CEMS shelter, HRSG 2 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 273 | 93
A-I-0049 | A | Power block | Analog instrument to JB JB-CEMS-3-AI01: 12 x 1 pr (field cables) | CEMS-3 | CEMS shelter, HRSG 3 | JB-CEMS-3-AI01 | CEMS shelter, HRSG 3 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0050 | A | Power block | Home run JB-CEMS-3-AI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-CEMS-3-AI01 | CEMS shelter, HRSG 3 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 277 | 97
A-I-0051 | A | Power block | Discrete device to JB JB-CEMS-3-DI01: 10 x 1 pr (field cables) | CEMS-3 | CEMS shelter, HRSG 3 | JB-CEMS-3-DI01 | CEMS shelter, HRSG 3 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0052 | A | Power block | Home run JB-CEMS-3-DI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-CEMS-3-DI01 | CEMS shelter, HRSG 3 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 277 | 97
A-I-0053 | A | Power block | Analog instrument to JB JB-Chem feed-AI01: 8 x 1 pr (field cables) | Chem feed | Chemical feed | JB-Chem feed-AI01 | Chemical feed | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 75 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0054 | A | Power block | Home run JB-Chem feed-AI01 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-Chem feed-AI01 | Chemical feed | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 258 | 35
A-I-0055 | A | Power block | Discrete device to JB JB-Chem feed-DI01: 12 x 1 pr (field cables) | Chem feed | Chemical feed | JB-Chem feed-DI01 | Chemical feed | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 75 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0056 | A | Power block | Home run JB-Chem feed-DI01 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-Chem feed-DI01 | Chemical feed | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 258 | 35
A-I-0057 | A | Power block | Analog instrument to JB JB-EHC-ST-AI01: 10 x 1 pr (field cables) | EHC-ST | EHC-ST: ST electro-hydraulic control power unit | JB-EHC-ST-AI01 | EHC-ST: ST electro-hydraulic control power unit | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0058 | A | Power block | Home run JB-EHC-ST-AI01 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-EHC-ST-AI01 | EHC-ST: ST electro-hydraulic control power unit | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 67 | 89
A-I-0059 | A | Power block | Discrete device to JB JB-EHC-ST-DI01: 10 x 1 pr (field cables) | EHC-ST | EHC-ST: ST electro-hydraulic control power unit | JB-EHC-ST-DI01 | EHC-ST: ST electro-hydraulic control power unit | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0060 | A | Power block | Home run JB-EHC-ST-DI01 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-EHC-ST-DI01 | EHC-ST: ST electro-hydraulic control power unit | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 67 | 89
A-I-0061 | A | Power block | Instrumentation | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | ET-1 | ET-1: excitation transformer (dry type, GTG-1 terminals) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 403 | 119
A-I-0062 | A | Power block | Instrumentation | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | ET-1 | ET-1: excitation transformer (dry type, GTG-1 terminals) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 403 | 119
A-I-0063 | A | Power block | Instrumentation | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | ET-1 | ET-1: excitation transformer (dry type, GTG-1 terminals) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Tray | 403 | 119
A-I-0064 | A | Power block | Instrumentation | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | ET-1 | ET-1: excitation transformer (dry type, GTG-1 terminals) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Tray | 403 | 119
A-I-0065 | A | Power block | Instrumentation | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | ET-1 | ET-1: excitation transformer (dry type, GTG-1 terminals) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Tray | 403 | 119
A-I-0066 | A | Power block | Instrumentation | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | ET-1 | ET-1: excitation transformer (dry type, GTG-1 terminals) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Tray | 403 | 119
A-I-0067 | A | Power block | Instrumentation | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | ET-1 | ET-1: excitation transformer (dry type, GTG-1 terminals) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Tray | 403 | 119
A-I-0068 | A | Power block | Instrumentation | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | ET-1 | ET-1: excitation transformer (dry type, GTG-1 terminals) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Tray | 403 | 119
A-I-0069 | A | Power block | Instrumentation | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | ET-1 | ET-1: excitation transformer (dry type, GTG-1 terminals) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Tray | 403 | 119
A-I-0070 | A | Power block | Instrumentation | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | ET-1 | ET-1: excitation transformer (dry type, GTG-1 terminals) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Tray | 403 | 119
A-I-0071 | A | Power block | Instrumentation | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | ET-2 | ET-2: excitation transformer (dry type, GTG-2 terminals) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 1277 | 209
A-I-0072 | A | Power block | Instrumentation | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | ET-2 | ET-2: excitation transformer (dry type, GTG-2 terminals) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 1277 | 209
A-I-0073 | A | Power block | Instrumentation | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | ET-2 | ET-2: excitation transformer (dry type, GTG-2 terminals) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Tray | 1277 | 209
A-I-0074 | A | Power block | Instrumentation | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | ET-2 | ET-2: excitation transformer (dry type, GTG-2 terminals) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Tray | 1277 | 209
A-I-0075 | A | Power block | Instrumentation | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | ET-2 | ET-2: excitation transformer (dry type, GTG-2 terminals) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Tray | 1277 | 209
A-I-0076 | A | Power block | Instrumentation | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | ET-2 | ET-2: excitation transformer (dry type, GTG-2 terminals) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Tray | 1277 | 209
A-I-0077 | A | Power block | Instrumentation | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | ET-2 | ET-2: excitation transformer (dry type, GTG-2 terminals) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Tray | 1277 | 209
A-I-0078 | A | Power block | Instrumentation | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | ET-2 | ET-2: excitation transformer (dry type, GTG-2 terminals) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Tray | 1277 | 209
A-I-0079 | A | Power block | Instrumentation | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | ET-2 | ET-2: excitation transformer (dry type, GTG-2 terminals) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Tray | 1277 | 209
A-I-0080 | A | Power block | Instrumentation | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | ET-2 | ET-2: excitation transformer (dry type, GTG-2 terminals) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Tray | 1277 | 209
A-I-0081 | A | Power block | Instrumentation | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | ET-3 | ET-3: excitation transformer (dry type, GTG-3 terminals) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1214 | 102
A-I-0082 | A | Power block | Instrumentation | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | ET-3 | ET-3: excitation transformer (dry type, GTG-3 terminals) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1214 | 102
A-I-0083 | A | Power block | Instrumentation | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | ET-3 | ET-3: excitation transformer (dry type, GTG-3 terminals) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1214 | 102
A-I-0084 | A | Power block | Instrumentation | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | ET-3 | ET-3: excitation transformer (dry type, GTG-3 terminals) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1214 | 102
A-I-0085 | A | Power block | Instrumentation | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | ET-3 | ET-3: excitation transformer (dry type, GTG-3 terminals) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1214 | 102
A-I-0086 | A | Power block | Instrumentation | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | ET-3 | ET-3: excitation transformer (dry type, GTG-3 terminals) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1214 | 102
A-I-0087 | A | Power block | Instrumentation | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | ET-3 | ET-3: excitation transformer (dry type, GTG-3 terminals) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1214 | 102
A-I-0088 | A | Power block | Instrumentation | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | ET-3 | ET-3: excitation transformer (dry type, GTG-3 terminals) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1214 | 102
A-I-0089 | A | Power block | Instrumentation | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | ET-3 | ET-3: excitation transformer (dry type, GTG-3 terminals) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1214 | 102
A-I-0090 | A | Power block | Instrumentation | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | ET-3 | ET-3: excitation transformer (dry type, GTG-3 terminals) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1214 | 102
A-I-0091 | A | Power block | Analog instrument to JB JB-EXC-1-AI01: 10 x 1 pr (field cables) | EXC-1 | EXC-1: static excitation cubicles (GTG-1) | JB-EXC-1-AI01 | EXC-1: static excitation cubicles (GTG-1) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0092 | A | Power block | Home run JB-EXC-1-AI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-EXC-1-AI01 | EXC-1: static excitation cubicles (GTG-1) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 366 | 106
A-I-0093 | A | Power block | Discrete device to JB JB-EXC-1-DI01: 20 x 1 pr (field cables) | EXC-1 | EXC-1: static excitation cubicles (GTG-1) | JB-EXC-1-DI01 | EXC-1: static excitation cubicles (GTG-1) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0094 | A | Power block | Home run JB-EXC-1-DI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-EXC-1-DI01 | EXC-1: static excitation cubicles (GTG-1) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 366 | 106
A-I-0095 | A | Power block | Analog instrument to JB JB-EXC-2-AI01: 10 x 1 pr (field cables) | EXC-2 | EXC-2: static excitation cubicles (GTG-2) | JB-EXC-2-AI01 | EXC-2: static excitation cubicles (GTG-2) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0096 | A | Power block | Home run JB-EXC-2-AI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-EXC-2-AI01 | EXC-2: static excitation cubicles (GTG-2) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1240 | 196
A-I-0097 | A | Power block | Discrete device to JB JB-EXC-2-DI01: 20 x 1 pr (field cables) | EXC-2 | EXC-2: static excitation cubicles (GTG-2) | JB-EXC-2-DI01 | EXC-2: static excitation cubicles (GTG-2) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0098 | A | Power block | Home run JB-EXC-2-DI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-EXC-2-DI01 | EXC-2: static excitation cubicles (GTG-2) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1240 | 196
A-I-0099 | A | Power block | Analog instrument to JB JB-EXC-3-AI01: 10 x 1 pr (field cables) | EXC-3 | EXC-3: static excitation cubicles (GTG-3) | JB-EXC-3-AI01 | EXC-3: static excitation cubicles (GTG-3) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0100 | A | Power block | Home run JB-EXC-3-AI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-EXC-3-AI01 | EXC-3: static excitation cubicles (GTG-3) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1260 | 148
A-I-0101 | A | Power block | Discrete device to JB JB-EXC-3-DI01: 20 x 1 pr (field cables) | EXC-3 | EXC-3: static excitation cubicles (GTG-3) | JB-EXC-3-DI01 | EXC-3: static excitation cubicles (GTG-3) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0102 | A | Power block | Home run JB-EXC-3-DI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-EXC-3-DI01 | EXC-3: static excitation cubicles (GTG-3) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1260 | 148
A-I-0103 | A | Power block | Analog instrument to JB JB-EXC-ST-AI01: 10 x 1 pr (field cables) | EXC-ST | EXC-ST: static excitation cubicles (STG) | JB-EXC-ST-AI01 | EXC-ST: static excitation cubicles (STG) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0104 | A | Power block | Home run JB-EXC-ST-AI01 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-EXC-ST-AI01 | EXC-ST: static excitation cubicles (STG) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 392 | 96
A-I-0105 | A | Power block | Discrete device to JB JB-EXC-ST-DI01: 20 x 1 pr (field cables) | EXC-ST | EXC-ST: static excitation cubicles (STG) | JB-EXC-ST-DI01 | EXC-ST: static excitation cubicles (STG) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0106 | A | Power block | Home run JB-EXC-ST-DI01 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-EXC-ST-DI01 | EXC-ST: static excitation cubicles (STG) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 392 | 96
A-I-0107 | A | Power block | Analog instrument to JB JB-FH-1-AI01: 10 x 1 pr (field cables) | FH-1 | FH-1: GT inlet filter house on its own frame | JB-FH-1-AI01 | FH-1: GT inlet filter house on its own frame | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 140 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0108 | A | Power block | Home run JB-FH-1-AI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-FH-1-AI01 | FH-1: GT inlet filter house on its own frame | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 373 | 106
A-I-0109 | A | Power block | Discrete device to JB JB-FH-1-DI01: 20 x 1 pr (field cables) | FH-1 | FH-1: GT inlet filter house on its own frame | JB-FH-1-DI01 | FH-1: GT inlet filter house on its own frame | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 140 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0110 | A | Power block | Home run JB-FH-1-DI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-FH-1-DI01 | FH-1: GT inlet filter house on its own frame | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 373 | 106
A-I-0111 | A | Power block | Discrete device to JB JB-FH-1-DI02: 10 x 1 pr (field cables) | FH-1 | FH-1: GT inlet filter house on its own frame | JB-FH-1-DI02 | FH-1: GT inlet filter house on its own frame | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 140 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0112 | A | Power block | Home run JB-FH-1-DI02 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-FH-1-DI02 | FH-1: GT inlet filter house on its own frame | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 373 | 106
A-I-0113 | A | Power block | Analog instrument to JB JB-FH-2-AI01: 10 x 1 pr (field cables) | FH-2 | FH-2: GT inlet filter house on its own frame | JB-FH-2-AI01 | FH-2: GT inlet filter house on its own frame | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 140 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0114 | A | Power block | Home run JB-FH-2-AI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-FH-2-AI01 | FH-2: GT inlet filter house on its own frame | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1247 | 196
A-I-0115 | A | Power block | Discrete device to JB JB-FH-2-DI01: 20 x 1 pr (field cables) | FH-2 | FH-2: GT inlet filter house on its own frame | JB-FH-2-DI01 | FH-2: GT inlet filter house on its own frame | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 140 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0116 | A | Power block | Home run JB-FH-2-DI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-FH-2-DI01 | FH-2: GT inlet filter house on its own frame | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1247 | 196
A-I-0117 | A | Power block | Discrete device to JB JB-FH-2-DI02: 10 x 1 pr (field cables) | FH-2 | FH-2: GT inlet filter house on its own frame | JB-FH-2-DI02 | FH-2: GT inlet filter house on its own frame | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 140 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0118 | A | Power block | Home run JB-FH-2-DI02 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-FH-2-DI02 | FH-2: GT inlet filter house on its own frame | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1247 | 196
A-I-0119 | A | Power block | Analog instrument to JB JB-FH-3-AI01: 10 x 1 pr (field cables) | FH-3 | FH-3: GT inlet filter house on its own frame | JB-FH-3-AI01 | FH-3: GT inlet filter house on its own frame | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 140 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0120 | A | Power block | Home run JB-FH-3-AI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-FH-3-AI01 | FH-3: GT inlet filter house on its own frame | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1193 | 96
A-I-0121 | A | Power block | Discrete device to JB JB-FH-3-DI01: 20 x 1 pr (field cables) | FH-3 | FH-3: GT inlet filter house on its own frame | JB-FH-3-DI01 | FH-3: GT inlet filter house on its own frame | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 140 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0122 | A | Power block | Home run JB-FH-3-DI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-FH-3-DI01 | FH-3: GT inlet filter house on its own frame | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1193 | 96
A-I-0123 | A | Power block | Discrete device to JB JB-FH-3-DI02: 10 x 1 pr (field cables) | FH-3 | FH-3: GT inlet filter house on its own frame | JB-FH-3-DI02 | FH-3: GT inlet filter house on its own frame | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 140 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0124 | A | Power block | Home run JB-FH-3-DI02 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-FH-3-DI02 | FH-3: GT inlet filter house on its own frame | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1193 | 96
A-I-0125 | A | Power block | Analog instrument to JB JB-FS-GT1-AI01: 4 x 1 pr (field cables) | FS-GT1 | FS-GT1: CO2 fire-suppression skid | JB-FS-GT1-AI01 | FS-GT1: CO2 fire-suppression skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0126 | A | Power block | Home run JB-FS-GT1-AI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-FS-GT1-AI01 | FS-GT1: CO2 fire-suppression skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 210 | 104
A-I-0127 | A | Power block | Discrete device to JB JB-FS-GT1-DI01: 20 x 1 pr (field cables) | FS-GT1 | FS-GT1: CO2 fire-suppression skid | JB-FS-GT1-DI01 | FS-GT1: CO2 fire-suppression skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0128 | A | Power block | Home run JB-FS-GT1-DI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-FS-GT1-DI01 | FS-GT1: CO2 fire-suppression skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 210 | 104
A-I-0129 | A | Power block | Analog instrument to JB JB-FS-GT2-AI01: 4 x 1 pr (field cables) | FS-GT2 | FS-GT2: CO2 fire-suppression skid | JB-FS-GT2-AI01 | FS-GT2: CO2 fire-suppression skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0130 | A | Power block | Home run JB-FS-GT2-AI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-FS-GT2-AI01 | FS-GT2: CO2 fire-suppression skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1102 | 198
A-I-0131 | A | Power block | Discrete device to JB JB-FS-GT2-DI01: 20 x 1 pr (field cables) | FS-GT2 | FS-GT2: CO2 fire-suppression skid | JB-FS-GT2-DI01 | FS-GT2: CO2 fire-suppression skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0132 | A | Power block | Home run JB-FS-GT2-DI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-FS-GT2-DI01 | FS-GT2: CO2 fire-suppression skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1102 | 198
A-I-0133 | A | Power block | Analog instrument to JB JB-FS-GT3-AI01: 4 x 1 pr (field cables) | FS-GT3 | FS-GT3: CO2 fire-suppression skid | JB-FS-GT3-AI01 | FS-GT3: CO2 fire-suppression skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0134 | A | Power block | Home run JB-FS-GT3-AI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-FS-GT3-AI01 | FS-GT3: CO2 fire-suppression skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 908 | 238
A-I-0135 | A | Power block | Discrete device to JB JB-FS-GT3-DI01: 20 x 1 pr (field cables) | FS-GT3 | FS-GT3: CO2 fire-suppression skid | JB-FS-GT3-DI01 | FS-GT3: CO2 fire-suppression skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0136 | A | Power block | Home run JB-FS-GT3-DI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-FS-GT3-DI01 | FS-GT3: CO2 fire-suppression skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 908 | 238
A-I-0137 | A | Power block | Discrete device to JB JB-GCB-1-DI01: 20 x 1 pr (field cables) | GCB-1 | GCB-1: generator circuit breaker | JB-GCB-1-DI01 | GCB-1: generator circuit breaker | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 47 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0138 | A | Power block | Home run JB-GCB-1-DI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GCB-1-DI01 | GCB-1: generator circuit breaker | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 373 | 118
A-I-0139 | A | Power block | Discrete device to JB JB-GCB-2-DI01: 20 x 1 pr (field cables) | GCB-2 | GCB-2: generator circuit breaker | JB-GCB-2-DI01 | GCB-2: generator circuit breaker | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 47 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0140 | A | Power block | Home run JB-GCB-2-DI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GCB-2-DI01 | GCB-2: generator circuit breaker | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1247 | 208
A-I-0141 | A | Power block | Discrete device to JB JB-GCB-3-DI01: 20 x 1 pr (field cables) | GCB-3 | GCB-3: generator circuit breaker | JB-GCB-3-DI01 | GCB-3: generator circuit breaker | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 47 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0142 | A | Power block | Home run JB-GCB-3-DI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GCB-3-DI01 | GCB-3: generator circuit breaker | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1193 | 97
A-I-0143 | A | Power block | Discrete device to JB JB-GCB-ST-DI01: 20 x 1 pr (field cables) | GCB-ST | GCB-ST | JB-GCB-ST-DI01 | GCB-ST | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 47 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0144 | A | Power block | Home run JB-GCB-ST-DI01 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-GCB-ST-DI01 | GCB-ST | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 366 | 111
A-I-0145 | A | Power block | Analog instrument to JB JB-GFM-1-AI01: 15 x 1 pr (field cables) | GFM-1 | GFM-1: GT1 gas fuel module (stop / control valves, final strainer) | JB-GFM-1-AI01 | GFM-1: GT1 gas fuel module (stop / control valves, final strainer) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 15 | 1 |  |  |  | Tray / conduit | 70 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0146 | A | Power block | Home run JB-GFM-1-AI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GFM-1-AI01 | GFM-1: GT1 gas fuel module (stop / control valves, final strainer) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 220 | 94
A-I-0147 | A | Power block | Discrete device to JB JB-GFM-1-DI01: 15 x 1 pr (field cables) | GFM-1 | GFM-1: GT1 gas fuel module (stop / control valves, final strainer) | JB-GFM-1-DI01 | GFM-1: GT1 gas fuel module (stop / control valves, final strainer) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 15 | 1 |  |  |  | Tray / conduit | 70 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0148 | A | Power block | Home run JB-GFM-1-DI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GFM-1-DI01 | GFM-1: GT1 gas fuel module (stop / control valves, final strainer) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 220 | 94
A-I-0149 | A | Power block | Analog instrument to JB JB-GFM-2-AI01: 15 x 1 pr (field cables) | GFM-2 | GFM-2: GT2 gas fuel module (stop / control valves, final strainer) | JB-GFM-2-AI01 | GFM-2: GT2 gas fuel module (stop / control valves, final strainer) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 15 | 1 |  |  |  | Tray / conduit | 70 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0150 | A | Power block | Home run JB-GFM-2-AI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GFM-2-AI01 | GFM-2: GT2 gas fuel module (stop / control valves, final strainer) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1124 | 188
A-I-0151 | A | Power block | Discrete device to JB JB-GFM-2-DI01: 15 x 1 pr (field cables) | GFM-2 | GFM-2: GT2 gas fuel module (stop / control valves, final strainer) | JB-GFM-2-DI01 | GFM-2: GT2 gas fuel module (stop / control valves, final strainer) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 15 | 1 |  |  |  | Tray / conduit | 70 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0152 | A | Power block | Home run JB-GFM-2-DI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GFM-2-DI01 | GFM-2: GT2 gas fuel module (stop / control valves, final strainer) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1124 | 188
A-I-0153 | A | Power block | Analog instrument to JB JB-GFM-3-AI01: 15 x 1 pr (field cables) | GFM-3 | GFM-3: GT3 gas fuel module (stop / control valves, final strainer) | JB-GFM-3-AI01 | GFM-3: GT3 gas fuel module (stop / control valves, final strainer) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 15 | 1 |  |  |  | Tray / conduit | 70 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0154 | A | Power block | Home run JB-GFM-3-AI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GFM-3-AI01 | GFM-3: GT3 gas fuel module (stop / control valves, final strainer) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 896 | 212
A-I-0155 | A | Power block | Discrete device to JB JB-GFM-3-DI01: 15 x 1 pr (field cables) | GFM-3 | GFM-3: GT3 gas fuel module (stop / control valves, final strainer) | JB-GFM-3-DI01 | GFM-3: GT3 gas fuel module (stop / control valves, final strainer) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 15 | 1 |  |  |  | Tray / conduit | 70 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0156 | A | Power block | Home run JB-GFM-3-DI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GFM-3-DI01 | GFM-3: GT3 gas fuel module (stop / control valves, final strainer) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 896 | 212
A-I-0157 | A | Power block | Analog instrument to JB JB-GSC-ST-AI01: 6 x 1 pr (field cables) | GSC-ST | GSC-ST: gland-steam condenser and exhausters | JB-GSC-ST-AI01 | GSC-ST: gland-steam condenser and exhausters | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 55 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0158 | A | Power block | Home run JB-GSC-ST-AI01 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-GSC-ST-AI01 | GSC-ST: gland-steam condenser and exhausters | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 72 | 139
A-I-0159 | A | Power block | Discrete device to JB JB-GSC-ST-DI01: 6 x 1 pr (field cables) | GSC-ST | GSC-ST: gland-steam condenser and exhausters | JB-GSC-ST-DI01 | GSC-ST: gland-steam condenser and exhausters | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 55 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0160 | A | Power block | Home run JB-GSC-ST-DI01 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-GSC-ST-DI01 | GSC-ST: gland-steam condenser and exhausters | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 72 | 139
A-I-0161 | A | Power block | Analog instrument to JB JB-GSU-1 firewall-AI01: 8 x 1 pr (field cables) |  | GSU-1 firewall | JB-GSU-1 firewall-AI01 | GSU-1 firewall | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 63 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0162 | A | Power block | Home run JB-GSU-1 firewall-AI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GSU-1 firewall-AI01 | GSU-1 firewall | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 416 | 181
A-I-0163 | A | Power block | Discrete device to JB JB-GSU-1 firewall-DI01: 16 x 1 pr (field cables) |  | GSU-1 firewall | JB-GSU-1 firewall-DI01 | GSU-1 firewall | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 63 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0164 | A | Power block | Home run JB-GSU-1 firewall-DI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GSU-1 firewall-DI01 | GSU-1 firewall | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 416 | 181
A-I-0165 | A | Power block | Analog instrument to JB JB-GSU-1-AI01: 8 x 1 pr (field cables) | GSU-1 | GSU-1: 21/230 kV generator step-up transformer | JB-GSU-1-AI01 | GSU-1: 21/230 kV generator step-up transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 83 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0166 | A | Power block | Home run JB-GSU-1-AI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GSU-1-AI01 | GSU-1: 21/230 kV generator step-up transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 419 | 179
A-I-0167 | A | Power block | Discrete device to JB JB-GSU-1-DI01: 16 x 1 pr (field cables) | GSU-1 | GSU-1: 21/230 kV generator step-up transformer | JB-GSU-1-DI01 | GSU-1: 21/230 kV generator step-up transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 83 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0168 | A | Power block | Home run JB-GSU-1-DI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GSU-1-DI01 | GSU-1: 21/230 kV generator step-up transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 419 | 179
A-I-0169 | A | Power block | Analog instrument to JB JB-GSU-2 firewall-AI01: 8 x 1 pr (field cables) |  | GSU-2 firewall | JB-GSU-2 firewall-AI01 | GSU-2 firewall | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 63 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0170 | A | Power block | Home run JB-GSU-2 firewall-AI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GSU-2 firewall-AI01 | GSU-2 firewall | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1290 | 271
A-I-0171 | A | Power block | Discrete device to JB JB-GSU-2 firewall-DI01: 16 x 1 pr (field cables) |  | GSU-2 firewall | JB-GSU-2 firewall-DI01 | GSU-2 firewall | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 63 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0172 | A | Power block | Home run JB-GSU-2 firewall-DI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GSU-2 firewall-DI01 | GSU-2 firewall | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1290 | 271
A-I-0173 | A | Power block | Analog instrument to JB JB-GSU-2-AI01: 8 x 1 pr (field cables) | GSU-2 | GSU-2: 21/230 kV generator step-up transformer | JB-GSU-2-AI01 | GSU-2: 21/230 kV generator step-up transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 83 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0174 | A | Power block | Home run JB-GSU-2-AI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GSU-2-AI01 | GSU-2: 21/230 kV generator step-up transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1423 | 113
A-I-0175 | A | Power block | Discrete device to JB JB-GSU-2-DI01: 16 x 1 pr (field cables) | GSU-2 | GSU-2: 21/230 kV generator step-up transformer | JB-GSU-2-DI01 | GSU-2: 21/230 kV generator step-up transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 83 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0176 | A | Power block | Home run JB-GSU-2-DI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GSU-2-DI01 | GSU-2: 21/230 kV generator step-up transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1423 | 113
A-I-0177 | A | Power block | Analog instrument to JB JB-GSU-3 firewall-AI01: 8 x 1 pr (field cables) |  | GSU-3 firewall | JB-GSU-3 firewall-AI01 | GSU-3 firewall | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 63 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0178 | A | Power block | Home run JB-GSU-3 firewall-AI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GSU-3 firewall-AI01 | GSU-3 firewall | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1140 | 110
A-I-0179 | A | Power block | Discrete device to JB JB-GSU-3 firewall-DI01: 16 x 1 pr (field cables) |  | GSU-3 firewall | JB-GSU-3 firewall-DI01 | GSU-3 firewall | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 63 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0180 | A | Power block | Home run JB-GSU-3 firewall-DI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GSU-3 firewall-DI01 | GSU-3 firewall | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1140 | 110
A-I-0181 | A | Power block | Analog instrument to JB JB-GSU-3-AI01: 8 x 1 pr (field cables) | GSU-3 | GSU-3: 21/230 kV generator step-up transformer | JB-GSU-3-AI01 | GSU-3: 21/230 kV generator step-up transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 83 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0182 | A | Power block | Home run JB-GSU-3-AI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GSU-3-AI01 | GSU-3: 21/230 kV generator step-up transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1103 | 113
A-I-0183 | A | Power block | Discrete device to JB JB-GSU-3-DI01: 16 x 1 pr (field cables) | GSU-3 | GSU-3: 21/230 kV generator step-up transformer | JB-GSU-3-DI01 | GSU-3: 21/230 kV generator step-up transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 83 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0184 | A | Power block | Home run JB-GSU-3-DI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GSU-3-DI01 | GSU-3: 21/230 kV generator step-up transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1103 | 113
A-I-0185 | A | Power block | Analog instrument to JB JB-GSU-ST firewall-AI01: 8 x 1 pr (field cables) |  | GSU-ST firewall | JB-GSU-ST firewall-AI01 | GSU-ST firewall | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 63 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0186 | A | Power block | Home run JB-GSU-ST firewall-AI01 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-GSU-ST firewall-AI01 | GSU-ST firewall | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 463 | 35
A-I-0187 | A | Power block | Discrete device to JB JB-GSU-ST firewall-DI01: 16 x 1 pr (field cables) |  | GSU-ST firewall | JB-GSU-ST firewall-DI01 | GSU-ST firewall | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 63 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0188 | A | Power block | Home run JB-GSU-ST firewall-DI01 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-GSU-ST firewall-DI01 | GSU-ST firewall | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 463 | 35
A-I-0189 | A | Power block | Analog instrument to JB JB-GSU-ST-AI01: 8 x 1 pr (field cables) | GSU-ST | GSU-ST: 21/230 kV (one ST GSU, baseline) | JB-GSU-ST-AI01 | GSU-ST: 21/230 kV (one ST GSU, baseline) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 89 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0190 | A | Power block | Home run JB-GSU-ST-AI01 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-GSU-ST-AI01 | GSU-ST: 21/230 kV (one ST GSU, baseline) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 408 | 32
A-I-0191 | A | Power block | Discrete device to JB JB-GSU-ST-DI01: 16 x 1 pr (field cables) | GSU-ST | GSU-ST: 21/230 kV (one ST GSU, baseline) | JB-GSU-ST-DI01 | GSU-ST: 21/230 kV (one ST GSU, baseline) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 89 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0192 | A | Power block | Home run JB-GSU-ST-DI01 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-GSU-ST-DI01 | GSU-ST: 21/230 kV (one ST GSU, baseline) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 408 | 32
A-I-0193 | A | Power block | Analog instrument to JB JB-GT1 aux-AI01: 20 x 1 pr (field cables) | GT1 aux | GT1 aux: lube oil, hydraulics, enclosure fans | JB-GT1 aux-AI01 | GT1 aux: lube oil, hydraulics, enclosure fans | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 62 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0194 | A | Power block | Home run JB-GT1 aux-AI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT1 aux-AI01 | GT1 aux: lube oil, hydraulics, enclosure fans | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 224 | 119
A-I-0195 | A | Power block | Analog instrument to JB JB-GT1 aux-AI02: 20 x 1 pr (field cables) | GT1 aux | GT1 aux: lube oil, hydraulics, enclosure fans | JB-GT1 aux-AI02 | GT1 aux: lube oil, hydraulics, enclosure fans | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 62 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0196 | A | Power block | Home run JB-GT1 aux-AI02 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT1 aux-AI02 | GT1 aux: lube oil, hydraulics, enclosure fans | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 224 | 119
A-I-0197 | A | Power block | Discrete device to JB JB-GT1 aux-DI01: 20 x 1 pr (field cables) | GT1 aux | GT1 aux: lube oil, hydraulics, enclosure fans | JB-GT1 aux-DI01 | GT1 aux: lube oil, hydraulics, enclosure fans | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 62 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0198 | A | Power block | Home run JB-GT1 aux-DI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT1 aux-DI01 | GT1 aux: lube oil, hydraulics, enclosure fans | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 224 | 119
A-I-0199 | A | Power block | Discrete device to JB JB-GT1 aux-DI02: 20 x 1 pr (field cables) | GT1 aux | GT1 aux: lube oil, hydraulics, enclosure fans | JB-GT1 aux-DI02 | GT1 aux: lube oil, hydraulics, enclosure fans | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 62 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0200 | A | Power block | Home run JB-GT1 aux-DI02 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT1 aux-DI02 | GT1 aux: lube oil, hydraulics, enclosure fans | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 224 | 119
A-I-0201 | A | Power block | Analog instrument to JB JB-INL-1-AI01: 6 x 1 pr (field cables) | INL-1 | GT1 inlet duct (drop + horizontal EL 23-37) | JB-INL-1-AI01 | GT1 inlet duct (drop + horizontal EL 23-37) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 132 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0202 | A | Power block | Home run JB-INL-1-AI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-INL-1-AI01 | GT1 inlet duct (drop + horizontal EL 23-37) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 359 | 109
A-I-0203 | A | Power block | Thermocouple to TC JB JB-INL-1-TC01: 4 x 1 pr (field cables) | INL-1 | GT1 inlet duct (drop + horizontal EL 23-37) | JB-INL-1-TC01 | GT1 inlet duct (drop + horizontal EL 23-37) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 132 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0204 | A | Power block | Home run JB-INL-1-TC01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-INL-1-TC01 | GT1 inlet duct (drop + horizontal EL 23-37) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Tray | 359 | 109
A-I-0205 | A | Power block | Analog instrument to JB JB-GT1-AI01: 20 x 1 pr (field cables) | GT1 | GT1: H-class gas turbine (60 Hz) | JB-GT1-AI01 | GT1: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0206 | A | Power block | Home run JB-GT1-AI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT1-AI01 | GT1: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 154 | 103
A-I-0207 | A | Power block | Analog instrument to JB JB-GT1-AI02: 20 x 1 pr (field cables) | GT1 | GT1: H-class gas turbine (60 Hz) | JB-GT1-AI02 | GT1: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0208 | A | Power block | Home run JB-GT1-AI02 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT1-AI02 | GT1: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 154 | 103
A-I-0209 | A | Power block | Analog instrument to JB JB-GT1-AI03: 20 x 1 pr (field cables) | GT1 | GT1: H-class gas turbine (60 Hz) | JB-GT1-AI03 | GT1: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0210 | A | Power block | Home run JB-GT1-AI03 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT1-AI03 | GT1: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 154 | 103
A-I-0211 | A | Power block | Analog instrument to JB JB-GT1-AI04: 20 x 1 pr (field cables) | GT1 | GT1: H-class gas turbine (60 Hz) | JB-GT1-AI04 | GT1: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0212 | A | Power block | Home run JB-GT1-AI04 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT1-AI04 | GT1: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 154 | 103
A-I-0213 | A | Power block | Analog instrument to JB JB-GT1-AI05: 20 x 1 pr (field cables) | GT1 | GT1: H-class gas turbine (60 Hz) | JB-GT1-AI05 | GT1: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0214 | A | Power block | Home run JB-GT1-AI05 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT1-AI05 | GT1: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 154 | 103
A-I-0215 | A | Power block | Analog instrument to JB JB-GT1-AI06: 20 x 1 pr (field cables) | GT1 | GT1: H-class gas turbine (60 Hz) | JB-GT1-AI06 | GT1: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0216 | A | Power block | Home run JB-GT1-AI06 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT1-AI06 | GT1: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 154 | 103
A-I-0217 | A | Power block | Discrete device to JB JB-GT1-DI01: 20 x 1 pr (field cables) | GT1 | GT1: H-class gas turbine (60 Hz) | JB-GT1-DI01 | GT1: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0218 | A | Power block | Home run JB-GT1-DI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT1-DI01 | GT1: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 154 | 103
A-I-0219 | A | Power block | Discrete device to JB JB-GT1-DI02: 20 x 1 pr (field cables) | GT1 | GT1: H-class gas turbine (60 Hz) | JB-GT1-DI02 | GT1: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0220 | A | Power block | Home run JB-GT1-DI02 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT1-DI02 | GT1: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 154 | 103
A-I-0221 | A | Power block | Discrete device to JB JB-GT1-DI03: 20 x 1 pr (field cables) | GT1 | GT1: H-class gas turbine (60 Hz) | JB-GT1-DI03 | GT1: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0222 | A | Power block | Home run JB-GT1-DI03 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT1-DI03 | GT1: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 154 | 103
A-I-0223 | A | Power block | Discrete device to JB JB-GT1-DI04: 20 x 1 pr (field cables) | GT1 | GT1: H-class gas turbine (60 Hz) | JB-GT1-DI04 | GT1: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0224 | A | Power block | Home run JB-GT1-DI04 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT1-DI04 | GT1: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 154 | 103
A-I-0225 | A | Power block | Thermocouple to TC JB JB-GT1-TC01: 20 x 1 pr (field cables) | GT1 | GT1: H-class gas turbine (60 Hz) | JB-GT1-TC01 | GT1: H-class gas turbine (60 Hz) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0226 | A | Power block | Home run JB-GT1-TC01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT1-TC01 | GT1: H-class gas turbine (60 Hz) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Tray | 154 | 103
A-I-0227 | A | Power block | Thermocouple to TC JB JB-GT1-TC02: 20 x 1 pr (field cables) | GT1 | GT1: H-class gas turbine (60 Hz) | JB-GT1-TC02 | GT1: H-class gas turbine (60 Hz) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0228 | A | Power block | Home run JB-GT1-TC02 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT1-TC02 | GT1: H-class gas turbine (60 Hz) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Tray | 154 | 103
A-I-0229 | A | Power block | Thermocouple to TC JB JB-GT1-TC03: 20 x 1 pr (field cables) | GT1 | GT1: H-class gas turbine (60 Hz) | JB-GT1-TC03 | GT1: H-class gas turbine (60 Hz) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0230 | A | Power block | Home run JB-GT1-TC03 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT1-TC03 | GT1: H-class gas turbine (60 Hz) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Tray | 154 | 103
A-I-0231 | A | Power block | Vibration monitoring | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | GT1 | GT1: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 154 | 103
A-I-0232 | A | Power block | Analog instrument to JB JB-GT2 aux-AI01: 20 x 1 pr (field cables) | GT2 aux | GT2 aux: lube oil, hydraulics, enclosure fans | JB-GT2 aux-AI01 | GT2 aux: lube oil, hydraulics, enclosure fans | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 62 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0233 | A | Power block | Home run JB-GT2 aux-AI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT2 aux-AI01 | GT2 aux: lube oil, hydraulics, enclosure fans | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1116 | 213
A-I-0234 | A | Power block | Analog instrument to JB JB-GT2 aux-AI02: 20 x 1 pr (field cables) | GT2 aux | GT2 aux: lube oil, hydraulics, enclosure fans | JB-GT2 aux-AI02 | GT2 aux: lube oil, hydraulics, enclosure fans | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 62 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0235 | A | Power block | Home run JB-GT2 aux-AI02 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT2 aux-AI02 | GT2 aux: lube oil, hydraulics, enclosure fans | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1116 | 213
A-I-0236 | A | Power block | Discrete device to JB JB-GT2 aux-DI01: 20 x 1 pr (field cables) | GT2 aux | GT2 aux: lube oil, hydraulics, enclosure fans | JB-GT2 aux-DI01 | GT2 aux: lube oil, hydraulics, enclosure fans | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 62 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0237 | A | Power block | Home run JB-GT2 aux-DI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT2 aux-DI01 | GT2 aux: lube oil, hydraulics, enclosure fans | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1116 | 213
A-I-0238 | A | Power block | Discrete device to JB JB-GT2 aux-DI02: 20 x 1 pr (field cables) | GT2 aux | GT2 aux: lube oil, hydraulics, enclosure fans | JB-GT2 aux-DI02 | GT2 aux: lube oil, hydraulics, enclosure fans | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 62 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0239 | A | Power block | Home run JB-GT2 aux-DI02 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT2 aux-DI02 | GT2 aux: lube oil, hydraulics, enclosure fans | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1116 | 213
A-I-0240 | A | Power block | Analog instrument to JB JB-INL-2-AI01: 6 x 1 pr (field cables) | INL-2 | GT2 inlet duct (drop + horizontal EL 23-37) | JB-INL-2-AI01 | GT2 inlet duct (drop + horizontal EL 23-37) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 132 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0241 | A | Power block | Home run JB-INL-2-AI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-INL-2-AI01 | GT2 inlet duct (drop + horizontal EL 23-37) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1233 | 199
A-I-0242 | A | Power block | Thermocouple to TC JB JB-INL-2-TC01: 4 x 1 pr (field cables) | INL-2 | GT2 inlet duct (drop + horizontal EL 23-37) | JB-INL-2-TC01 | GT2 inlet duct (drop + horizontal EL 23-37) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 132 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0243 | A | Power block | Home run JB-INL-2-TC01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-INL-2-TC01 | GT2 inlet duct (drop + horizontal EL 23-37) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Tray | 1233 | 199
A-I-0244 | A | Power block | Analog instrument to JB JB-GT2-AI01: 20 x 1 pr (field cables) | GT2 | GT2: H-class gas turbine (60 Hz) | JB-GT2-AI01 | GT2: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0245 | A | Power block | Home run JB-GT2-AI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT2-AI01 | GT2: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1046 | 197
A-I-0246 | A | Power block | Analog instrument to JB JB-GT2-AI02: 20 x 1 pr (field cables) | GT2 | GT2: H-class gas turbine (60 Hz) | JB-GT2-AI02 | GT2: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0247 | A | Power block | Home run JB-GT2-AI02 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT2-AI02 | GT2: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1046 | 197
A-I-0248 | A | Power block | Analog instrument to JB JB-GT2-AI03: 20 x 1 pr (field cables) | GT2 | GT2: H-class gas turbine (60 Hz) | JB-GT2-AI03 | GT2: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0249 | A | Power block | Home run JB-GT2-AI03 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT2-AI03 | GT2: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1046 | 197
A-I-0250 | A | Power block | Analog instrument to JB JB-GT2-AI04: 20 x 1 pr (field cables) | GT2 | GT2: H-class gas turbine (60 Hz) | JB-GT2-AI04 | GT2: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0251 | A | Power block | Home run JB-GT2-AI04 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT2-AI04 | GT2: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1046 | 197
A-I-0252 | A | Power block | Analog instrument to JB JB-GT2-AI05: 20 x 1 pr (field cables) | GT2 | GT2: H-class gas turbine (60 Hz) | JB-GT2-AI05 | GT2: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0253 | A | Power block | Home run JB-GT2-AI05 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT2-AI05 | GT2: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1046 | 197
A-I-0254 | A | Power block | Analog instrument to JB JB-GT2-AI06: 20 x 1 pr (field cables) | GT2 | GT2: H-class gas turbine (60 Hz) | JB-GT2-AI06 | GT2: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0255 | A | Power block | Home run JB-GT2-AI06 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT2-AI06 | GT2: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1046 | 197
A-I-0256 | A | Power block | Discrete device to JB JB-GT2-DI01: 20 x 1 pr (field cables) | GT2 | GT2: H-class gas turbine (60 Hz) | JB-GT2-DI01 | GT2: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0257 | A | Power block | Home run JB-GT2-DI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT2-DI01 | GT2: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1046 | 197
A-I-0258 | A | Power block | Discrete device to JB JB-GT2-DI02: 20 x 1 pr (field cables) | GT2 | GT2: H-class gas turbine (60 Hz) | JB-GT2-DI02 | GT2: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0259 | A | Power block | Home run JB-GT2-DI02 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT2-DI02 | GT2: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1046 | 197
A-I-0260 | A | Power block | Discrete device to JB JB-GT2-DI03: 20 x 1 pr (field cables) | GT2 | GT2: H-class gas turbine (60 Hz) | JB-GT2-DI03 | GT2: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0261 | A | Power block | Home run JB-GT2-DI03 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT2-DI03 | GT2: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1046 | 197
A-I-0262 | A | Power block | Discrete device to JB JB-GT2-DI04: 20 x 1 pr (field cables) | GT2 | GT2: H-class gas turbine (60 Hz) | JB-GT2-DI04 | GT2: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0263 | A | Power block | Home run JB-GT2-DI04 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT2-DI04 | GT2: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1046 | 197
A-I-0264 | A | Power block | Thermocouple to TC JB JB-GT2-TC01: 20 x 1 pr (field cables) | GT2 | GT2: H-class gas turbine (60 Hz) | JB-GT2-TC01 | GT2: H-class gas turbine (60 Hz) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0265 | A | Power block | Home run JB-GT2-TC01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT2-TC01 | GT2: H-class gas turbine (60 Hz) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Tray | 1046 | 197
A-I-0266 | A | Power block | Thermocouple to TC JB JB-GT2-TC02: 20 x 1 pr (field cables) | GT2 | GT2: H-class gas turbine (60 Hz) | JB-GT2-TC02 | GT2: H-class gas turbine (60 Hz) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0267 | A | Power block | Home run JB-GT2-TC02 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT2-TC02 | GT2: H-class gas turbine (60 Hz) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Tray | 1046 | 197
A-I-0268 | A | Power block | Thermocouple to TC JB JB-GT2-TC03: 20 x 1 pr (field cables) | GT2 | GT2: H-class gas turbine (60 Hz) | JB-GT2-TC03 | GT2: H-class gas turbine (60 Hz) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0269 | A | Power block | Home run JB-GT2-TC03 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT2-TC03 | GT2: H-class gas turbine (60 Hz) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Tray | 1046 | 197
A-I-0270 | A | Power block | Vibration monitoring | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | GT2 | GT2: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 1046 | 197
A-I-0271 | A | Power block | Analog instrument to JB JB-GT3 aux-AI01: 20 x 1 pr (field cables) | GT3 aux | GT3 aux: lube oil, hydraulics, enclosure fans | JB-GT3 aux-AI01 | GT3 aux: lube oil, hydraulics, enclosure fans | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 62 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0272 | A | Power block | Home run JB-GT3 aux-AI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT3 aux-AI01 | GT3 aux: lube oil, hydraulics, enclosure fans | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 926 | 248
A-I-0273 | A | Power block | Analog instrument to JB JB-GT3 aux-AI02: 20 x 1 pr (field cables) | GT3 aux | GT3 aux: lube oil, hydraulics, enclosure fans | JB-GT3 aux-AI02 | GT3 aux: lube oil, hydraulics, enclosure fans | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 62 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0274 | A | Power block | Home run JB-GT3 aux-AI02 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT3 aux-AI02 | GT3 aux: lube oil, hydraulics, enclosure fans | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 926 | 248
A-I-0275 | A | Power block | Discrete device to JB JB-GT3 aux-DI01: 20 x 1 pr (field cables) | GT3 aux | GT3 aux: lube oil, hydraulics, enclosure fans | JB-GT3 aux-DI01 | GT3 aux: lube oil, hydraulics, enclosure fans | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 62 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0276 | A | Power block | Home run JB-GT3 aux-DI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT3 aux-DI01 | GT3 aux: lube oil, hydraulics, enclosure fans | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 926 | 248
A-I-0277 | A | Power block | Discrete device to JB JB-GT3 aux-DI02: 20 x 1 pr (field cables) | GT3 aux | GT3 aux: lube oil, hydraulics, enclosure fans | JB-GT3 aux-DI02 | GT3 aux: lube oil, hydraulics, enclosure fans | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 62 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0278 | A | Power block | Home run JB-GT3 aux-DI02 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT3 aux-DI02 | GT3 aux: lube oil, hydraulics, enclosure fans | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 926 | 248
A-I-0279 | A | Power block | Analog instrument to JB JB-INL-3-AI01: 6 x 1 pr (field cables) | INL-3 | GT3 inlet duct (drop + horizontal EL 23-37) | JB-INL-3-AI01 | GT3 inlet duct (drop + horizontal EL 23-37) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 132 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0280 | A | Power block | Home run JB-INL-3-AI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-INL-3-AI01 | GT3 inlet duct (drop + horizontal EL 23-37) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1135 | 96
A-I-0281 | A | Power block | Thermocouple to TC JB JB-INL-3-TC01: 4 x 1 pr (field cables) | INL-3 | GT3 inlet duct (drop + horizontal EL 23-37) | JB-INL-3-TC01 | GT3 inlet duct (drop + horizontal EL 23-37) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 132 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0282 | A | Power block | Home run JB-INL-3-TC01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-INL-3-TC01 | GT3 inlet duct (drop + horizontal EL 23-37) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Duct bank | 1135 | 96
A-I-0283 | A | Power block | Analog instrument to JB JB-GT3-AI01: 20 x 1 pr (field cables) | GT3 | GT3: H-class gas turbine (60 Hz) | JB-GT3-AI01 | GT3: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0284 | A | Power block | Home run JB-GT3-AI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT3-AI01 | GT3: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 986 | 249
A-I-0285 | A | Power block | Analog instrument to JB JB-GT3-AI02: 20 x 1 pr (field cables) | GT3 | GT3: H-class gas turbine (60 Hz) | JB-GT3-AI02 | GT3: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0286 | A | Power block | Home run JB-GT3-AI02 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT3-AI02 | GT3: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 986 | 249
A-I-0287 | A | Power block | Analog instrument to JB JB-GT3-AI03: 20 x 1 pr (field cables) | GT3 | GT3: H-class gas turbine (60 Hz) | JB-GT3-AI03 | GT3: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0288 | A | Power block | Home run JB-GT3-AI03 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT3-AI03 | GT3: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 986 | 249
A-I-0289 | A | Power block | Analog instrument to JB JB-GT3-AI04: 20 x 1 pr (field cables) | GT3 | GT3: H-class gas turbine (60 Hz) | JB-GT3-AI04 | GT3: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0290 | A | Power block | Home run JB-GT3-AI04 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT3-AI04 | GT3: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 986 | 249
A-I-0291 | A | Power block | Analog instrument to JB JB-GT3-AI05: 20 x 1 pr (field cables) | GT3 | GT3: H-class gas turbine (60 Hz) | JB-GT3-AI05 | GT3: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0292 | A | Power block | Home run JB-GT3-AI05 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT3-AI05 | GT3: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 986 | 249
A-I-0293 | A | Power block | Analog instrument to JB JB-GT3-AI06: 20 x 1 pr (field cables) | GT3 | GT3: H-class gas turbine (60 Hz) | JB-GT3-AI06 | GT3: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0294 | A | Power block | Home run JB-GT3-AI06 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT3-AI06 | GT3: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 986 | 249
A-I-0295 | A | Power block | Discrete device to JB JB-GT3-DI01: 20 x 1 pr (field cables) | GT3 | GT3: H-class gas turbine (60 Hz) | JB-GT3-DI01 | GT3: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0296 | A | Power block | Home run JB-GT3-DI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT3-DI01 | GT3: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 986 | 249
A-I-0297 | A | Power block | Discrete device to JB JB-GT3-DI02: 20 x 1 pr (field cables) | GT3 | GT3: H-class gas turbine (60 Hz) | JB-GT3-DI02 | GT3: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0298 | A | Power block | Home run JB-GT3-DI02 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT3-DI02 | GT3: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 986 | 249
A-I-0299 | A | Power block | Discrete device to JB JB-GT3-DI03: 20 x 1 pr (field cables) | GT3 | GT3: H-class gas turbine (60 Hz) | JB-GT3-DI03 | GT3: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0300 | A | Power block | Home run JB-GT3-DI03 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT3-DI03 | GT3: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 986 | 249
A-I-0301 | A | Power block | Discrete device to JB JB-GT3-DI04: 20 x 1 pr (field cables) | GT3 | GT3: H-class gas turbine (60 Hz) | JB-GT3-DI04 | GT3: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0302 | A | Power block | Home run JB-GT3-DI04 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT3-DI04 | GT3: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 986 | 249
A-I-0303 | A | Power block | Thermocouple to TC JB JB-GT3-TC01: 20 x 1 pr (field cables) | GT3 | GT3: H-class gas turbine (60 Hz) | JB-GT3-TC01 | GT3: H-class gas turbine (60 Hz) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0304 | A | Power block | Home run JB-GT3-TC01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT3-TC01 | GT3: H-class gas turbine (60 Hz) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Tray | 986 | 249
A-I-0305 | A | Power block | Thermocouple to TC JB JB-GT3-TC02: 20 x 1 pr (field cables) | GT3 | GT3: H-class gas turbine (60 Hz) | JB-GT3-TC02 | GT3: H-class gas turbine (60 Hz) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0306 | A | Power block | Home run JB-GT3-TC02 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT3-TC02 | GT3: H-class gas turbine (60 Hz) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Tray | 986 | 249
A-I-0307 | A | Power block | Thermocouple to TC JB JB-GT3-TC03: 20 x 1 pr (field cables) | GT3 | GT3: H-class gas turbine (60 Hz) | JB-GT3-TC03 | GT3: H-class gas turbine (60 Hz) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 96 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0308 | A | Power block | Home run JB-GT3-TC03 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GT3-TC03 | GT3: H-class gas turbine (60 Hz) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Tray | 986 | 249
A-I-0309 | A | Power block | Vibration monitoring | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | GT3 | GT3: H-class gas turbine (60 Hz) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 986 | 249
A-I-0310 | A | Power block | Analog instrument to JB JB-GTG-1-AI01: 20 x 1 pr (field cables) | GTG-1 | GTG-1: GT generator | JB-GTG-1-AI01 | GTG-1: GT generator | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 70 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0311 | A | Power block | Home run JB-GTG-1-AI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GTG-1-AI01 | GTG-1: GT generator | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 367 | 127
A-I-0312 | A | Power block | Discrete device to JB JB-GTG-1-DI01: 20 x 1 pr (field cables) | GTG-1 | GTG-1: GT generator | JB-GTG-1-DI01 | GTG-1: GT generator | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 70 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0313 | A | Power block | Home run JB-GTG-1-DI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GTG-1-DI01 | GTG-1: GT generator | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 367 | 127
A-I-0314 | A | Power block | RTD to JB JB-GTG-1-RTD01: 10 x 1 tri (field cables) | GTG-1 | GTG-1: GT generator | JB-GTG-1-RTD01 | GTG-1: GT generator | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 70 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0315 | A | Power block | Home run JB-GTG-1-RTD01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GTG-1-RTD01 | GTG-1: GT generator | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Tray | 367 | 127
A-I-0316 | A | Power block | RTD to JB JB-GTG-1-RTD02: 10 x 1 tri (field cables) | GTG-1 | GTG-1: GT generator | JB-GTG-1-RTD02 | GTG-1: GT generator | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 70 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0317 | A | Power block | Home run JB-GTG-1-RTD02 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GTG-1-RTD02 | GTG-1: GT generator | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Tray | 367 | 127
A-I-0318 | A | Power block | RTD to JB JB-GTG-1-RTD03: 4 x 1 tri (field cables) | GTG-1 | GTG-1: GT generator | JB-GTG-1-RTD03 | GTG-1: GT generator | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 4 | 1 |  |  |  | Tray / conduit | 70 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0319 | A | Power block | Home run JB-GTG-1-RTD03 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-GTG-1-RTD03 | GTG-1: GT generator | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Tray | 367 | 127
A-I-0320 | A | Power block | Vibration monitoring | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | GTG-1 | GTG-1: GT generator | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 367 | 127
A-I-0321 | A | Power block | Analog instrument to JB JB-GTG-2-AI01: 20 x 1 pr (field cables) | GTG-2 | GTG-2: GT generator | JB-GTG-2-AI01 | GTG-2: GT generator | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 70 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0322 | A | Power block | Home run JB-GTG-2-AI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GTG-2-AI01 | GTG-2: GT generator | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1241 | 217
A-I-0323 | A | Power block | Discrete device to JB JB-GTG-2-DI01: 20 x 1 pr (field cables) | GTG-2 | GTG-2: GT generator | JB-GTG-2-DI01 | GTG-2: GT generator | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 70 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0324 | A | Power block | Home run JB-GTG-2-DI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GTG-2-DI01 | GTG-2: GT generator | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1241 | 217
A-I-0325 | A | Power block | RTD to JB JB-GTG-2-RTD01: 10 x 1 tri (field cables) | GTG-2 | GTG-2: GT generator | JB-GTG-2-RTD01 | GTG-2: GT generator | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 70 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0326 | A | Power block | Home run JB-GTG-2-RTD01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GTG-2-RTD01 | GTG-2: GT generator | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Tray | 1241 | 217
A-I-0327 | A | Power block | RTD to JB JB-GTG-2-RTD02: 10 x 1 tri (field cables) | GTG-2 | GTG-2: GT generator | JB-GTG-2-RTD02 | GTG-2: GT generator | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 70 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0328 | A | Power block | Home run JB-GTG-2-RTD02 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GTG-2-RTD02 | GTG-2: GT generator | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Tray | 1241 | 217
A-I-0329 | A | Power block | RTD to JB JB-GTG-2-RTD03: 4 x 1 tri (field cables) | GTG-2 | GTG-2: GT generator | JB-GTG-2-RTD03 | GTG-2: GT generator | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 4 | 1 |  |  |  | Tray / conduit | 70 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0330 | A | Power block | Home run JB-GTG-2-RTD03 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-GTG-2-RTD03 | GTG-2: GT generator | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Tray | 1241 | 217
A-I-0331 | A | Power block | Vibration monitoring | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | GTG-2 | GTG-2: GT generator | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 1241 | 217
A-I-0332 | A | Power block | Analog instrument to JB JB-GTG-3-AI01: 20 x 1 pr (field cables) | GTG-3 | GTG-3: GT generator | JB-GTG-3-AI01 | GTG-3: GT generator | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 70 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0333 | A | Power block | Home run JB-GTG-3-AI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GTG-3-AI01 | GTG-3: GT generator | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1193 | 117
A-I-0334 | A | Power block | Discrete device to JB JB-GTG-3-DI01: 20 x 1 pr (field cables) | GTG-3 | GTG-3: GT generator | JB-GTG-3-DI01 | GTG-3: GT generator | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 70 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0335 | A | Power block | Home run JB-GTG-3-DI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GTG-3-DI01 | GTG-3: GT generator | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1193 | 117
A-I-0336 | A | Power block | RTD to JB JB-GTG-3-RTD01: 10 x 1 tri (field cables) | GTG-3 | GTG-3: GT generator | JB-GTG-3-RTD01 | GTG-3: GT generator | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 70 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0337 | A | Power block | Home run JB-GTG-3-RTD01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GTG-3-RTD01 | GTG-3: GT generator | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 1193 | 117
A-I-0338 | A | Power block | RTD to JB JB-GTG-3-RTD02: 10 x 1 tri (field cables) | GTG-3 | GTG-3: GT generator | JB-GTG-3-RTD02 | GTG-3: GT generator | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 70 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0339 | A | Power block | Home run JB-GTG-3-RTD02 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GTG-3-RTD02 | GTG-3: GT generator | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 1193 | 117
A-I-0340 | A | Power block | RTD to JB JB-GTG-3-RTD03: 4 x 1 tri (field cables) | GTG-3 | GTG-3: GT generator | JB-GTG-3-RTD03 | GTG-3: GT generator | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 4 | 1 |  |  |  | Tray / conduit | 70 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0341 | A | Power block | Home run JB-GTG-3-RTD03 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-GTG-3-RTD03 | GTG-3: GT generator | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 1193 | 117
A-I-0342 | A | Power block | Vibration monitoring | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | GTG-3 | GTG-3: GT generator | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1193 | 117
A-I-0343 | A | Power block | Analog instrument to JB JB-HRSG-1-AI01: 20 x 1 pr (field cables) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | JB-HRSG-1-AI01 | HRSG 1 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0344 | A | Power block | Home run JB-HRSG-1-AI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-1-AI01 | HRSG 1 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 87
A-I-0345 | A | Power block | Analog instrument to JB JB-HRSG-1-AI02: 20 x 1 pr (field cables) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | JB-HRSG-1-AI02 | HRSG 1 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0346 | A | Power block | Home run JB-HRSG-1-AI02 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-1-AI02 | HRSG 1 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 87
A-I-0347 | A | Power block | Analog instrument to JB JB-HRSG-1-AI03: 20 x 1 pr (field cables) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | JB-HRSG-1-AI03 | HRSG 1 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0348 | A | Power block | Home run JB-HRSG-1-AI03 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-1-AI03 | HRSG 1 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 87
A-I-0349 | A | Power block | Analog instrument to JB JB-HRSG-1-AI04: 20 x 1 pr (field cables) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | JB-HRSG-1-AI04 | HRSG 1 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0350 | A | Power block | Home run JB-HRSG-1-AI04 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-1-AI04 | HRSG 1 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 87
A-I-0351 | A | Power block | Analog instrument to JB JB-HRSG-1-AI05: 20 x 1 pr (field cables) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | JB-HRSG-1-AI05 | HRSG 1 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0352 | A | Power block | Home run JB-HRSG-1-AI05 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-1-AI05 | HRSG 1 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 87
A-I-0353 | A | Power block | Analog instrument to JB JB-HRSG-1-AI06: 20 x 1 pr (field cables) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | JB-HRSG-1-AI06 | HRSG 1 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0354 | A | Power block | Home run JB-HRSG-1-AI06 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-1-AI06 | HRSG 1 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 87
A-I-0355 | A | Power block | Analog instrument to JB JB-HRSG-1-AI07: 20 x 1 pr (field cables) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | JB-HRSG-1-AI07 | HRSG 1 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0356 | A | Power block | Home run JB-HRSG-1-AI07 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-1-AI07 | HRSG 1 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 87
A-I-0357 | A | Power block | Analog instrument to JB JB-HRSG-1-AI08: 20 x 1 pr (field cables) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | JB-HRSG-1-AI08 | HRSG 1 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0358 | A | Power block | Home run JB-HRSG-1-AI08 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-1-AI08 | HRSG 1 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 87
A-I-0359 | A | Power block | Discrete device to JB JB-HRSG-1-DI01: 20 x 1 pr (field cables) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | JB-HRSG-1-DI01 | HRSG 1 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0360 | A | Power block | Home run JB-HRSG-1-DI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-1-DI01 | HRSG 1 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 87
A-I-0361 | A | Power block | Discrete device to JB JB-HRSG-1-DI02: 20 x 1 pr (field cables) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | JB-HRSG-1-DI02 | HRSG 1 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0362 | A | Power block | Home run JB-HRSG-1-DI02 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-1-DI02 | HRSG 1 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 87
A-I-0363 | A | Power block | Discrete device to JB JB-HRSG-1-DI03: 20 x 1 pr (field cables) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | JB-HRSG-1-DI03 | HRSG 1 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0364 | A | Power block | Home run JB-HRSG-1-DI03 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-1-DI03 | HRSG 1 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 87
A-I-0365 | A | Power block | Discrete device to JB JB-HRSG-1-DI04: 20 x 1 pr (field cables) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | JB-HRSG-1-DI04 | HRSG 1 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0366 | A | Power block | Home run JB-HRSG-1-DI04 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-1-DI04 | HRSG 1 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 87
A-I-0367 | A | Power block | Thermocouple to TC JB JB-HRSG-1-TC01: 20 x 1 pr (field cables) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | JB-HRSG-1-TC01 | HRSG 1 + SCR (3P reheat, horizontal) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0368 | A | Power block | Home run JB-HRSG-1-TC01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-1-TC01 | HRSG 1 + SCR (3P reheat, horizontal) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Tray | 0 | 87
A-I-0369 | A | Power block | Thermocouple to TC JB JB-HRSG-1-TC02: 20 x 1 pr (field cables) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | JB-HRSG-1-TC02 | HRSG 1 + SCR (3P reheat, horizontal) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0370 | A | Power block | Home run JB-HRSG-1-TC02 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-1-TC02 | HRSG 1 + SCR (3P reheat, horizontal) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Tray | 0 | 87
A-I-0371 | A | Power block | Thermocouple to TC JB JB-HRSG-1-TC03: 20 x 1 pr (field cables) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | JB-HRSG-1-TC03 | HRSG 1 + SCR (3P reheat, horizontal) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0372 | A | Power block | Home run JB-HRSG-1-TC03 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-1-TC03 | HRSG 1 + SCR (3P reheat, horizontal) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Tray | 0 | 87
A-I-0373 | A | Power block | Thermocouple to TC JB JB-HRSG-1-TC04: 20 x 1 pr (field cables) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | JB-HRSG-1-TC04 | HRSG 1 + SCR (3P reheat, horizontal) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0374 | A | Power block | Home run JB-HRSG-1-TC04 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-1-TC04 | HRSG 1 + SCR (3P reheat, horizontal) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Tray | 0 | 87
A-I-0375 | A | Power block | Analog instrument to JB JB-HRSG 1 blowdown ta-AI01: 6 x 1 pr (field cables) |  | HRSG 1 blowdown tank (continuous / intermittent) | JB-HRSG 1 blowdown ta-AI01 | HRSG 1 blowdown tank (continuous / intermittent) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0376 | A | Power block | Home run JB-HRSG 1 blowdown ta-AI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG 1 blowdown ta-AI01 | HRSG 1 blowdown tank (continuous / intermittent) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 38 | 86
A-I-0377 | A | Power block | Discrete device to JB JB-HRSG 1 blowdown ta-DI01: 4 x 1 pr (field cables) |  | HRSG 1 blowdown tank (continuous / intermittent) | JB-HRSG 1 blowdown ta-DI01 | HRSG 1 blowdown tank (continuous / intermittent) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0378 | A | Power block | Home run JB-HRSG 1 blowdown ta-DI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG 1 blowdown ta-DI01 | HRSG 1 blowdown tank (continuous / intermittent) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 38 | 86
A-I-0379 | A | Power block | Analog instrument to JB JB-HRSG 1 chemical fe-AI01: 8 x 1 pr (field cables) |  | HRSG 1 chemical feed skid (phosphate / amine) | JB-HRSG 1 chemical fe-AI01 | HRSG 1 chemical feed skid (phosphate / amine) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 42 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0380 | A | Power block | Home run JB-HRSG 1 chemical fe-AI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG 1 chemical fe-AI01 | HRSG 1 chemical feed skid (phosphate / amine) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 404 | 108
A-I-0381 | A | Power block | Discrete device to JB JB-HRSG 1 chemical fe-DI01: 12 x 1 pr (field cables) |  | HRSG 1 chemical feed skid (phosphate / amine) | JB-HRSG 1 chemical fe-DI01 | HRSG 1 chemical feed skid (phosphate / amine) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 42 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0382 | A | Power block | Home run JB-HRSG 1 chemical fe-DI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG 1 chemical fe-DI01 | HRSG 1 chemical feed skid (phosphate / amine) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 404 | 108
A-I-0383 | A | Power block | Analog instrument to JB JB-HRSG-2-AI01: 20 x 1 pr (field cables) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | JB-HRSG-2-AI01 | HRSG 2 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0384 | A | Power block | Home run JB-HRSG-2-AI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-2-AI01 | HRSG 2 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 53 | 96
A-I-0385 | A | Power block | Analog instrument to JB JB-HRSG-2-AI02: 20 x 1 pr (field cables) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | JB-HRSG-2-AI02 | HRSG 2 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0386 | A | Power block | Home run JB-HRSG-2-AI02 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-2-AI02 | HRSG 2 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 53 | 96
A-I-0387 | A | Power block | Analog instrument to JB JB-HRSG-2-AI03: 20 x 1 pr (field cables) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | JB-HRSG-2-AI03 | HRSG 2 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0388 | A | Power block | Home run JB-HRSG-2-AI03 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-2-AI03 | HRSG 2 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 53 | 96
A-I-0389 | A | Power block | Analog instrument to JB JB-HRSG-2-AI04: 20 x 1 pr (field cables) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | JB-HRSG-2-AI04 | HRSG 2 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0390 | A | Power block | Home run JB-HRSG-2-AI04 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-2-AI04 | HRSG 2 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 53 | 96
A-I-0391 | A | Power block | Analog instrument to JB JB-HRSG-2-AI05: 20 x 1 pr (field cables) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | JB-HRSG-2-AI05 | HRSG 2 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0392 | A | Power block | Home run JB-HRSG-2-AI05 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-2-AI05 | HRSG 2 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 53 | 96
A-I-0393 | A | Power block | Analog instrument to JB JB-HRSG-2-AI06: 20 x 1 pr (field cables) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | JB-HRSG-2-AI06 | HRSG 2 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0394 | A | Power block | Home run JB-HRSG-2-AI06 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-2-AI06 | HRSG 2 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 53 | 96
A-I-0395 | A | Power block | Analog instrument to JB JB-HRSG-2-AI07: 20 x 1 pr (field cables) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | JB-HRSG-2-AI07 | HRSG 2 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0396 | A | Power block | Home run JB-HRSG-2-AI07 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-2-AI07 | HRSG 2 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 53 | 96
A-I-0397 | A | Power block | Analog instrument to JB JB-HRSG-2-AI08: 20 x 1 pr (field cables) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | JB-HRSG-2-AI08 | HRSG 2 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0398 | A | Power block | Home run JB-HRSG-2-AI08 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-2-AI08 | HRSG 2 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 53 | 96
A-I-0399 | A | Power block | Discrete device to JB JB-HRSG-2-DI01: 20 x 1 pr (field cables) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | JB-HRSG-2-DI01 | HRSG 2 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0400 | A | Power block | Home run JB-HRSG-2-DI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-2-DI01 | HRSG 2 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 53 | 96
A-I-0401 | A | Power block | Discrete device to JB JB-HRSG-2-DI02: 20 x 1 pr (field cables) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | JB-HRSG-2-DI02 | HRSG 2 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0402 | A | Power block | Home run JB-HRSG-2-DI02 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-2-DI02 | HRSG 2 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 53 | 96
A-I-0403 | A | Power block | Discrete device to JB JB-HRSG-2-DI03: 20 x 1 pr (field cables) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | JB-HRSG-2-DI03 | HRSG 2 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0404 | A | Power block | Home run JB-HRSG-2-DI03 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-2-DI03 | HRSG 2 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 53 | 96
A-I-0405 | A | Power block | Discrete device to JB JB-HRSG-2-DI04: 20 x 1 pr (field cables) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | JB-HRSG-2-DI04 | HRSG 2 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0406 | A | Power block | Home run JB-HRSG-2-DI04 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-2-DI04 | HRSG 2 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 53 | 96
A-I-0407 | A | Power block | Thermocouple to TC JB JB-HRSG-2-TC01: 20 x 1 pr (field cables) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | JB-HRSG-2-TC01 | HRSG 2 + SCR (3P reheat, horizontal) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0408 | A | Power block | Home run JB-HRSG-2-TC01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-2-TC01 | HRSG 2 + SCR (3P reheat, horizontal) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Tray | 53 | 96
A-I-0409 | A | Power block | Thermocouple to TC JB JB-HRSG-2-TC02: 20 x 1 pr (field cables) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | JB-HRSG-2-TC02 | HRSG 2 + SCR (3P reheat, horizontal) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0410 | A | Power block | Home run JB-HRSG-2-TC02 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-2-TC02 | HRSG 2 + SCR (3P reheat, horizontal) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Tray | 53 | 96
A-I-0411 | A | Power block | Thermocouple to TC JB JB-HRSG-2-TC03: 20 x 1 pr (field cables) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | JB-HRSG-2-TC03 | HRSG 2 + SCR (3P reheat, horizontal) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0412 | A | Power block | Home run JB-HRSG-2-TC03 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-2-TC03 | HRSG 2 + SCR (3P reheat, horizontal) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Tray | 53 | 96
A-I-0413 | A | Power block | Thermocouple to TC JB JB-HRSG-2-TC04: 20 x 1 pr (field cables) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | JB-HRSG-2-TC04 | HRSG 2 + SCR (3P reheat, horizontal) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0414 | A | Power block | Home run JB-HRSG-2-TC04 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-2-TC04 | HRSG 2 + SCR (3P reheat, horizontal) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Tray | 53 | 96
A-I-0415 | A | Power block | Analog instrument to JB JB-HRSG 2 blowdown ta-AI01: 6 x 1 pr (field cables) |  | HRSG 2 blowdown tank (continuous / intermittent) | JB-HRSG 2 blowdown ta-AI01 | HRSG 2 blowdown tank (continuous / intermittent) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0416 | A | Power block | Home run JB-HRSG 2 blowdown ta-AI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG 2 blowdown ta-AI01 | HRSG 2 blowdown tank (continuous / intermittent) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 38 | 86
A-I-0417 | A | Power block | Discrete device to JB JB-HRSG 2 blowdown ta-DI01: 4 x 1 pr (field cables) |  | HRSG 2 blowdown tank (continuous / intermittent) | JB-HRSG 2 blowdown ta-DI01 | HRSG 2 blowdown tank (continuous / intermittent) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0418 | A | Power block | Home run JB-HRSG 2 blowdown ta-DI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG 2 blowdown ta-DI01 | HRSG 2 blowdown tank (continuous / intermittent) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 38 | 86
A-I-0419 | A | Power block | Analog instrument to JB JB-HRSG 2 chemical fe-AI01: 8 x 1 pr (field cables) |  | HRSG 2 chemical feed skid (phosphate / amine) | JB-HRSG 2 chemical fe-AI01 | HRSG 2 chemical feed skid (phosphate / amine) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 42 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0420 | A | Power block | Home run JB-HRSG 2 chemical fe-AI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG 2 chemical fe-AI01 | HRSG 2 chemical feed skid (phosphate / amine) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 404 | 108
A-I-0421 | A | Power block | Discrete device to JB JB-HRSG 2 chemical fe-DI01: 12 x 1 pr (field cables) |  | HRSG 2 chemical feed skid (phosphate / amine) | JB-HRSG 2 chemical fe-DI01 | HRSG 2 chemical feed skid (phosphate / amine) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 42 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0422 | A | Power block | Home run JB-HRSG 2 chemical fe-DI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG 2 chemical fe-DI01 | HRSG 2 chemical feed skid (phosphate / amine) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 404 | 108
A-I-0423 | A | Power block | Analog instrument to JB JB-HRSG-3-AI01: 20 x 1 pr (field cables) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | JB-HRSG-3-AI01 | HRSG 3 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0424 | A | Power block | Home run JB-HRSG-3-AI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-3-AI01 | HRSG 3 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 87
A-I-0425 | A | Power block | Analog instrument to JB JB-HRSG-3-AI02: 20 x 1 pr (field cables) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | JB-HRSG-3-AI02 | HRSG 3 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0426 | A | Power block | Home run JB-HRSG-3-AI02 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-3-AI02 | HRSG 3 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 87
A-I-0427 | A | Power block | Analog instrument to JB JB-HRSG-3-AI03: 20 x 1 pr (field cables) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | JB-HRSG-3-AI03 | HRSG 3 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0428 | A | Power block | Home run JB-HRSG-3-AI03 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-3-AI03 | HRSG 3 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 87
A-I-0429 | A | Power block | Analog instrument to JB JB-HRSG-3-AI04: 20 x 1 pr (field cables) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | JB-HRSG-3-AI04 | HRSG 3 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0430 | A | Power block | Home run JB-HRSG-3-AI04 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-3-AI04 | HRSG 3 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 87
A-I-0431 | A | Power block | Analog instrument to JB JB-HRSG-3-AI05: 20 x 1 pr (field cables) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | JB-HRSG-3-AI05 | HRSG 3 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0432 | A | Power block | Home run JB-HRSG-3-AI05 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-3-AI05 | HRSG 3 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 87
A-I-0433 | A | Power block | Analog instrument to JB JB-HRSG-3-AI06: 20 x 1 pr (field cables) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | JB-HRSG-3-AI06 | HRSG 3 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0434 | A | Power block | Home run JB-HRSG-3-AI06 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-3-AI06 | HRSG 3 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 87
A-I-0435 | A | Power block | Analog instrument to JB JB-HRSG-3-AI07: 20 x 1 pr (field cables) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | JB-HRSG-3-AI07 | HRSG 3 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0436 | A | Power block | Home run JB-HRSG-3-AI07 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-3-AI07 | HRSG 3 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 87
A-I-0437 | A | Power block | Analog instrument to JB JB-HRSG-3-AI08: 20 x 1 pr (field cables) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | JB-HRSG-3-AI08 | HRSG 3 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0438 | A | Power block | Home run JB-HRSG-3-AI08 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-3-AI08 | HRSG 3 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 87
A-I-0439 | A | Power block | Discrete device to JB JB-HRSG-3-DI01: 20 x 1 pr (field cables) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | JB-HRSG-3-DI01 | HRSG 3 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0440 | A | Power block | Home run JB-HRSG-3-DI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-3-DI01 | HRSG 3 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 87
A-I-0441 | A | Power block | Discrete device to JB JB-HRSG-3-DI02: 20 x 1 pr (field cables) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | JB-HRSG-3-DI02 | HRSG 3 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0442 | A | Power block | Home run JB-HRSG-3-DI02 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-3-DI02 | HRSG 3 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 87
A-I-0443 | A | Power block | Discrete device to JB JB-HRSG-3-DI03: 20 x 1 pr (field cables) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | JB-HRSG-3-DI03 | HRSG 3 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0444 | A | Power block | Home run JB-HRSG-3-DI03 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-3-DI03 | HRSG 3 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 87
A-I-0445 | A | Power block | Discrete device to JB JB-HRSG-3-DI04: 20 x 1 pr (field cables) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | JB-HRSG-3-DI04 | HRSG 3 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0446 | A | Power block | Home run JB-HRSG-3-DI04 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-3-DI04 | HRSG 3 + SCR (3P reheat, horizontal) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 87
A-I-0447 | A | Power block | Thermocouple to TC JB JB-HRSG-3-TC01: 20 x 1 pr (field cables) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | JB-HRSG-3-TC01 | HRSG 3 + SCR (3P reheat, horizontal) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0448 | A | Power block | Home run JB-HRSG-3-TC01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-3-TC01 | HRSG 3 + SCR (3P reheat, horizontal) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Tray | 0 | 87
A-I-0449 | A | Power block | Thermocouple to TC JB JB-HRSG-3-TC02: 20 x 1 pr (field cables) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | JB-HRSG-3-TC02 | HRSG 3 + SCR (3P reheat, horizontal) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0450 | A | Power block | Home run JB-HRSG-3-TC02 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-3-TC02 | HRSG 3 + SCR (3P reheat, horizontal) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Tray | 0 | 87
A-I-0451 | A | Power block | Thermocouple to TC JB JB-HRSG-3-TC03: 20 x 1 pr (field cables) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | JB-HRSG-3-TC03 | HRSG 3 + SCR (3P reheat, horizontal) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0452 | A | Power block | Home run JB-HRSG-3-TC03 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-3-TC03 | HRSG 3 + SCR (3P reheat, horizontal) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Tray | 0 | 87
A-I-0453 | A | Power block | Thermocouple to TC JB JB-HRSG-3-TC04: 20 x 1 pr (field cables) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | JB-HRSG-3-TC04 | HRSG 3 + SCR (3P reheat, horizontal) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 180 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0454 | A | Power block | Home run JB-HRSG-3-TC04 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG-3-TC04 | HRSG 3 + SCR (3P reheat, horizontal) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Tray | 0 | 87
A-I-0455 | A | Power block | Analog instrument to JB JB-HRSG 3 blowdown ta-AI01: 6 x 1 pr (field cables) |  | HRSG 3 blowdown tank (continuous / intermittent) | JB-HRSG 3 blowdown ta-AI01 | HRSG 3 blowdown tank (continuous / intermittent) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0456 | A | Power block | Home run JB-HRSG 3 blowdown ta-AI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG 3 blowdown ta-AI01 | HRSG 3 blowdown tank (continuous / intermittent) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 38 | 86
A-I-0457 | A | Power block | Discrete device to JB JB-HRSG 3 blowdown ta-DI01: 4 x 1 pr (field cables) |  | HRSG 3 blowdown tank (continuous / intermittent) | JB-HRSG 3 blowdown ta-DI01 | HRSG 3 blowdown tank (continuous / intermittent) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0458 | A | Power block | Home run JB-HRSG 3 blowdown ta-DI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG 3 blowdown ta-DI01 | HRSG 3 blowdown tank (continuous / intermittent) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 38 | 86
A-I-0459 | A | Power block | Analog instrument to JB JB-HRSG 3 chemical fe-AI01: 8 x 1 pr (field cables) |  | HRSG 3 chemical feed skid (phosphate / amine) | JB-HRSG 3 chemical fe-AI01 | HRSG 3 chemical feed skid (phosphate / amine) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 42 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0460 | A | Power block | Home run JB-HRSG 3 chemical fe-AI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG 3 chemical fe-AI01 | HRSG 3 chemical feed skid (phosphate / amine) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 404 | 108
A-I-0461 | A | Power block | Discrete device to JB JB-HRSG 3 chemical fe-DI01: 12 x 1 pr (field cables) |  | HRSG 3 chemical feed skid (phosphate / amine) | JB-HRSG 3 chemical fe-DI01 | HRSG 3 chemical feed skid (phosphate / amine) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 42 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0462 | A | Power block | Home run JB-HRSG 3 chemical fe-DI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-HRSG 3 chemical fe-DI01 | HRSG 3 chemical feed skid (phosphate / amine) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 404 | 108
A-I-0463 | A | Power block | Analog instrument to JB JB-LCT-A-AI01: 8 x 1 pr (field cables) | LCT-A | LCT-A: 13.8/0.48 kV load-centre transformer | JB-LCT-A-AI01 | LCT-A: 13.8/0.48 kV load-centre transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0464 | A | Power block | Home run JB-LCT-A-AI01 to the control / marshalling room | R1 | R1: main electrical building (64 x 180 ft) | JB-LCT-A-AI01 | LCT-A: 13.8/0.48 kV load-centre transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 718 | 124
A-I-0465 | A | Power block | Discrete device to JB JB-LCT-A-DI01: 16 x 1 pr (field cables) | LCT-A | LCT-A: 13.8/0.48 kV load-centre transformer | JB-LCT-A-DI01 | LCT-A: 13.8/0.48 kV load-centre transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0466 | A | Power block | Home run JB-LCT-A-DI01 to the control / marshalling room | R1 | R1: main electrical building (64 x 180 ft) | JB-LCT-A-DI01 | LCT-A: 13.8/0.48 kV load-centre transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 718 | 124
A-I-0467 | A | Power block | Analog instrument to JB JB-LCT-B-AI01: 8 x 1 pr (field cables) | LCT-B | LCT-B: 13.8/0.48 kV load-centre transformer | JB-LCT-B-AI01 | LCT-B: 13.8/0.48 kV load-centre transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0468 | A | Power block | Home run JB-LCT-B-AI01 to the control / marshalling room | R1 | R1: main electrical building (64 x 180 ft) | JB-LCT-B-AI01 | LCT-B: 13.8/0.48 kV load-centre transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 718 | 146
A-I-0469 | A | Power block | Discrete device to JB JB-LCT-B-DI01: 16 x 1 pr (field cables) | LCT-B | LCT-B: 13.8/0.48 kV load-centre transformer | JB-LCT-B-DI01 | LCT-B: 13.8/0.48 kV load-centre transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0470 | A | Power block | Home run JB-LCT-B-DI01 to the control / marshalling room | R1 | R1: main electrical building (64 x 180 ft) | JB-LCT-B-DI01 | LCT-B: 13.8/0.48 kV load-centre transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 718 | 146
A-I-0471 | A | Power block | Analog instrument to JB JB-NGT-1-AI01: 10 x 1 pr (field cables) | NGT-1 | NGT-1: neutral grounding cubicle (GTG-1) | JB-NGT-1-AI01 | NGT-1: neutral grounding cubicle (GTG-1) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0472 | A | Power block | Home run JB-NGT-1-AI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-NGT-1-AI01 | NGT-1: neutral grounding cubicle (GTG-1) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 359 | 120
A-I-0473 | A | Power block | Discrete device to JB JB-NGT-1-DI01: 20 x 1 pr (field cables) | NGT-1 | NGT-1: neutral grounding cubicle (GTG-1) | JB-NGT-1-DI01 | NGT-1: neutral grounding cubicle (GTG-1) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0474 | A | Power block | Home run JB-NGT-1-DI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-NGT-1-DI01 | NGT-1: neutral grounding cubicle (GTG-1) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 359 | 120
A-I-0475 | A | Power block | Analog instrument to JB JB-NGT-2-AI01: 10 x 1 pr (field cables) | NGT-2 | NGT-2: neutral grounding cubicle (GTG-2) | JB-NGT-2-AI01 | NGT-2: neutral grounding cubicle (GTG-2) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0476 | A | Power block | Home run JB-NGT-2-AI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-NGT-2-AI01 | NGT-2: neutral grounding cubicle (GTG-2) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1233 | 210
A-I-0477 | A | Power block | Discrete device to JB JB-NGT-2-DI01: 20 x 1 pr (field cables) | NGT-2 | NGT-2: neutral grounding cubicle (GTG-2) | JB-NGT-2-DI01 | NGT-2: neutral grounding cubicle (GTG-2) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0478 | A | Power block | Home run JB-NGT-2-DI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-NGT-2-DI01 | NGT-2: neutral grounding cubicle (GTG-2) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1233 | 210
A-I-0479 | A | Power block | Analog instrument to JB JB-NGT-3-AI01: 10 x 1 pr (field cables) | NGT-3 | NGT-3: neutral grounding cubicle (GTG-3) | JB-NGT-3-AI01 | NGT-3: neutral grounding cubicle (GTG-3) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0480 | A | Power block | Home run JB-NGT-3-AI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-NGT-3-AI01 | NGT-3: neutral grounding cubicle (GTG-3) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1229 | 198
A-I-0481 | A | Power block | Discrete device to JB JB-NGT-3-DI01: 20 x 1 pr (field cables) | NGT-3 | NGT-3: neutral grounding cubicle (GTG-3) | JB-NGT-3-DI01 | NGT-3: neutral grounding cubicle (GTG-3) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0482 | A | Power block | Home run JB-NGT-3-DI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-NGT-3-DI01 | NGT-3: neutral grounding cubicle (GTG-3) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1229 | 198
A-I-0483 | A | Power block | Analog instrument to JB JB-NGT-ST-AI01: 10 x 1 pr (field cables) | NGT-ST | NGT-ST: neutral grounding cubicle (STG) | JB-NGT-ST-AI01 | NGT-ST: neutral grounding cubicle (STG) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0484 | A | Power block | Home run JB-NGT-ST-AI01 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-NGT-ST-AI01 | NGT-ST: neutral grounding cubicle (STG) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 392 | 105
A-I-0485 | A | Power block | Discrete device to JB JB-NGT-ST-DI01: 20 x 1 pr (field cables) | NGT-ST | NGT-ST: neutral grounding cubicle (STG) | JB-NGT-ST-DI01 | NGT-ST: neutral grounding cubicle (STG) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0486 | A | Power block | Home run JB-NGT-ST-DI01 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-NGT-ST-DI01 | NGT-ST: neutral grounding cubicle (STG) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 392 | 105
A-I-0487 | A | Power block | Instrumentation | R1 | R1: main electrical building (64 x 180 ft) | TX-LCI-1 | R1 TX-LCI-1 dry-type input transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 73
A-I-0488 | A | Power block | Instrumentation | R1 | R1: main electrical building (64 x 180 ft) | TX-LCI-2 | R1 TX-LCI-2 dry-type input transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 109
A-I-0489 | A | Power block | Instrumentation | R1 | R1: main electrical building (64 x 180 ft) | TX-LCI-3 | R1 TX-LCI-3 dry-type input transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 667 | 144
A-I-0490 | A | Power block | Analog instrument to JB JB-SCRB-1-AI01: 6 x 1 pr (field cables) | SCRB-1 | SCRB-1A/B: SCR dilution-air blowers | JB-SCRB-1-AI01 | SCRB-1A/B: SCR dilution-air blowers | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 51 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0491 | A | Power block | Home run JB-SCRB-1-AI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-SCRB-1-AI01 | SCRB-1A/B: SCR dilution-air blowers | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 404 | 72
A-I-0492 | A | Power block | Discrete device to JB JB-SCRB-1-DI01: 6 x 1 pr (field cables) | SCRB-1 | SCRB-1A/B: SCR dilution-air blowers | JB-SCRB-1-DI01 | SCRB-1A/B: SCR dilution-air blowers | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 51 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0493 | A | Power block | Home run JB-SCRB-1-DI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-SCRB-1-DI01 | SCRB-1A/B: SCR dilution-air blowers | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 404 | 72
A-I-0494 | A | Power block | Analog instrument to JB JB-SCRB-2-AI01: 6 x 1 pr (field cables) | SCRB-2 | SCRB-2A/B: SCR dilution-air blowers | JB-SCRB-2-AI01 | SCRB-2A/B: SCR dilution-air blowers | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 51 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0495 | A | Power block | Home run JB-SCRB-2-AI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-SCRB-2-AI01 | SCRB-2A/B: SCR dilution-air blowers | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 404 | 72
A-I-0496 | A | Power block | Discrete device to JB JB-SCRB-2-DI01: 6 x 1 pr (field cables) | SCRB-2 | SCRB-2A/B: SCR dilution-air blowers | JB-SCRB-2-DI01 | SCRB-2A/B: SCR dilution-air blowers | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 51 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0497 | A | Power block | Home run JB-SCRB-2-DI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-SCRB-2-DI01 | SCRB-2A/B: SCR dilution-air blowers | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 404 | 72
A-I-0498 | A | Power block | Analog instrument to JB JB-SCRB-3-AI01: 6 x 1 pr (field cables) | SCRB-3 | SCRB-3A/B: SCR dilution-air blowers | JB-SCRB-3-AI01 | SCRB-3A/B: SCR dilution-air blowers | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 51 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0499 | A | Power block | Home run JB-SCRB-3-AI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-SCRB-3-AI01 | SCRB-3A/B: SCR dilution-air blowers | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 404 | 72
A-I-0500 | A | Power block | Discrete device to JB JB-SCRB-3-DI01: 6 x 1 pr (field cables) | SCRB-3 | SCRB-3A/B: SCR dilution-air blowers | JB-SCRB-3-DI01 | SCRB-3A/B: SCR dilution-air blowers | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 51 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0501 | A | Power block | Home run JB-SCRB-3-DI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-SCRB-3-DI01 | SCRB-3A/B: SCR dilution-air blowers | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 404 | 72
A-I-0502 | A | Power block | Analog instrument to JB JB-SFC-1-AI01: 10 x 1 pr (field cables) | SFC-1 | SFC-1: GT1 static starter (LCI) and isolation transformer | JB-SFC-1-AI01 | SFC-1: GT1 static starter (LCI) and isolation transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0503 | A | Power block | Home run JB-SFC-1-AI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-SFC-1-AI01 | SFC-1: GT1 static starter (LCI) and isolation transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 359 | 147
A-I-0504 | A | Power block | Discrete device to JB JB-SFC-1-DI01: 20 x 1 pr (field cables) | SFC-1 | SFC-1: GT1 static starter (LCI) and isolation transformer | JB-SFC-1-DI01 | SFC-1: GT1 static starter (LCI) and isolation transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0505 | A | Power block | Home run JB-SFC-1-DI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-SFC-1-DI01 | SFC-1: GT1 static starter (LCI) and isolation transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 359 | 147
A-I-0506 | A | Power block | Analog instrument to JB JB-SFC-2-AI01: 10 x 1 pr (field cables) | SFC-2 | SFC-2: GT2 static starter (LCI) and isolation transformer | JB-SFC-2-AI01 | SFC-2: GT2 static starter (LCI) and isolation transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0507 | A | Power block | Home run JB-SFC-2-AI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-SFC-2-AI01 | SFC-2: GT2 static starter (LCI) and isolation transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1233 | 237
A-I-0508 | A | Power block | Discrete device to JB JB-SFC-2-DI01: 20 x 1 pr (field cables) | SFC-2 | SFC-2: GT2 static starter (LCI) and isolation transformer | JB-SFC-2-DI01 | SFC-2: GT2 static starter (LCI) and isolation transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0509 | A | Power block | Home run JB-SFC-2-DI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-SFC-2-DI01 | SFC-2: GT2 static starter (LCI) and isolation transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1233 | 237
A-I-0510 | A | Power block | Analog instrument to JB JB-SFC-3-AI01: 10 x 1 pr (field cables) | SFC-3 | SFC-3: GT3 static starter (LCI) and isolation transformer | JB-SFC-3-AI01 | SFC-3: GT3 static starter (LCI) and isolation transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0511 | A | Power block | Home run JB-SFC-3-AI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-SFC-3-AI01 | SFC-3: GT3 static starter (LCI) and isolation transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 987 | 184
A-I-0512 | A | Power block | Discrete device to JB JB-SFC-3-DI01: 20 x 1 pr (field cables) | SFC-3 | SFC-3: GT3 static starter (LCI) and isolation transformer | JB-SFC-3-DI01 | SFC-3: GT3 static starter (LCI) and isolation transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0513 | A | Power block | Home run JB-SFC-3-DI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-SFC-3-DI01 | SFC-3: GT3 static starter (LCI) and isolation transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 987 | 184
A-I-0514 | A | Power block | Analog instrument to JB JB-SOS-1-AI01: 15 x 1 pr (field cables) | SOS-1 | SOS-1: GTG-1 seal-oil and H2 / CO2 gas-control skid | JB-SOS-1-AI01 | SOS-1: GTG-1 seal-oil and H2 / CO2 gas-control skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 15 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0515 | A | Power block | Home run JB-SOS-1-AI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-SOS-1-AI01 | SOS-1: GTG-1 seal-oil and H2 / CO2 gas-control skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 403 | 138
A-I-0516 | A | Power block | Discrete device to JB JB-SOS-1-DI01: 15 x 1 pr (field cables) | SOS-1 | SOS-1: GTG-1 seal-oil and H2 / CO2 gas-control skid | JB-SOS-1-DI01 | SOS-1: GTG-1 seal-oil and H2 / CO2 gas-control skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 15 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0517 | A | Power block | Home run JB-SOS-1-DI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-SOS-1-DI01 | SOS-1: GTG-1 seal-oil and H2 / CO2 gas-control skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 403 | 138
A-I-0518 | A | Power block | Analog instrument to JB JB-SOS-2-AI01: 15 x 1 pr (field cables) | SOS-2 | SOS-2: GTG-2 seal-oil and H2 / CO2 gas-control skid | JB-SOS-2-AI01 | SOS-2: GTG-2 seal-oil and H2 / CO2 gas-control skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 15 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0519 | A | Power block | Home run JB-SOS-2-AI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-SOS-2-AI01 | SOS-2: GTG-2 seal-oil and H2 / CO2 gas-control skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1277 | 228
A-I-0520 | A | Power block | Discrete device to JB JB-SOS-2-DI01: 15 x 1 pr (field cables) | SOS-2 | SOS-2: GTG-2 seal-oil and H2 / CO2 gas-control skid | JB-SOS-2-DI01 | SOS-2: GTG-2 seal-oil and H2 / CO2 gas-control skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 15 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0521 | A | Power block | Home run JB-SOS-2-DI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-SOS-2-DI01 | SOS-2: GTG-2 seal-oil and H2 / CO2 gas-control skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1277 | 228
A-I-0522 | A | Power block | Analog instrument to JB JB-SOS-3-AI01: 15 x 1 pr (field cables) | SOS-3 | SOS-3: GTG-3 seal-oil and H2 / CO2 gas-control skid | JB-SOS-3-AI01 | SOS-3: GTG-3 seal-oil and H2 / CO2 gas-control skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 15 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0523 | A | Power block | Home run JB-SOS-3-AI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-SOS-3-AI01 | SOS-3: GTG-3 seal-oil and H2 / CO2 gas-control skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1214 | 126
A-I-0524 | A | Power block | Discrete device to JB JB-SOS-3-DI01: 15 x 1 pr (field cables) | SOS-3 | SOS-3: GTG-3 seal-oil and H2 / CO2 gas-control skid | JB-SOS-3-DI01 | SOS-3: GTG-3 seal-oil and H2 / CO2 gas-control skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 15 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0525 | A | Power block | Home run JB-SOS-3-DI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-SOS-3-DI01 | SOS-3: GTG-3 seal-oil and H2 / CO2 gas-control skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1214 | 126
A-I-0526 | A | Power block | Analog instrument to JB JB-SPC-1-AI01: 10 x 1 pr (field cables) | SPC-1 | SPC-1: surge-protection and VT cubicle on the IPB (GTG-1) | JB-SPC-1-AI01 | SPC-1: surge-protection and VT cubicle on the IPB (GTG-1) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 40 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0527 | A | Power block | Home run JB-SPC-1-AI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-SPC-1-AI01 | SPC-1: surge-protection and VT cubicle on the IPB (GTG-1) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 395 | 124
A-I-0528 | A | Power block | Discrete device to JB JB-SPC-1-DI01: 20 x 1 pr (field cables) | SPC-1 | SPC-1: surge-protection and VT cubicle on the IPB (GTG-1) | JB-SPC-1-DI01 | SPC-1: surge-protection and VT cubicle on the IPB (GTG-1) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 40 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0529 | A | Power block | Home run JB-SPC-1-DI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-SPC-1-DI01 | SPC-1: surge-protection and VT cubicle on the IPB (GTG-1) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 395 | 124
A-I-0530 | A | Power block | Analog instrument to JB JB-SPC-2-AI01: 10 x 1 pr (field cables) | SPC-2 | SPC-2: surge-protection and VT cubicle on the IPB (GTG-2) | JB-SPC-2-AI01 | SPC-2: surge-protection and VT cubicle on the IPB (GTG-2) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 40 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0531 | A | Power block | Home run JB-SPC-2-AI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-SPC-2-AI01 | SPC-2: surge-protection and VT cubicle on the IPB (GTG-2) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1269 | 214
A-I-0532 | A | Power block | Discrete device to JB JB-SPC-2-DI01: 20 x 1 pr (field cables) | SPC-2 | SPC-2: surge-protection and VT cubicle on the IPB (GTG-2) | JB-SPC-2-DI01 | SPC-2: surge-protection and VT cubicle on the IPB (GTG-2) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 40 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0533 | A | Power block | Home run JB-SPC-2-DI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-SPC-2-DI01 | SPC-2: surge-protection and VT cubicle on the IPB (GTG-2) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1269 | 214
A-I-0534 | A | Power block | Analog instrument to JB JB-SPC-3-AI01: 10 x 1 pr (field cables) | SPC-3 | SPC-3: surge-protection and VT cubicle on the IPB (GTG-3) | JB-SPC-3-AI01 | SPC-3: surge-protection and VT cubicle on the IPB (GTG-3) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 40 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0535 | A | Power block | Home run JB-SPC-3-AI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-SPC-3-AI01 | SPC-3: surge-protection and VT cubicle on the IPB (GTG-3) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1193 | 114
A-I-0536 | A | Power block | Discrete device to JB JB-SPC-3-DI01: 20 x 1 pr (field cables) | SPC-3 | SPC-3: surge-protection and VT cubicle on the IPB (GTG-3) | JB-SPC-3-DI01 | SPC-3: surge-protection and VT cubicle on the IPB (GTG-3) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 40 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0537 | A | Power block | Home run JB-SPC-3-DI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-SPC-3-DI01 | SPC-3: surge-protection and VT cubicle on the IPB (GTG-3) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1193 | 114
A-I-0538 | A | Power block | Analog instrument to JB JB-ST aux-AI01: 20 x 1 pr (field cables) | ST aux | ST aux: lube oil, turning gear, EHC | JB-ST aux-AI01 | ST aux: lube oil, turning gear, EHC | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 62 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0539 | A | Power block | Home run JB-ST aux-AI01 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-ST aux-AI01 | ST aux: lube oil, turning gear, EHC | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 67 | 84
A-I-0540 | A | Power block | Analog instrument to JB JB-ST aux-AI02: 10 x 1 pr (field cables) | ST aux | ST aux: lube oil, turning gear, EHC | JB-ST aux-AI02 | ST aux: lube oil, turning gear, EHC | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 62 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0541 | A | Power block | Home run JB-ST aux-AI02 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-ST aux-AI02 | ST aux: lube oil, turning gear, EHC | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 67 | 84
A-I-0542 | A | Power block | Discrete device to JB JB-ST aux-DI01: 20 x 1 pr (field cables) | ST aux | ST aux: lube oil, turning gear, EHC | JB-ST aux-DI01 | ST aux: lube oil, turning gear, EHC | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 62 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0543 | A | Power block | Home run JB-ST aux-DI01 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-ST aux-DI01 | ST aux: lube oil, turning gear, EHC | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 67 | 84
A-I-0544 | A | Power block | Discrete device to JB JB-ST aux-DI02: 10 x 1 pr (field cables) | ST aux | ST aux: lube oil, turning gear, EHC | JB-ST aux-DI02 | ST aux: lube oil, turning gear, EHC | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 62 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0545 | A | Power block | Home run JB-ST aux-DI02 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-ST aux-DI02 | ST aux: lube oil, turning gear, EHC | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 67 | 84
A-I-0546 | A | Power block | Analog instrument to JB JB-ST-AI01: 20 x 1 pr (field cables) | ST | ST: steam turbine (HP/IP + LP), ACC plant | JB-ST-AI01 | ST: steam turbine (HP/IP + LP), ACC plant | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 119 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0547 | A | Power block | Home run JB-ST-AI01 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-ST-AI01 | ST: steam turbine (HP/IP + LP), ACC plant | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-I-0548 | A | Power block | Analog instrument to JB JB-ST-AI02: 20 x 1 pr (field cables) | ST | ST: steam turbine (HP/IP + LP), ACC plant | JB-ST-AI02 | ST: steam turbine (HP/IP + LP), ACC plant | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 119 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0549 | A | Power block | Home run JB-ST-AI02 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-ST-AI02 | ST: steam turbine (HP/IP + LP), ACC plant | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-I-0550 | A | Power block | Analog instrument to JB JB-ST-AI03: 20 x 1 pr (field cables) | ST | ST: steam turbine (HP/IP + LP), ACC plant | JB-ST-AI03 | ST: steam turbine (HP/IP + LP), ACC plant | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 119 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0551 | A | Power block | Home run JB-ST-AI03 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-ST-AI03 | ST: steam turbine (HP/IP + LP), ACC plant | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-I-0552 | A | Power block | Analog instrument to JB JB-ST-AI04: 20 x 1 pr (field cables) | ST | ST: steam turbine (HP/IP + LP), ACC plant | JB-ST-AI04 | ST: steam turbine (HP/IP + LP), ACC plant | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 119 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0553 | A | Power block | Home run JB-ST-AI04 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-ST-AI04 | ST: steam turbine (HP/IP + LP), ACC plant | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-I-0554 | A | Power block | Analog instrument to JB JB-ST-AI05: 20 x 1 pr (field cables) | ST | ST: steam turbine (HP/IP + LP), ACC plant | JB-ST-AI05 | ST: steam turbine (HP/IP + LP), ACC plant | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 119 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0555 | A | Power block | Home run JB-ST-AI05 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-ST-AI05 | ST: steam turbine (HP/IP + LP), ACC plant | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-I-0556 | A | Power block | Analog instrument to JB JB-ST-AI06: 20 x 1 pr (field cables) | ST | ST: steam turbine (HP/IP + LP), ACC plant | JB-ST-AI06 | ST: steam turbine (HP/IP + LP), ACC plant | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 119 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0557 | A | Power block | Home run JB-ST-AI06 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-ST-AI06 | ST: steam turbine (HP/IP + LP), ACC plant | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-I-0558 | A | Power block | Analog instrument to JB JB-ST-AI07: 20 x 1 pr (field cables) | ST | ST: steam turbine (HP/IP + LP), ACC plant | JB-ST-AI07 | ST: steam turbine (HP/IP + LP), ACC plant | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 119 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0559 | A | Power block | Home run JB-ST-AI07 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-ST-AI07 | ST: steam turbine (HP/IP + LP), ACC plant | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-I-0560 | A | Power block | Analog instrument to JB JB-ST-AI08: 10 x 1 pr (field cables) | ST | ST: steam turbine (HP/IP + LP), ACC plant | JB-ST-AI08 | ST: steam turbine (HP/IP + LP), ACC plant | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 119 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0561 | A | Power block | Home run JB-ST-AI08 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-ST-AI08 | ST: steam turbine (HP/IP + LP), ACC plant | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-I-0562 | A | Power block | Discrete device to JB JB-ST-DI01: 20 x 1 pr (field cables) | ST | ST: steam turbine (HP/IP + LP), ACC plant | JB-ST-DI01 | ST: steam turbine (HP/IP + LP), ACC plant | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 119 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0563 | A | Power block | Home run JB-ST-DI01 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-ST-DI01 | ST: steam turbine (HP/IP + LP), ACC plant | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-I-0564 | A | Power block | Discrete device to JB JB-ST-DI02: 20 x 1 pr (field cables) | ST | ST: steam turbine (HP/IP + LP), ACC plant | JB-ST-DI02 | ST: steam turbine (HP/IP + LP), ACC plant | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 119 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0565 | A | Power block | Home run JB-ST-DI02 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-ST-DI02 | ST: steam turbine (HP/IP + LP), ACC plant | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-I-0566 | A | Power block | Discrete device to JB JB-ST-DI03: 20 x 1 pr (field cables) | ST | ST: steam turbine (HP/IP + LP), ACC plant | JB-ST-DI03 | ST: steam turbine (HP/IP + LP), ACC plant | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 119 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0567 | A | Power block | Home run JB-ST-DI03 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-ST-DI03 | ST: steam turbine (HP/IP + LP), ACC plant | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-I-0568 | A | Power block | Discrete device to JB JB-ST-DI04: 20 x 1 pr (field cables) | ST | ST: steam turbine (HP/IP + LP), ACC plant | JB-ST-DI04 | ST: steam turbine (HP/IP + LP), ACC plant | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 119 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0569 | A | Power block | Home run JB-ST-DI04 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-ST-DI04 | ST: steam turbine (HP/IP + LP), ACC plant | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-I-0570 | A | Power block | Discrete device to JB JB-ST-DI05: 20 x 1 pr (field cables) | ST | ST: steam turbine (HP/IP + LP), ACC plant | JB-ST-DI05 | ST: steam turbine (HP/IP + LP), ACC plant | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 119 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0571 | A | Power block | Home run JB-ST-DI05 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-ST-DI05 | ST: steam turbine (HP/IP + LP), ACC plant | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-I-0572 | A | Power block | Thermocouple to TC JB JB-ST-TC01: 20 x 1 pr (field cables) | ST | ST: steam turbine (HP/IP + LP), ACC plant | JB-ST-TC01 | ST: steam turbine (HP/IP + LP), ACC plant | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 119 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0573 | A | Power block | Home run JB-ST-TC01 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-ST-TC01 | ST: steam turbine (HP/IP + LP), ACC plant | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-I-0574 | A | Power block | Thermocouple to TC JB JB-ST-TC02: 20 x 1 pr (field cables) | ST | ST: steam turbine (HP/IP + LP), ACC plant | JB-ST-TC02 | ST: steam turbine (HP/IP + LP), ACC plant | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 119 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0575 | A | Power block | Home run JB-ST-TC02 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-ST-TC02 | ST: steam turbine (HP/IP + LP), ACC plant | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-I-0576 | A | Power block | Vibration monitoring | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Duct bank | 12 | 50
A-I-0577 | A | Power block | Analog instrument to JB JB-STG-AI01: 20 x 1 pr (field cables) | STG | STG: steam-turbine generator | JB-STG-AI01 | STG: steam-turbine generator | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 74 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0578 | A | Power block | Home run JB-STG-AI01 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-STG-AI01 | STG: steam-turbine generator | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 517 | 35
A-I-0579 | A | Power block | Discrete device to JB JB-STG-DI01: 20 x 1 pr (field cables) | STG | STG: steam-turbine generator | JB-STG-DI01 | STG: steam-turbine generator | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 74 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0580 | A | Power block | Home run JB-STG-DI01 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-STG-DI01 | STG: steam-turbine generator | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 517 | 35
A-I-0581 | A | Power block | RTD to JB JB-STG-RTD01: 10 x 1 tri (field cables) | STG | STG: steam-turbine generator | JB-STG-RTD01 | STG: steam-turbine generator | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 74 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0582 | A | Power block | Home run JB-STG-RTD01 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-STG-RTD01 | STG: steam-turbine generator | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 517 | 35
A-I-0583 | A | Power block | RTD to JB JB-STG-RTD02: 10 x 1 tri (field cables) | STG | STG: steam-turbine generator | JB-STG-RTD02 | STG: steam-turbine generator | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 74 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0584 | A | Power block | Home run JB-STG-RTD02 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-STG-RTD02 | STG: steam-turbine generator | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 517 | 35
A-I-0585 | A | Power block | RTD to JB JB-STG-RTD03: 10 x 1 tri (field cables) | STG | STG: steam-turbine generator | JB-STG-RTD03 | STG: steam-turbine generator | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 74 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0586 | A | Power block | Home run JB-STG-RTD03 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-STG-RTD03 | STG: steam-turbine generator | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 517 | 35
A-I-0587 | A | Power block | Vibration monitoring | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | STG | STG: steam-turbine generator | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Duct bank | 517 | 35
A-I-0588 | A | Power block | Analog instrument to JB JB-SWAS-AI01: 20 x 1 pr (field cables) | SWAS | SWAS: steam and water analysis | JB-SWAS-AI01 | SWAS: steam and water analysis | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 75 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0589 | A | Power block | Home run JB-SWAS-AI01 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-SWAS-AI01 | SWAS: steam and water analysis | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 258 | 32
A-I-0590 | A | Power block | Analog instrument to JB JB-SWAS-AI02: 4 x 1 pr (field cables) | SWAS | SWAS: steam and water analysis | JB-SWAS-AI02 | SWAS: steam and water analysis | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 75 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0591 | A | Power block | Home run JB-SWAS-AI02 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-SWAS-AI02 | SWAS: steam and water analysis | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 258 | 32
A-I-0592 | A | Power block | Discrete device to JB JB-SWAS-DI01: 8 x 1 pr (field cables) | SWAS | SWAS: steam and water analysis | JB-SWAS-DI01 | SWAS: steam and water analysis | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 75 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0593 | A | Power block | Home run JB-SWAS-DI01 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-SWAS-DI01 | SWAS: steam and water analysis | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 258 | 32
A-I-0594 | A | Power block | Analog instrument to JB JB-T-R2A: 13.8/0.48 k-AI01: 8 x 1 pr (field cables) |  | T-R2A: 13.8/0.48 kV | JB-T-R2A: 13.8/0.48 k-AI01 | T-R2A: 13.8/0.48 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0595 | A | Power block | Home run JB-T-R2A: 13.8/0.48 k-AI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-T-R2A: 13.8/0.48 k-AI01 | T-R2A: 13.8/0.48 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 86
A-I-0596 | A | Power block | Discrete device to JB JB-T-R2A: 13.8/0.48 k-DI01: 16 x 1 pr (field cables) |  | T-R2A: 13.8/0.48 kV | JB-T-R2A: 13.8/0.48 k-DI01 | T-R2A: 13.8/0.48 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0597 | A | Power block | Home run JB-T-R2A: 13.8/0.48 k-DI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-T-R2A: 13.8/0.48 k-DI01 | T-R2A: 13.8/0.48 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 86
A-I-0598 | A | Power block | Analog instrument to JB JB-T-R2B: 13.8/0.48 k-AI01: 8 x 1 pr (field cables) |  | T-R2B: 13.8/0.48 kV | JB-T-R2B: 13.8/0.48 k-AI01 | T-R2B: 13.8/0.48 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0599 | A | Power block | Home run JB-T-R2B: 13.8/0.48 k-AI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-T-R2B: 13.8/0.48 k-AI01 | T-R2B: 13.8/0.48 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 97
A-I-0600 | A | Power block | Discrete device to JB JB-T-R2B: 13.8/0.48 k-DI01: 16 x 1 pr (field cables) |  | T-R2B: 13.8/0.48 kV | JB-T-R2B: 13.8/0.48 k-DI01 | T-R2B: 13.8/0.48 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0601 | A | Power block | Home run JB-T-R2B: 13.8/0.48 k-DI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-T-R2B: 13.8/0.48 k-DI01 | T-R2B: 13.8/0.48 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 97
A-I-0602 | A | Power block | Analog instrument to JB JB-T-R2C: 13.8/0.48 k-AI01: 8 x 1 pr (field cables) |  | T-R2C: 13.8/0.48 kV | JB-T-R2C: 13.8/0.48 k-AI01 | T-R2C: 13.8/0.48 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0603 | A | Power block | Home run JB-T-R2C: 13.8/0.48 k-AI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-T-R2C: 13.8/0.48 k-AI01 | T-R2C: 13.8/0.48 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 97
A-I-0604 | A | Power block | Discrete device to JB JB-T-R2C: 13.8/0.48 k-DI01: 16 x 1 pr (field cables) |  | T-R2C: 13.8/0.48 kV | JB-T-R2C: 13.8/0.48 k-DI01 | T-R2C: 13.8/0.48 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0605 | A | Power block | Home run JB-T-R2C: 13.8/0.48 k-DI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-T-R2C: 13.8/0.48 k-DI01 | T-R2C: 13.8/0.48 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 97
A-I-0606 | A | Power block | Analog instrument to JB JB-T-R3: 13.8/0.48 kV-AI01: 8 x 1 pr (field cables) |  | T-R3: 13.8/0.48 kV | JB-T-R3: 13.8/0.48 kV-AI01 | T-R3: 13.8/0.48 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0607 | A | Power block | Home run JB-T-R3: 13.8/0.48 kV-AI01 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-T-R3: 13.8/0.48 kV-AI01 | T-R3: 13.8/0.48 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 0 | 71
A-I-0608 | A | Power block | Discrete device to JB JB-T-R3: 13.8/0.48 kV-DI01: 16 x 1 pr (field cables) |  | T-R3: 13.8/0.48 kV | JB-T-R3: 13.8/0.48 kV-DI01 | T-R3: 13.8/0.48 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0609 | A | Power block | Home run JB-T-R3: 13.8/0.48 kV-DI01 to the control / marshalling room | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | JB-T-R3: 13.8/0.48 kV-DI01 | T-R3: 13.8/0.48 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 0 | 71
A-I-0610 | A | Power block | Analog instrument to JB JB-T4-A-AI01: 8 x 1 pr (field cables) | T4-A | T4-A: 13.8/4.16 kV station transformer | JB-T4-A-AI01 | T4-A: 13.8/4.16 kV station transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 49 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0611 | A | Power block | Home run JB-T4-A-AI01 to the control / marshalling room | R1 | R1: main electrical building (64 x 180 ft) | JB-T4-A-AI01 | T4-A: 13.8/4.16 kV station transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 730 | 124
A-I-0612 | A | Power block | Discrete device to JB JB-T4-A-DI01: 16 x 1 pr (field cables) | T4-A | T4-A: 13.8/4.16 kV station transformer | JB-T4-A-DI01 | T4-A: 13.8/4.16 kV station transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 49 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0613 | A | Power block | Home run JB-T4-A-DI01 to the control / marshalling room | R1 | R1: main electrical building (64 x 180 ft) | JB-T4-A-DI01 | T4-A: 13.8/4.16 kV station transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 730 | 124
A-I-0614 | A | Power block | Analog instrument to JB JB-T4-B-AI01: 8 x 1 pr (field cables) | T4-B | T4-B: 13.8/4.16 kV station transformer | JB-T4-B-AI01 | T4-B: 13.8/4.16 kV station transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 49 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0615 | A | Power block | Home run JB-T4-B-AI01 to the control / marshalling room | R1 | R1: main electrical building (64 x 180 ft) | JB-T4-B-AI01 | T4-B: 13.8/4.16 kV station transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 752 | 124
A-I-0616 | A | Power block | Discrete device to JB JB-T4-B-DI01: 16 x 1 pr (field cables) | T4-B | T4-B: 13.8/4.16 kV station transformer | JB-T4-B-DI01 | T4-B: 13.8/4.16 kV station transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 49 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0617 | A | Power block | Home run JB-T4-B-DI01 to the control / marshalling room | R1 | R1: main electrical building (64 x 180 ft) | JB-T4-B-DI01 | T4-B: 13.8/4.16 kV station transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 752 | 124
A-I-0618 | A | Power block | Instrumentation | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | TCP-1 | TCP-1: GT1 turbine control and protection cabinets | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 178 | 94
A-I-0619 | A | Power block | Instrumentation | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | TCP-2 | TCP-2: GT2 turbine control and protection cabinets | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 1069 | 184
A-I-0620 | A | Power block | Instrumentation | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | TCP-3 | TCP-3: GT3 turbine control and protection cabinets | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 1024 | 240
A-I-0621 | A | Power block | Instrumentation | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | TCP-ST | TCP-ST: ST turbine control and protection cabinets | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 408 | 183
A-I-0622 | A | Power block | Analog instrument to JB JB-UAT-1-AI01: 8 x 1 pr (field cables) | UAT-1 | UAT-1: 21/13.8 kV unit auxiliary transformer | JB-UAT-1-AI01 | UAT-1: 21/13.8 kV unit auxiliary transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 51 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0623 | A | Power block | Home run JB-UAT-1-AI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-UAT-1-AI01 | UAT-1: 21/13.8 kV unit auxiliary transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 566 | 158
A-I-0624 | A | Power block | Discrete device to JB JB-UAT-1-DI01: 16 x 1 pr (field cables) | UAT-1 | UAT-1: 21/13.8 kV unit auxiliary transformer | JB-UAT-1-DI01 | UAT-1: 21/13.8 kV unit auxiliary transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 51 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0625 | A | Power block | Home run JB-UAT-1-DI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-UAT-1-DI01 | UAT-1: 21/13.8 kV unit auxiliary transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 566 | 158
A-I-0626 | A | Power block | Analog instrument to JB JB-UAT-2-AI01: 8 x 1 pr (field cables) | UAT-2 | UAT-2: 21/13.8 kV unit auxiliary transformer | JB-UAT-2-AI01 | UAT-2: 21/13.8 kV unit auxiliary transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 51 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0627 | A | Power block | Home run JB-UAT-2-AI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-UAT-2-AI01 | UAT-2: 21/13.8 kV unit auxiliary transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1423 | 96
A-I-0628 | A | Power block | Discrete device to JB JB-UAT-2-DI01: 16 x 1 pr (field cables) | UAT-2 | UAT-2: 21/13.8 kV unit auxiliary transformer | JB-UAT-2-DI01 | UAT-2: 21/13.8 kV unit auxiliary transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 51 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0629 | A | Power block | Home run JB-UAT-2-DI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-UAT-2-DI01 | UAT-2: 21/13.8 kV unit auxiliary transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1423 | 96
A-I-0630 | A | Power block | Analog instrument to JB JB-UAT-3-AI01: 8 x 1 pr (field cables) | UAT-3 | UAT-3: 21/13.8 kV unit auxiliary transformer | JB-UAT-3-AI01 | UAT-3: 21/13.8 kV unit auxiliary transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 51 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0631 | A | Power block | Home run JB-UAT-3-AI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-UAT-3-AI01 | UAT-3: 21/13.8 kV unit auxiliary transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1103 | 96
A-I-0632 | A | Power block | Discrete device to JB JB-UAT-3-DI01: 16 x 1 pr (field cables) | UAT-3 | UAT-3: 21/13.8 kV unit auxiliary transformer | JB-UAT-3-DI01 | UAT-3: 21/13.8 kV unit auxiliary transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 51 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0633 | A | Power block | Home run JB-UAT-3-DI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-UAT-3-DI01 | UAT-3: 21/13.8 kV unit auxiliary transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1103 | 96
A-I-0634 | A | Power block | Analog instrument to JB JB-WASH-GT1-AI01: 4 x 1 pr (field cables) | WASH-GT1 | WASH-GT1: compressor water-wash skid | JB-WASH-GT1-AI01 | WASH-GT1: compressor water-wash skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0635 | A | Power block | Home run JB-WASH-GT1-AI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-WASH-GT1-AI01 | WASH-GT1: compressor water-wash skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 183 | 94
A-I-0636 | A | Power block | Discrete device to JB JB-WASH-GT1-DI01: 6 x 1 pr (field cables) | WASH-GT1 | WASH-GT1: compressor water-wash skid | JB-WASH-GT1-DI01 | WASH-GT1: compressor water-wash skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0637 | A | Power block | Home run JB-WASH-GT1-DI01 to the control / marshalling room | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | JB-WASH-GT1-DI01 | WASH-GT1: compressor water-wash skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 183 | 94
A-I-0638 | A | Power block | Analog instrument to JB JB-WASH-GT2-AI01: 4 x 1 pr (field cables) | WASH-GT2 | WASH-GT2: compressor water-wash skid | JB-WASH-GT2-AI01 | WASH-GT2: compressor water-wash skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0639 | A | Power block | Home run JB-WASH-GT2-AI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-WASH-GT2-AI01 | WASH-GT2: compressor water-wash skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1075 | 188
A-I-0640 | A | Power block | Discrete device to JB JB-WASH-GT2-DI01: 6 x 1 pr (field cables) | WASH-GT2 | WASH-GT2: compressor water-wash skid | JB-WASH-GT2-DI01 | WASH-GT2: compressor water-wash skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0641 | A | Power block | Home run JB-WASH-GT2-DI01 to the control / marshalling room | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | JB-WASH-GT2-DI01 | WASH-GT2: compressor water-wash skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1075 | 188
A-I-0642 | A | Power block | Analog instrument to JB JB-WASH-GT3-AI01: 4 x 1 pr (field cables) | WASH-GT3 | WASH-GT3: compressor water-wash skid | JB-WASH-GT3-AI01 | WASH-GT3: compressor water-wash skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0643 | A | Power block | Home run JB-WASH-GT3-AI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-WASH-GT3-AI01 | WASH-GT3: compressor water-wash skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1024 | 267
A-I-0644 | A | Power block | Discrete device to JB JB-WASH-GT3-DI01: 6 x 1 pr (field cables) | WASH-GT3 | WASH-GT3: compressor water-wash skid | JB-WASH-GT3-DI01 | WASH-GT3: compressor water-wash skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
A-I-0645 | A | Power block | Home run JB-WASH-GT3-DI01 to the control / marshalling room | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | JB-WASH-GT3-DI01 | WASH-GT3: compressor water-wash skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1024 | 267
A-P-0001 | A | Power block | Motor 1 of 3, 250 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | AC-A/B/C | Air compressors AC-A/B/C | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦4/0 | 3/C+G | 4/0 | 2 | 1 | 480 | 250 | 353.8 | Tray | 88 | 84 |  |  |  |  | VD 0.7 %
A-P-0002 | A | Power block | Motor 2 of 3, 250 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | AC-A/B/C | Air compressors AC-A/B/C | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦4/0 | 3/C+G | 4/0 | 2 | 1 | 480 | 250 | 353.8 | Tray | 88 | 84 |  |  |  |  | VD 0.7 %
A-P-0003 | A | Power block | Motor 3 of 3, 250 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | AC-A/B/C | Air compressors AC-A/B/C | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦4/0 | 3/C+G | 4/0 | 2 | 1 | 480 | 250 | 353.8 | Tray | 88 | 84 |  |  |  |  | VD 0.7 %
A-P-0004 | A | Power block | Motor 1 of 4, 15 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | BFP-1 | BFP-1A/B: boiler feed pumps (13.8 kV DOL) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Tray | 481 | 84 |  |  |  |  | VD 2.3 %
A-P-0005 | A | Power block | Motor 2 of 4, 15 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | BFP-1 | BFP-1A/B: boiler feed pumps (13.8 kV DOL) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Tray | 481 | 84 |  |  |  |  | VD 2.3 %
A-P-0006 | A | Power block | Motor 3 of 4, 15 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | BFP-1 | BFP-1A/B: boiler feed pumps (13.8 kV DOL) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Tray | 481 | 84 |  |  |  |  | VD 2.3 %
A-P-0007 | A | Power block | Motor 4 of 4, 15 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | BFP-1 | BFP-1A/B: boiler feed pumps (13.8 kV DOL) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Tray | 481 | 84 |  |  |  |  | VD 2.3 %
A-P-0008 | A | Power block | Motor 1 of 4, 15 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | BFP-2 | BFP-2A/B: boiler feed pumps (13.8 kV DOL) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Tray | 479 | 84 |  |  |  |  | VD 2.3 %
A-P-0009 | A | Power block | Motor 2 of 4, 15 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | BFP-2 | BFP-2A/B: boiler feed pumps (13.8 kV DOL) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Tray | 479 | 84 |  |  |  |  | VD 2.3 %
A-P-0010 | A | Power block | Motor 3 of 4, 15 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | BFP-2 | BFP-2A/B: boiler feed pumps (13.8 kV DOL) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Tray | 479 | 84 |  |  |  |  | VD 2.3 %
A-P-0011 | A | Power block | Motor 4 of 4, 15 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | BFP-2 | BFP-2A/B: boiler feed pumps (13.8 kV DOL) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Tray | 479 | 84 |  |  |  |  | VD 2.3 %
A-P-0012 | A | Power block | Motor 1 of 4, 15 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | BFP-3 | BFP-3A/B: boiler feed pumps (13.8 kV DOL) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Tray | 481 | 84 |  |  |  |  | VD 2.3 %
A-P-0013 | A | Power block | Motor 2 of 4, 15 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | BFP-3 | BFP-3A/B: boiler feed pumps (13.8 kV DOL) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Tray | 481 | 84 |  |  |  |  | VD 2.3 %
A-P-0014 | A | Power block | Motor 3 of 4, 15 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | BFP-3 | BFP-3A/B: boiler feed pumps (13.8 kV DOL) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Tray | 481 | 84 |  |  |  |  | VD 2.3 %
A-P-0015 | A | Power block | Motor 4 of 4, 15 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | BFP-3 | BFP-3A/B: boiler feed pumps (13.8 kV DOL) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Tray | 481 | 84 |  |  |  |  | VD 2.3 %
A-P-0016 | A | Power block | Bridge crane conductor-bar feeder (fused disconnect, north wall) | LC-480-A | R1 LC-480-A (480 V switchgear) | CRANE | Bridge crane (parked over laydown bay) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 150 | 212.3 | Tray | 361 | 160 |  |  |  |  | VD 1.6 %
A-P-0017 | A | Power block | Motor 1 of 2, 5 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | CEMS-1 | CEMS shelter, HRSG 1 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 5 | 7.1 | Tray | 277 | 97 |  |  |  |  | VD 1.3 %
A-P-0018 | A | Power block | Motor 2 of 2, 5 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | CEMS-1 | CEMS shelter, HRSG 1 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 5 | 7.1 | Tray | 277 | 97 |  |  |  |  | VD 1.3 %
A-P-0019 | A | Power block | Motor 1 of 2, 5 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | CEMS-2 | CEMS shelter, HRSG 2 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 5 | 7.1 | Tray | 273 | 93 |  |  |  |  | VD 1.2 %
A-P-0020 | A | Power block | Motor 2 of 2, 5 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | CEMS-2 | CEMS shelter, HRSG 2 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 5 | 7.1 | Tray | 273 | 93 |  |  |  |  | VD 1.2 %
A-P-0021 | A | Power block | Motor 1 of 2, 5 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | CEMS-3 | CEMS shelter, HRSG 3 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 5 | 7.1 | Tray | 277 | 97 |  |  |  |  | VD 1.3 %
A-P-0022 | A | Power block | Motor 2 of 2, 5 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | CEMS-3 | CEMS shelter, HRSG 3 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 5 | 7.1 | Tray | 277 | 97 |  |  |  |  | VD 1.3 %
A-P-0023 | A | Power block | Motor 1 of 6, 2 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | Chem feed | Chemical feed | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 258 | 35 |  |  |  |  | VD 0.4 %
A-P-0024 | A | Power block | Motor 2 of 6, 2 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | Chem feed | Chemical feed | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 258 | 35 |  |  |  |  | VD 0.4 %
A-P-0025 | A | Power block | Motor 3 of 6, 2 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | Chem feed | Chemical feed | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 258 | 35 |  |  |  |  | VD 0.4 %
A-P-0026 | A | Power block | Motor 4 of 6, 2 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | Chem feed | Chemical feed | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 258 | 35 |  |  |  |  | VD 0.4 %
A-P-0027 | A | Power block | Motor 5 of 6, 2 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | Chem feed | Chemical feed | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 258 | 35 |  |  |  |  | VD 0.4 %
A-P-0028 | A | Power block | Motor 6 of 6, 2 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | Chem feed | Chemical feed | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 258 | 35 |  |  |  |  | VD 0.4 %
A-P-0029 | A | Power block | LV power feeder | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HALL | Common turbine hall | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 15 | 21.2 | Tray | 1069 | 184 |  |  |  |  | VD 2.0 %
A-P-0030 | A | Power block | Motor 1 of 2, 37 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | EHC-ST | EHC-ST: ST electro-hydraulic control power unit | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 37 | 52.4 | Tray | 67 | 89 |  |  |  |  | VD 1.0 %
A-P-0031 | A | Power block | Motor 2 of 2, 37 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | EHC-ST | EHC-ST: ST electro-hydraulic control power unit | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 37 | 52.4 | Tray | 67 | 89 |  |  |  |  | VD 1.0 %
A-P-0032 | A | Power block | Area / platform lighting circuit 1 (8 fixtures) | MCC-GT1 | R1 MCC-GT1 |  | FH-1 stair tower | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Duct bank | 907 | 98 |  |  |  |  | fixture-to-fixture run included
A-P-0033 | A | Power block | Motor 1 of 2, 15 kW | MCC-GT1 | R1 MCC-GT1 | FH-1 | FH-1: GT inlet filter house on its own frame | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Tray | 451 | 157 |  |  |  |  | VD 2.5 %
A-P-0034 | A | Power block | Motor 2 of 2, 15 kW | MCC-GT1 | R1 MCC-GT1 | FH-1 | FH-1: GT inlet filter house on its own frame | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Tray | 451 | 157 |  |  |  |  | VD 2.5 %
A-P-0035 | A | Power block | Area / platform lighting circuit 1 (12 fixtures) | MCC-GT1 | R1 MCC-GT1 | FH-1 | FH-1: GT inlet filter house on its own frame | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 751 | 157 |  |  |  |  | fixture-to-fixture run included
A-P-0036 | A | Power block | Area / platform lighting circuit 1 (8 fixtures) | MCC-GT2 | R1 MCC-GT2 |  | FH-2 stair tower | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Duct bank | 1071 | 110 |  |  |  |  | fixture-to-fixture run included
A-P-0037 | A | Power block | Motor 1 of 2, 15 kW | MCC-GT2 | R1 MCC-GT2 | FH-2 | FH-2: GT inlet filter house on its own frame | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 15 | 21.2 | Tray | 631 | 137 |  |  |  |  | VD 2.0 %
A-P-0038 | A | Power block | Motor 2 of 2, 15 kW | MCC-GT2 | R1 MCC-GT2 | FH-2 | FH-2: GT inlet filter house on its own frame | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 15 | 21.2 | Tray | 631 | 137 |  |  |  |  | VD 2.0 %
A-P-0039 | A | Power block | Area / platform lighting circuit 1 (12 fixtures) | MCC-GT2 | R1 MCC-GT2 | FH-2 | FH-2: GT inlet filter house on its own frame | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 931 | 137 |  |  |  |  | fixture-to-fixture run included
A-P-0040 | A | Power block | Area / platform lighting circuit 1 (8 fixtures) | MCC-GT3 | R1 MCC-GT3 |  | FH-3 stair tower | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 3 | 5 | Tray | 1179 | 172 |  |  |  |  | fixture-to-fixture run included
A-P-0041 | A | Power block | Motor 1 of 2, 15 kW | MCC-GT3 | R1 MCC-GT3 | FH-3 | FH-3: GT inlet filter house on its own frame | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 15 | 21.2 | Tray | 799 | 145 |  |  |  |  | VD 2.4 %
A-P-0042 | A | Power block | Motor 2 of 2, 15 kW | MCC-GT3 | R1 MCC-GT3 | FH-3 | FH-3: GT inlet filter house on its own frame | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 15 | 21.2 | Tray | 799 | 145 |  |  |  |  | VD 2.4 %
A-P-0043 | A | Power block | Area / platform lighting circuit 1 (12 fixtures) | MCC-GT3 | R1 MCC-GT3 | FH-3 | FH-3: GT inlet filter house on its own frame | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 1099 | 145 |  |  |  |  | fixture-to-fixture run included
A-P-0044 | A | Power block | LV power feeder | MCC-GT1 | R1 MCC-GT1 | FS-GT1 | FS-GT1: CO2 fire-suppression skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 150 | 212.3 | Tray | 288 | 155 |  |  |  |  | VD 1.4 %
A-P-0045 | A | Power block | LV power feeder | MCC-GT2 | R1 MCC-GT2 | FS-GT2 | FS-GT2: CO2 fire-suppression skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 150 | 212.3 | Tray | 468 | 135 |  |  |  |  | VD 1.9 %
A-P-0046 | A | Power block | LV power feeder | MCC-GT3 | R1 MCC-GT3 | FS-GT3 | FS-GT3: CO2 fire-suppression skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 150 | 212.3 | Tray | 636 | 143 |  |  |  |  | VD 2.4 %
A-P-0047 | A | Power block | LV power feeder | MCC-GT1 | R1 MCC-GT1 | GFM-1 | GFM-1: GT1 gas fuel module (stop / control valves, final strainer) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 15 | 21.2 | Tray | 298 | 145 |  |  |  |  | VD 2.9 %
A-P-0048 | A | Power block | LV power feeder | MCC-GT2 | R1 MCC-GT2 | GFM-2 | GFM-2: GT2 gas fuel module (stop / control valves, final strainer) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Tray | 478 | 125 |  |  |  |  | VD 2.5 %
A-P-0049 | A | Power block | LV power feeder | MCC-GT3 | R1 MCC-GT3 | GFM-3 | GFM-3: GT3 gas fuel module (stop / control valves, final strainer) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 15 | 21.2 | Tray | 646 | 133 |  |  |  |  | VD 2.0 %
A-P-0050 | A | Power block | Motor 1 of 2, 30 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | GSC-ST | GSC-ST: gland-steam condenser and exhausters | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Tray | 72 | 139 |  |  |  |  | VD 1.7 %
A-P-0051 | A | Power block | Motor 2 of 2, 30 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | GSC-ST | GSC-ST: gland-steam condenser and exhausters | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Tray | 72 | 139 |  |  |  |  | VD 1.7 %
A-P-0052 | A | Power block | Motor 1 of 6, 2 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-1 firewall | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 416 | 181 |  |  |  |  | VD 0.8 %
A-P-0053 | A | Power block | Motor 2 of 6, 2 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-1 firewall | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 416 | 181 |  |  |  |  | VD 0.8 %
A-P-0054 | A | Power block | Motor 3 of 6, 2 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-1 firewall | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 416 | 181 |  |  |  |  | VD 0.8 %
A-P-0055 | A | Power block | Motor 4 of 6, 2 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-1 firewall | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 416 | 181 |  |  |  |  | VD 0.8 %
A-P-0056 | A | Power block | Motor 5 of 6, 2 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-1 firewall | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 416 | 181 |  |  |  |  | VD 0.8 %
A-P-0057 | A | Power block | Motor 6 of 6, 2 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-1 firewall | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 416 | 181 |  |  |  |  | VD 0.8 %
A-P-0058 | A | Power block | Motor 1 of 6, 2 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | GSU-1 | GSU-1: 21/230 kV generator step-up transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 419 | 179 |  |  |  |  | VD 0.8 %
A-P-0059 | A | Power block | Motor 2 of 6, 2 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | GSU-1 | GSU-1: 21/230 kV generator step-up transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 419 | 179 |  |  |  |  | VD 0.8 %
A-P-0060 | A | Power block | Motor 3 of 6, 2 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | GSU-1 | GSU-1: 21/230 kV generator step-up transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 419 | 179 |  |  |  |  | VD 0.8 %
A-P-0061 | A | Power block | Motor 4 of 6, 2 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | GSU-1 | GSU-1: 21/230 kV generator step-up transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 419 | 179 |  |  |  |  | VD 0.8 %
A-P-0062 | A | Power block | Motor 5 of 6, 2 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | GSU-1 | GSU-1: 21/230 kV generator step-up transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 419 | 179 |  |  |  |  | VD 0.8 %
A-P-0063 | A | Power block | Motor 6 of 6, 2 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | GSU-1 | GSU-1: 21/230 kV generator step-up transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 419 | 179 |  |  |  |  | VD 0.8 %
A-P-0064 | A | Power block | Motor 1 of 6, 2 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-2 firewall | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 1290 | 271 |  |  |  |  | VD 2.1 %
A-P-0065 | A | Power block | Motor 2 of 6, 2 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-2 firewall | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 1290 | 271 |  |  |  |  | VD 2.1 %
A-P-0066 | A | Power block | Motor 3 of 6, 2 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-2 firewall | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 1290 | 271 |  |  |  |  | VD 2.1 %
A-P-0067 | A | Power block | Motor 4 of 6, 2 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-2 firewall | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 1290 | 271 |  |  |  |  | VD 2.1 %
A-P-0068 | A | Power block | Motor 5 of 6, 2 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-2 firewall | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 1290 | 271 |  |  |  |  | VD 2.1 %
A-P-0069 | A | Power block | Motor 6 of 6, 2 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-2 firewall | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 1290 | 271 |  |  |  |  | VD 2.1 %
A-P-0070 | A | Power block | Motor 1 of 6, 2 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | GSU-2 | GSU-2: 21/230 kV generator step-up transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 1423 | 113 |  |  |  |  | VD 2.1 %
A-P-0071 | A | Power block | Motor 2 of 6, 2 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | GSU-2 | GSU-2: 21/230 kV generator step-up transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 1423 | 113 |  |  |  |  | VD 2.1 %
A-P-0072 | A | Power block | Motor 3 of 6, 2 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | GSU-2 | GSU-2: 21/230 kV generator step-up transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 1423 | 113 |  |  |  |  | VD 2.1 %
A-P-0073 | A | Power block | Motor 4 of 6, 2 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | GSU-2 | GSU-2: 21/230 kV generator step-up transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 1423 | 113 |  |  |  |  | VD 2.1 %
A-P-0074 | A | Power block | Motor 5 of 6, 2 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | GSU-2 | GSU-2: 21/230 kV generator step-up transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 1423 | 113 |  |  |  |  | VD 2.1 %
A-P-0075 | A | Power block | Motor 6 of 6, 2 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | GSU-2 | GSU-2: 21/230 kV generator step-up transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 1423 | 113 |  |  |  |  | VD 2.1 %
A-P-0076 | A | Power block | Motor 1 of 6, 2 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-3 firewall | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 1140 | 110 |  |  |  |  | VD 1.7 %
A-P-0077 | A | Power block | Motor 2 of 6, 2 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-3 firewall | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 1140 | 110 |  |  |  |  | VD 1.7 %
A-P-0078 | A | Power block | Motor 3 of 6, 2 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-3 firewall | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 1140 | 110 |  |  |  |  | VD 1.7 %
A-P-0079 | A | Power block | Motor 4 of 6, 2 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-3 firewall | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 1140 | 110 |  |  |  |  | VD 1.7 %
A-P-0080 | A | Power block | Motor 5 of 6, 2 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-3 firewall | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 1140 | 110 |  |  |  |  | VD 1.7 %
A-P-0081 | A | Power block | Motor 6 of 6, 2 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | GSU-3 firewall | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 1140 | 110 |  |  |  |  | VD 1.7 %
A-P-0082 | A | Power block | Motor 1 of 6, 2 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | GSU-3 | GSU-3: 21/230 kV generator step-up transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 1103 | 113 |  |  |  |  | VD 1.7 %
A-P-0083 | A | Power block | Motor 2 of 6, 2 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | GSU-3 | GSU-3: 21/230 kV generator step-up transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 1103 | 113 |  |  |  |  | VD 1.7 %
A-P-0084 | A | Power block | Motor 3 of 6, 2 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | GSU-3 | GSU-3: 21/230 kV generator step-up transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 1103 | 113 |  |  |  |  | VD 1.7 %
A-P-0085 | A | Power block | Motor 4 of 6, 2 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | GSU-3 | GSU-3: 21/230 kV generator step-up transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 1103 | 113 |  |  |  |  | VD 1.7 %
A-P-0086 | A | Power block | Motor 5 of 6, 2 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | GSU-3 | GSU-3: 21/230 kV generator step-up transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 1103 | 113 |  |  |  |  | VD 1.7 %
A-P-0087 | A | Power block | Motor 6 of 6, 2 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | GSU-3 | GSU-3: 21/230 kV generator step-up transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 1103 | 113 |  |  |  |  | VD 1.7 %
A-P-0088 | A | Power block | Motor 1 of 6, 2 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) |  | GSU-ST firewall | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 463 | 35 |  |  |  |  | VD 0.7 %
A-P-0089 | A | Power block | Motor 2 of 6, 2 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) |  | GSU-ST firewall | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 463 | 35 |  |  |  |  | VD 0.7 %
A-P-0090 | A | Power block | Motor 3 of 6, 2 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) |  | GSU-ST firewall | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 463 | 35 |  |  |  |  | VD 0.7 %
A-P-0091 | A | Power block | Motor 4 of 6, 2 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) |  | GSU-ST firewall | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 463 | 35 |  |  |  |  | VD 0.7 %
A-P-0092 | A | Power block | Motor 5 of 6, 2 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) |  | GSU-ST firewall | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 463 | 35 |  |  |  |  | VD 0.7 %
A-P-0093 | A | Power block | Motor 6 of 6, 2 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) |  | GSU-ST firewall | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 463 | 35 |  |  |  |  | VD 0.7 %
A-P-0094 | A | Power block | Motor 1 of 6, 2 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | GSU-ST | GSU-ST: 21/230 kV (one ST GSU, baseline) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 408 | 32 |  |  |  |  | VD 0.6 %
A-P-0095 | A | Power block | Motor 2 of 6, 2 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | GSU-ST | GSU-ST: 21/230 kV (one ST GSU, baseline) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 408 | 32 |  |  |  |  | VD 0.6 %
A-P-0096 | A | Power block | Motor 3 of 6, 2 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | GSU-ST | GSU-ST: 21/230 kV (one ST GSU, baseline) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 408 | 32 |  |  |  |  | VD 0.6 %
A-P-0097 | A | Power block | Motor 4 of 6, 2 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | GSU-ST | GSU-ST: 21/230 kV (one ST GSU, baseline) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 408 | 32 |  |  |  |  | VD 0.6 %
A-P-0098 | A | Power block | Motor 5 of 6, 2 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | GSU-ST | GSU-ST: 21/230 kV (one ST GSU, baseline) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 408 | 32 |  |  |  |  | VD 0.6 %
A-P-0099 | A | Power block | Motor 6 of 6, 2 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | GSU-ST | GSU-ST: 21/230 kV (one ST GSU, baseline) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 408 | 32 |  |  |  |  | VD 0.6 %
A-P-0100 | A | Power block | Motor 1 of 12, 45 kW | MCC-GT1 | R1 MCC-GT1 | GT1 aux | GT1 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 45 | 63.7 | Tray | 302 | 170 |  |  |  |  | VD 2.3 %
A-P-0101 | A | Power block | Motor 2 of 12, 45 kW | MCC-GT1 | R1 MCC-GT1 | GT1 aux | GT1 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 45 | 63.7 | Tray | 302 | 170 |  |  |  |  | VD 2.3 %
A-P-0102 | A | Power block | Motor 3 of 12, 45 kW | MCC-GT1 | R1 MCC-GT1 | GT1 aux | GT1 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 45 | 63.7 | Tray | 302 | 170 |  |  |  |  | VD 2.3 %
A-P-0103 | A | Power block | Motor 4 of 12, 45 kW | MCC-GT1 | R1 MCC-GT1 | GT1 aux | GT1 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 45 | 63.7 | Tray | 302 | 170 |  |  |  |  | VD 2.3 %
A-P-0104 | A | Power block | Motor 5 of 12, 45 kW | MCC-GT1 | R1 MCC-GT1 | GT1 aux | GT1 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 45 | 63.7 | Tray | 302 | 170 |  |  |  |  | VD 2.3 %
A-P-0105 | A | Power block | Motor 6 of 12, 45 kW | MCC-GT1 | R1 MCC-GT1 | GT1 aux | GT1 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 45 | 63.7 | Tray | 302 | 170 |  |  |  |  | VD 2.3 %
A-P-0106 | A | Power block | Motor 7 of 12, 45 kW | MCC-GT1 | R1 MCC-GT1 | GT1 aux | GT1 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 45 | 63.7 | Tray | 302 | 170 |  |  |  |  | VD 2.3 %
A-P-0107 | A | Power block | Motor 8 of 12, 45 kW | MCC-GT1 | R1 MCC-GT1 | GT1 aux | GT1 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 45 | 63.7 | Tray | 302 | 170 |  |  |  |  | VD 2.3 %
A-P-0108 | A | Power block | Motor 9 of 12, 45 kW | MCC-GT1 | R1 MCC-GT1 | GT1 aux | GT1 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 45 | 63.7 | Tray | 302 | 170 |  |  |  |  | VD 2.3 %
A-P-0109 | A | Power block | Motor 10 of 12, 45 kW | MCC-GT1 | R1 MCC-GT1 | GT1 aux | GT1 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 45 | 63.7 | Tray | 302 | 170 |  |  |  |  | VD 2.3 %
A-P-0110 | A | Power block | Motor 11 of 12, 45 kW | MCC-GT1 | R1 MCC-GT1 | GT1 aux | GT1 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 45 | 63.7 | Tray | 302 | 170 |  |  |  |  | VD 2.3 %
A-P-0111 | A | Power block | Motor 12 of 12, 45 kW | MCC-GT1 | R1 MCC-GT1 | GT1 aux | GT1 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 45 | 63.7 | Tray | 302 | 170 |  |  |  |  | VD 2.3 %
A-P-0112 | A | Power block | LV power feeder | MCC-GT1 | R1 MCC-GT1 | GT1 | GT1: H-class gas turbine (60 Hz) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 150 | 212.3 | Tray | 232 | 154 |  |  |  |  | VD 1.2 %
A-P-0113 | A | Power block | 480 V welding receptacle 1 | MCC-GT1 | R1 MCC-GT1 | GT1 | GT1: H-class gas turbine (60 Hz) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 232 | 154 |  |  |  |  | VD 2.3 %
A-P-0114 | A | Power block | 480 V welding receptacle 2 | MCC-GT1 | R1 MCC-GT1 | GT1 | GT1: H-class gas turbine (60 Hz) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 232 | 154 |  |  |  |  | VD 2.3 %
A-P-0115 | A | Power block | 480 V welding receptacle 3 | MCC-GT1 | R1 MCC-GT1 | GT1 | GT1: H-class gas turbine (60 Hz) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 232 | 154 |  |  |  |  | VD 2.3 %
A-P-0116 | A | Power block | 480 V welding receptacle 4 | MCC-GT1 | R1 MCC-GT1 | GT1 | GT1: H-class gas turbine (60 Hz) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 232 | 154 |  |  |  |  | VD 2.3 %
A-P-0117 | A | Power block | Motor 1 of 12, 45 kW | MCC-GT2 | R1 MCC-GT2 | GT2 aux | GT2 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 45 | 63.7 | Tray | 482 | 150 |  |  |  |  | VD 2.5 %
A-P-0118 | A | Power block | Motor 2 of 12, 45 kW | MCC-GT2 | R1 MCC-GT2 | GT2 aux | GT2 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 45 | 63.7 | Tray | 482 | 150 |  |  |  |  | VD 2.5 %
A-P-0119 | A | Power block | Motor 3 of 12, 45 kW | MCC-GT2 | R1 MCC-GT2 | GT2 aux | GT2 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 45 | 63.7 | Tray | 482 | 150 |  |  |  |  | VD 2.5 %
A-P-0120 | A | Power block | Motor 4 of 12, 45 kW | MCC-GT2 | R1 MCC-GT2 | GT2 aux | GT2 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 45 | 63.7 | Tray | 482 | 150 |  |  |  |  | VD 2.5 %
A-P-0121 | A | Power block | Motor 5 of 12, 45 kW | MCC-GT2 | R1 MCC-GT2 | GT2 aux | GT2 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 45 | 63.7 | Tray | 482 | 150 |  |  |  |  | VD 2.5 %
A-P-0122 | A | Power block | Motor 6 of 12, 45 kW | MCC-GT2 | R1 MCC-GT2 | GT2 aux | GT2 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 45 | 63.7 | Tray | 482 | 150 |  |  |  |  | VD 2.5 %
A-P-0123 | A | Power block | Motor 7 of 12, 45 kW | MCC-GT2 | R1 MCC-GT2 | GT2 aux | GT2 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 45 | 63.7 | Tray | 482 | 150 |  |  |  |  | VD 2.5 %
A-P-0124 | A | Power block | Motor 8 of 12, 45 kW | MCC-GT2 | R1 MCC-GT2 | GT2 aux | GT2 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 45 | 63.7 | Tray | 482 | 150 |  |  |  |  | VD 2.5 %
A-P-0125 | A | Power block | Motor 9 of 12, 45 kW | MCC-GT2 | R1 MCC-GT2 | GT2 aux | GT2 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 45 | 63.7 | Tray | 482 | 150 |  |  |  |  | VD 2.5 %
A-P-0126 | A | Power block | Motor 10 of 12, 45 kW | MCC-GT2 | R1 MCC-GT2 | GT2 aux | GT2 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 45 | 63.7 | Tray | 482 | 150 |  |  |  |  | VD 2.5 %
A-P-0127 | A | Power block | Motor 11 of 12, 45 kW | MCC-GT2 | R1 MCC-GT2 | GT2 aux | GT2 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 45 | 63.7 | Tray | 482 | 150 |  |  |  |  | VD 2.5 %
A-P-0128 | A | Power block | Motor 12 of 12, 45 kW | MCC-GT2 | R1 MCC-GT2 | GT2 aux | GT2 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 45 | 63.7 | Tray | 482 | 150 |  |  |  |  | VD 2.5 %
A-P-0129 | A | Power block | LV power feeder | MCC-GT2 | R1 MCC-GT2 | GT2 | GT2: H-class gas turbine (60 Hz) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 150 | 212.3 | Tray | 412 | 134 |  |  |  |  | VD 1.7 %
A-P-0130 | A | Power block | 480 V welding receptacle 1 | MCC-GT2 | R1 MCC-GT2 | GT2 | GT2: H-class gas turbine (60 Hz) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 60 | 76 | Tray | 412 | 134 |  |  |  |  | VD 2.5 %
A-P-0131 | A | Power block | 480 V welding receptacle 2 | MCC-GT2 | R1 MCC-GT2 | GT2 | GT2: H-class gas turbine (60 Hz) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 60 | 76 | Tray | 412 | 134 |  |  |  |  | VD 2.5 %
A-P-0132 | A | Power block | 480 V welding receptacle 3 | MCC-GT2 | R1 MCC-GT2 | GT2 | GT2: H-class gas turbine (60 Hz) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 60 | 76 | Tray | 412 | 134 |  |  |  |  | VD 2.5 %
A-P-0133 | A | Power block | 480 V welding receptacle 4 | MCC-GT2 | R1 MCC-GT2 | GT2 | GT2: H-class gas turbine (60 Hz) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 60 | 76 | Tray | 412 | 134 |  |  |  |  | VD 2.5 %
A-P-0134 | A | Power block | Motor 1 of 12, 45 kW | MCC-GT3 | R1 MCC-GT3 | GT3 aux | GT3 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 45 | 63.7 | Tray | 693 | 149 |  |  |  |  | VD 2.6 %
A-P-0135 | A | Power block | Motor 2 of 12, 45 kW | MCC-GT3 | R1 MCC-GT3 | GT3 aux | GT3 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 45 | 63.7 | Tray | 693 | 149 |  |  |  |  | VD 2.6 %
A-P-0136 | A | Power block | Motor 3 of 12, 45 kW | MCC-GT3 | R1 MCC-GT3 | GT3 aux | GT3 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 45 | 63.7 | Tray | 693 | 149 |  |  |  |  | VD 2.6 %
A-P-0137 | A | Power block | Motor 4 of 12, 45 kW | MCC-GT3 | R1 MCC-GT3 | GT3 aux | GT3 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 45 | 63.7 | Tray | 693 | 149 |  |  |  |  | VD 2.6 %
A-P-0138 | A | Power block | Motor 5 of 12, 45 kW | MCC-GT3 | R1 MCC-GT3 | GT3 aux | GT3 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 45 | 63.7 | Tray | 693 | 149 |  |  |  |  | VD 2.6 %
A-P-0139 | A | Power block | Motor 6 of 12, 45 kW | MCC-GT3 | R1 MCC-GT3 | GT3 aux | GT3 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 45 | 63.7 | Tray | 693 | 149 |  |  |  |  | VD 2.6 %
A-P-0140 | A | Power block | Motor 7 of 12, 45 kW | MCC-GT3 | R1 MCC-GT3 | GT3 aux | GT3 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 45 | 63.7 | Tray | 693 | 149 |  |  |  |  | VD 2.6 %
A-P-0141 | A | Power block | Motor 8 of 12, 45 kW | MCC-GT3 | R1 MCC-GT3 | GT3 aux | GT3 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 45 | 63.7 | Tray | 693 | 149 |  |  |  |  | VD 2.6 %
A-P-0142 | A | Power block | Motor 9 of 12, 45 kW | MCC-GT3 | R1 MCC-GT3 | GT3 aux | GT3 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 45 | 63.7 | Tray | 693 | 149 |  |  |  |  | VD 2.6 %
A-P-0143 | A | Power block | Motor 10 of 12, 45 kW | MCC-GT3 | R1 MCC-GT3 | GT3 aux | GT3 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 45 | 63.7 | Tray | 693 | 149 |  |  |  |  | VD 2.6 %
A-P-0144 | A | Power block | Motor 11 of 12, 45 kW | MCC-GT3 | R1 MCC-GT3 | GT3 aux | GT3 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 45 | 63.7 | Tray | 693 | 149 |  |  |  |  | VD 2.6 %
A-P-0145 | A | Power block | Motor 12 of 12, 45 kW | MCC-GT3 | R1 MCC-GT3 | GT3 aux | GT3 aux: lube oil, hydraulics, enclosure fans | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 45 | 63.7 | Tray | 693 | 149 |  |  |  |  | VD 2.6 %
A-P-0146 | A | Power block | LV power feeder | MCC-GT3 | R1 MCC-GT3 | GT3 | GT3: H-class gas turbine (60 Hz) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 150 | 212.3 | Tray | 580 | 142 |  |  |  |  | VD 2.2 %
A-P-0147 | A | Power block | 480 V welding receptacle 1 | MCC-GT3 | R1 MCC-GT3 | GT3 | GT3: H-class gas turbine (60 Hz) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 60 | 76 | Tray | 580 | 142 |  |  |  |  | VD 2.7 %
A-P-0148 | A | Power block | 480 V welding receptacle 2 | MCC-GT3 | R1 MCC-GT3 | GT3 | GT3: H-class gas turbine (60 Hz) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 60 | 76 | Tray | 580 | 142 |  |  |  |  | VD 2.7 %
A-P-0149 | A | Power block | 480 V welding receptacle 3 | MCC-GT3 | R1 MCC-GT3 | GT3 | GT3: H-class gas turbine (60 Hz) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 60 | 76 | Tray | 580 | 142 |  |  |  |  | VD 2.7 %
A-P-0150 | A | Power block | 480 V welding receptacle 4 | MCC-GT3 | R1 MCC-GT3 | GT3 | GT3: H-class gas turbine (60 Hz) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 60 | 76 | Tray | 580 | 142 |  |  |  |  | VD 2.7 %
A-P-0151 | A | Power block | Motor 1 of 4, 2 kW | MCC-GT1 | R1 MCC-GT1 | GTG-1 | GTG-1: GT generator | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 445 | 178 |  |  |  |  | VD 0.8 %
A-P-0152 | A | Power block | Motor 2 of 4, 2 kW | MCC-GT1 | R1 MCC-GT1 | GTG-1 | GTG-1: GT generator | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 445 | 178 |  |  |  |  | VD 0.8 %
A-P-0153 | A | Power block | Motor 3 of 4, 2 kW | MCC-GT1 | R1 MCC-GT1 | GTG-1 | GTG-1: GT generator | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 445 | 178 |  |  |  |  | VD 0.8 %
A-P-0154 | A | Power block | Motor 4 of 4, 2 kW | MCC-GT1 | R1 MCC-GT1 | GTG-1 | GTG-1: GT generator | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 445 | 178 |  |  |  |  | VD 0.8 %
A-P-0155 | A | Power block | Motor 1 of 4, 2 kW | MCC-GT2 | R1 MCC-GT2 | GTG-2 | GTG-2: GT generator | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 625 | 158 |  |  |  |  | VD 1.1 %
A-P-0156 | A | Power block | Motor 2 of 4, 2 kW | MCC-GT2 | R1 MCC-GT2 | GTG-2 | GTG-2: GT generator | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 625 | 158 |  |  |  |  | VD 1.1 %
A-P-0157 | A | Power block | Motor 3 of 4, 2 kW | MCC-GT2 | R1 MCC-GT2 | GTG-2 | GTG-2: GT generator | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 625 | 158 |  |  |  |  | VD 1.1 %
A-P-0158 | A | Power block | Motor 4 of 4, 2 kW | MCC-GT2 | R1 MCC-GT2 | GTG-2 | GTG-2: GT generator | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 625 | 158 |  |  |  |  | VD 1.1 %
A-P-0159 | A | Power block | Motor 1 of 4, 2 kW | MCC-GT3 | R1 MCC-GT3 | GTG-3 | GTG-3: GT generator | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 793 | 166 |  |  |  |  | VD 1.3 %
A-P-0160 | A | Power block | Motor 2 of 4, 2 kW | MCC-GT3 | R1 MCC-GT3 | GTG-3 | GTG-3: GT generator | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 793 | 166 |  |  |  |  | VD 1.3 %
A-P-0161 | A | Power block | Motor 3 of 4, 2 kW | MCC-GT3 | R1 MCC-GT3 | GTG-3 | GTG-3: GT generator | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 793 | 166 |  |  |  |  | VD 1.3 %
A-P-0162 | A | Power block | Motor 4 of 4, 2 kW | MCC-GT3 | R1 MCC-GT3 | GTG-3 | GTG-3: GT generator | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 793 | 166 |  |  |  |  | VD 1.3 %
A-P-0163 | A | Power block | Motor 1 of 4, 15 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Tray | 0 | 87 |  |  |  |  | VD 0.9 %
A-P-0164 | A | Power block | Motor 2 of 4, 15 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Tray | 0 | 87 |  |  |  |  | VD 0.9 %
A-P-0165 | A | Power block | Motor 3 of 4, 15 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Tray | 0 | 87 |  |  |  |  | VD 0.9 %
A-P-0166 | A | Power block | Motor 4 of 4, 15 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Tray | 0 | 87 |  |  |  |  | VD 0.9 %
A-P-0167 | A | Power block | MOV 1: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0168 | A | Power block | MOV 2: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0169 | A | Power block | MOV 3: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0170 | A | Power block | MOV 4: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0171 | A | Power block | MOV 5: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0172 | A | Power block | MOV 6: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0173 | A | Power block | MOV 7: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0174 | A | Power block | MOV 8: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0175 | A | Power block | MOV 9: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0176 | A | Power block | MOV 10: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0177 | A | Power block | MOV 11: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0178 | A | Power block | MOV 12: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0179 | A | Power block | MOV 13: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0180 | A | Power block | MOV 14: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0181 | A | Power block | MOV 15: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0182 | A | Power block | MOV 16: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0183 | A | Power block | MOV 17: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0184 | A | Power block | MOV 18: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0185 | A | Power block | MOV 19: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0186 | A | Power block | MOV 20: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0187 | A | Power block | MOV 21: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0188 | A | Power block | MOV 22: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0189 | A | Power block | MOV 23: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0190 | A | Power block | MOV 24: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0191 | A | Power block | MOV 25: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0192 | A | Power block | MOV 26: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0193 | A | Power block | MOV 27: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0194 | A | Power block | MOV 28: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0195 | A | Power block | MOV 29: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0196 | A | Power block | MOV 30: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0197 | A | Power block | MOV 31: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0198 | A | Power block | MOV 32: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0199 | A | Power block | MOV 33: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0200 | A | Power block | MOV 34: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0201 | A | Power block | MOV 35: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0202 | A | Power block | MOV 36: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0203 | A | Power block | MOV 37: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0204 | A | Power block | MOV 38: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0205 | A | Power block | MOV 39: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0206 | A | Power block | MOV 40: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0207 | A | Power block | MOV 41: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0208 | A | Power block | MOV 42: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0209 | A | Power block | MOV 43: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0210 | A | Power block | MOV 44: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0211 | A | Power block | MOV 45: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0212 | A | Power block | Area / platform lighting circuit 1 (12 fixtures) | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 300 | 87 |  |  |  |  | fixture-to-fixture run included
A-P-0213 | A | Power block | Area / platform lighting circuit 2 (12 fixtures) | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 300 | 87 |  |  |  |  | fixture-to-fixture run included
A-P-0214 | A | Power block | Area / platform lighting circuit 3 (12 fixtures) | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 300 | 87 |  |  |  |  | fixture-to-fixture run included
A-P-0215 | A | Power block | Area / platform lighting circuit 4 (4 fixtures) | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 300 | 87 |  |  |  |  | fixture-to-fixture run included
A-P-0216 | A | Power block | 480 V welding receptacle 1 | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 0 | 87 |  |  |  |  | VD 0.5 %
A-P-0217 | A | Power block | 480 V welding receptacle 2 | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 0 | 87 |  |  |  |  | VD 0.5 %
A-P-0218 | A | Power block | 480 V welding receptacle 3 | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 0 | 87 |  |  |  |  | VD 0.5 %
A-P-0219 | A | Power block | 480 V welding receptacle 4 | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-1 | HRSG 1 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 0 | 87 |  |  |  |  | VD 0.5 %
A-P-0220 | A | Power block | MOV 1: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 1 blowdown tank (continuous / intermittent) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 38 | 86 |  |  |  |  | VD 0.2 %
A-P-0221 | A | Power block | MOV 2: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 1 blowdown tank (continuous / intermittent) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 38 | 86 |  |  |  |  | VD 0.2 %
A-P-0222 | A | Power block | MOV 3: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 1 blowdown tank (continuous / intermittent) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 38 | 86 |  |  |  |  | VD 0.2 %
A-P-0223 | A | Power block | MOV 4: power | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 1 blowdown tank (continuous / intermittent) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 38 | 86 |  |  |  |  | VD 0.2 %
A-P-0224 | A | Power block | LV power feeder | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 1 blowdown tank (continuous / intermittent) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 10 | 14.2 | Tray | 38 | 86 |  |  |  |  | VD 0.8 %
A-P-0225 | A | Power block | Motor 1 of 6, 2 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 1 chemical feed skid (phosphate / amine) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 404 | 108 |  |  |  |  | VD 0.7 %
A-P-0226 | A | Power block | Motor 2 of 6, 2 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 1 chemical feed skid (phosphate / amine) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 404 | 108 |  |  |  |  | VD 0.7 %
A-P-0227 | A | Power block | Motor 3 of 6, 2 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 1 chemical feed skid (phosphate / amine) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 404 | 108 |  |  |  |  | VD 0.7 %
A-P-0228 | A | Power block | Motor 4 of 6, 2 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 1 chemical feed skid (phosphate / amine) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 404 | 108 |  |  |  |  | VD 0.7 %
A-P-0229 | A | Power block | Motor 5 of 6, 2 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 1 chemical feed skid (phosphate / amine) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 404 | 108 |  |  |  |  | VD 0.7 %
A-P-0230 | A | Power block | Motor 6 of 6, 2 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 1 chemical feed skid (phosphate / amine) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 404 | 108 |  |  |  |  | VD 0.7 %
A-P-0231 | A | Power block | Area / platform lighting circuit 1 (6 fixtures) | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | STK-1 | HRSG 1 stack | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 486 | 148 |  |  |  |  | fixture-to-fixture run included
A-P-0232 | A | Power block | Motor 1 of 4, 15 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Tray | 53 | 96 |  |  |  |  | VD 1.5 %
A-P-0233 | A | Power block | Motor 2 of 4, 15 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Tray | 53 | 96 |  |  |  |  | VD 1.5 %
A-P-0234 | A | Power block | Motor 3 of 4, 15 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Tray | 53 | 96 |  |  |  |  | VD 1.5 %
A-P-0235 | A | Power block | Motor 4 of 4, 15 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Tray | 53 | 96 |  |  |  |  | VD 1.5 %
A-P-0236 | A | Power block | MOV 1: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0237 | A | Power block | MOV 2: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0238 | A | Power block | MOV 3: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0239 | A | Power block | MOV 4: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0240 | A | Power block | MOV 5: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0241 | A | Power block | MOV 6: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0242 | A | Power block | MOV 7: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0243 | A | Power block | MOV 8: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0244 | A | Power block | MOV 9: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0245 | A | Power block | MOV 10: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0246 | A | Power block | MOV 11: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0247 | A | Power block | MOV 12: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0248 | A | Power block | MOV 13: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0249 | A | Power block | MOV 14: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0250 | A | Power block | MOV 15: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0251 | A | Power block | MOV 16: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0252 | A | Power block | MOV 17: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0253 | A | Power block | MOV 18: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0254 | A | Power block | MOV 19: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0255 | A | Power block | MOV 20: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0256 | A | Power block | MOV 21: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0257 | A | Power block | MOV 22: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0258 | A | Power block | MOV 23: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0259 | A | Power block | MOV 24: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0260 | A | Power block | MOV 25: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0261 | A | Power block | MOV 26: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0262 | A | Power block | MOV 27: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0263 | A | Power block | MOV 28: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0264 | A | Power block | MOV 29: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0265 | A | Power block | MOV 30: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0266 | A | Power block | MOV 31: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0267 | A | Power block | MOV 32: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0268 | A | Power block | MOV 33: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0269 | A | Power block | MOV 34: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0270 | A | Power block | MOV 35: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0271 | A | Power block | MOV 36: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0272 | A | Power block | MOV 37: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0273 | A | Power block | MOV 38: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0274 | A | Power block | MOV 39: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0275 | A | Power block | MOV 40: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0276 | A | Power block | MOV 41: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0277 | A | Power block | MOV 42: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0278 | A | Power block | MOV 43: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0279 | A | Power block | MOV 44: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0280 | A | Power block | MOV 45: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 53 | 96 |  |  |  |  | VD 0.3 %
A-P-0281 | A | Power block | Area / platform lighting circuit 1 (12 fixtures) | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 353 | 96 |  |  |  |  | fixture-to-fixture run included
A-P-0282 | A | Power block | Area / platform lighting circuit 2 (12 fixtures) | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 353 | 96 |  |  |  |  | fixture-to-fixture run included
A-P-0283 | A | Power block | Area / platform lighting circuit 3 (12 fixtures) | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 353 | 96 |  |  |  |  | fixture-to-fixture run included
A-P-0284 | A | Power block | Area / platform lighting circuit 4 (4 fixtures) | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 353 | 96 |  |  |  |  | fixture-to-fixture run included
A-P-0285 | A | Power block | 480 V welding receptacle 1 | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 53 | 96 |  |  |  |  | VD 0.9 %
A-P-0286 | A | Power block | 480 V welding receptacle 2 | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 53 | 96 |  |  |  |  | VD 0.9 %
A-P-0287 | A | Power block | 480 V welding receptacle 3 | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 53 | 96 |  |  |  |  | VD 0.9 %
A-P-0288 | A | Power block | 480 V welding receptacle 4 | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-2 | HRSG 2 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 53 | 96 |  |  |  |  | VD 0.9 %
A-P-0289 | A | Power block | MOV 1: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 2 blowdown tank (continuous / intermittent) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 38 | 86 |  |  |  |  | VD 0.2 %
A-P-0290 | A | Power block | MOV 2: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 2 blowdown tank (continuous / intermittent) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 38 | 86 |  |  |  |  | VD 0.2 %
A-P-0291 | A | Power block | MOV 3: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 2 blowdown tank (continuous / intermittent) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 38 | 86 |  |  |  |  | VD 0.2 %
A-P-0292 | A | Power block | MOV 4: power | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 2 blowdown tank (continuous / intermittent) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 38 | 86 |  |  |  |  | VD 0.2 %
A-P-0293 | A | Power block | LV power feeder | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 2 blowdown tank (continuous / intermittent) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 10 | 14.2 | Tray | 38 | 86 |  |  |  |  | VD 0.8 %
A-P-0294 | A | Power block | Motor 1 of 6, 2 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 2 chemical feed skid (phosphate / amine) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 404 | 108 |  |  |  |  | VD 0.7 %
A-P-0295 | A | Power block | Motor 2 of 6, 2 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 2 chemical feed skid (phosphate / amine) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 404 | 108 |  |  |  |  | VD 0.7 %
A-P-0296 | A | Power block | Motor 3 of 6, 2 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 2 chemical feed skid (phosphate / amine) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 404 | 108 |  |  |  |  | VD 0.7 %
A-P-0297 | A | Power block | Motor 4 of 6, 2 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 2 chemical feed skid (phosphate / amine) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 404 | 108 |  |  |  |  | VD 0.7 %
A-P-0298 | A | Power block | Motor 5 of 6, 2 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 2 chemical feed skid (phosphate / amine) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 404 | 108 |  |  |  |  | VD 0.7 %
A-P-0299 | A | Power block | Motor 6 of 6, 2 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 2 chemical feed skid (phosphate / amine) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 404 | 108 |  |  |  |  | VD 0.7 %
A-P-0300 | A | Power block | Area / platform lighting circuit 1 (6 fixtures) | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | STK-2 | HRSG 2 stack | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 573 | 135 |  |  |  |  | fixture-to-fixture run included
A-P-0301 | A | Power block | Motor 1 of 4, 15 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Tray | 0 | 87 |  |  |  |  | VD 0.9 %
A-P-0302 | A | Power block | Motor 2 of 4, 15 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Tray | 0 | 87 |  |  |  |  | VD 0.9 %
A-P-0303 | A | Power block | Motor 3 of 4, 15 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Tray | 0 | 87 |  |  |  |  | VD 0.9 %
A-P-0304 | A | Power block | Motor 4 of 4, 15 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Tray | 0 | 87 |  |  |  |  | VD 0.9 %
A-P-0305 | A | Power block | MOV 1: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0306 | A | Power block | MOV 2: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0307 | A | Power block | MOV 3: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0308 | A | Power block | MOV 4: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0309 | A | Power block | MOV 5: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0310 | A | Power block | MOV 6: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0311 | A | Power block | MOV 7: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0312 | A | Power block | MOV 8: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0313 | A | Power block | MOV 9: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0314 | A | Power block | MOV 10: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0315 | A | Power block | MOV 11: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0316 | A | Power block | MOV 12: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0317 | A | Power block | MOV 13: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0318 | A | Power block | MOV 14: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0319 | A | Power block | MOV 15: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0320 | A | Power block | MOV 16: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0321 | A | Power block | MOV 17: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0322 | A | Power block | MOV 18: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0323 | A | Power block | MOV 19: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0324 | A | Power block | MOV 20: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0325 | A | Power block | MOV 21: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0326 | A | Power block | MOV 22: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0327 | A | Power block | MOV 23: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0328 | A | Power block | MOV 24: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0329 | A | Power block | MOV 25: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0330 | A | Power block | MOV 26: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0331 | A | Power block | MOV 27: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0332 | A | Power block | MOV 28: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0333 | A | Power block | MOV 29: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0334 | A | Power block | MOV 30: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0335 | A | Power block | MOV 31: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0336 | A | Power block | MOV 32: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0337 | A | Power block | MOV 33: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0338 | A | Power block | MOV 34: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0339 | A | Power block | MOV 35: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0340 | A | Power block | MOV 36: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0341 | A | Power block | MOV 37: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0342 | A | Power block | MOV 38: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0343 | A | Power block | MOV 39: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0344 | A | Power block | MOV 40: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0345 | A | Power block | MOV 41: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0346 | A | Power block | MOV 42: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0347 | A | Power block | MOV 43: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0348 | A | Power block | MOV 44: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0349 | A | Power block | MOV 45: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 87 |  |  |  |  | VD 0.1 %
A-P-0350 | A | Power block | Area / platform lighting circuit 1 (12 fixtures) | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 300 | 87 |  |  |  |  | fixture-to-fixture run included
A-P-0351 | A | Power block | Area / platform lighting circuit 2 (12 fixtures) | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 300 | 87 |  |  |  |  | fixture-to-fixture run included
A-P-0352 | A | Power block | Area / platform lighting circuit 3 (12 fixtures) | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 300 | 87 |  |  |  |  | fixture-to-fixture run included
A-P-0353 | A | Power block | Area / platform lighting circuit 4 (4 fixtures) | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 300 | 87 |  |  |  |  | fixture-to-fixture run included
A-P-0354 | A | Power block | 480 V welding receptacle 1 | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 0 | 87 |  |  |  |  | VD 0.5 %
A-P-0355 | A | Power block | 480 V welding receptacle 2 | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 0 | 87 |  |  |  |  | VD 0.5 %
A-P-0356 | A | Power block | 480 V welding receptacle 3 | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 0 | 87 |  |  |  |  | VD 0.5 %
A-P-0357 | A | Power block | 480 V welding receptacle 4 | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | HRSG-3 | HRSG 3 + SCR (3P reheat, horizontal) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 0 | 87 |  |  |  |  | VD 0.5 %
A-P-0358 | A | Power block | MOV 1: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 3 blowdown tank (continuous / intermittent) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 38 | 86 |  |  |  |  | VD 0.2 %
A-P-0359 | A | Power block | MOV 2: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 3 blowdown tank (continuous / intermittent) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 38 | 86 |  |  |  |  | VD 0.2 %
A-P-0360 | A | Power block | MOV 3: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 3 blowdown tank (continuous / intermittent) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 38 | 86 |  |  |  |  | VD 0.2 %
A-P-0361 | A | Power block | MOV 4: power | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 3 blowdown tank (continuous / intermittent) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 38 | 86 |  |  |  |  | VD 0.2 %
A-P-0362 | A | Power block | LV power feeder | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 3 blowdown tank (continuous / intermittent) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 10 | 14.2 | Tray | 38 | 86 |  |  |  |  | VD 0.8 %
A-P-0363 | A | Power block | Motor 1 of 6, 2 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 3 chemical feed skid (phosphate / amine) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 404 | 108 |  |  |  |  | VD 0.7 %
A-P-0364 | A | Power block | Motor 2 of 6, 2 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 3 chemical feed skid (phosphate / amine) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 404 | 108 |  |  |  |  | VD 0.7 %
A-P-0365 | A | Power block | Motor 3 of 6, 2 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 3 chemical feed skid (phosphate / amine) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 404 | 108 |  |  |  |  | VD 0.7 %
A-P-0366 | A | Power block | Motor 4 of 6, 2 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 3 chemical feed skid (phosphate / amine) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 404 | 108 |  |  |  |  | VD 0.7 %
A-P-0367 | A | Power block | Motor 5 of 6, 2 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 3 chemical feed skid (phosphate / amine) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 404 | 108 |  |  |  |  | VD 0.7 %
A-P-0368 | A | Power block | Motor 6 of 6, 2 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | HRSG 3 chemical feed skid (phosphate / amine) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 404 | 108 |  |  |  |  | VD 0.7 %
A-P-0369 | A | Power block | Area / platform lighting circuit 1 (6 fixtures) | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | STK-3 | HRSG 3 stack | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 486 | 148 |  |  |  |  | fixture-to-fixture run included
A-P-0370 | A | Power block | LV power feeder | LC-480-B | R1 LC-480-B (480 V switchgear) | HTP-1 | HTP-1: heat-trace panel (rack) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4/0 | 3/C+G | 4/0 | 1 | 1 | 480 | 120 | 169.8 | Tray | 208 | 135 |  |  |  |  | VD 1.4 %
A-P-0371 | A | Power block | Heat-trace circuit 1 (power to the trace junction box) | HTP-1 | HTP-1: heat-trace panel (rack) | HTP-1 | HTP-1: heat-trace panel (rack) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
A-P-0372 | A | Power block | Heat-trace circuit 2 (power to the trace junction box) | HTP-1 | HTP-1: heat-trace panel (rack) | HTP-1 | HTP-1: heat-trace panel (rack) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
A-P-0373 | A | Power block | Heat-trace circuit 3 (power to the trace junction box) | HTP-1 | HTP-1: heat-trace panel (rack) | HTP-1 | HTP-1: heat-trace panel (rack) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
A-P-0374 | A | Power block | Heat-trace circuit 4 (power to the trace junction box) | HTP-1 | HTP-1: heat-trace panel (rack) | HTP-1 | HTP-1: heat-trace panel (rack) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
A-P-0375 | A | Power block | Heat-trace circuit 5 (power to the trace junction box) | HTP-1 | HTP-1: heat-trace panel (rack) | HTP-1 | HTP-1: heat-trace panel (rack) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
A-P-0376 | A | Power block | Heat-trace circuit 6 (power to the trace junction box) | HTP-1 | HTP-1: heat-trace panel (rack) | HTP-1 | HTP-1: heat-trace panel (rack) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
A-P-0377 | A | Power block | Heat-trace circuit 7 (power to the trace junction box) | HTP-1 | HTP-1: heat-trace panel (rack) | HTP-1 | HTP-1: heat-trace panel (rack) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
A-P-0378 | A | Power block | Heat-trace circuit 8 (power to the trace junction box) | HTP-1 | HTP-1: heat-trace panel (rack) | HTP-1 | HTP-1: heat-trace panel (rack) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
A-P-0379 | A | Power block | Heat-trace circuit 9 (power to the trace junction box) | HTP-1 | HTP-1: heat-trace panel (rack) | HTP-1 | HTP-1: heat-trace panel (rack) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
A-P-0380 | A | Power block | Heat-trace circuit 10 (power to the trace junction box) | HTP-1 | HTP-1: heat-trace panel (rack) | HTP-1 | HTP-1: heat-trace panel (rack) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
A-P-0381 | A | Power block | Heat-trace circuit 11 (power to the trace junction box) | HTP-1 | HTP-1: heat-trace panel (rack) | HTP-1 | HTP-1: heat-trace panel (rack) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
A-P-0382 | A | Power block | Heat-trace circuit 12 (power to the trace junction box) | HTP-1 | HTP-1: heat-trace panel (rack) | HTP-1 | HTP-1: heat-trace panel (rack) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
A-P-0383 | A | Power block | Heat-trace circuit 13 (power to the trace junction box) | HTP-1 | HTP-1: heat-trace panel (rack) | HTP-1 | HTP-1: heat-trace panel (rack) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
A-P-0384 | A | Power block | Heat-trace circuit 14 (power to the trace junction box) | HTP-1 | HTP-1: heat-trace panel (rack) | HTP-1 | HTP-1: heat-trace panel (rack) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
A-P-0385 | A | Power block | Heat-trace circuit 15 (power to the trace junction box) | HTP-1 | HTP-1: heat-trace panel (rack) | HTP-1 | HTP-1: heat-trace panel (rack) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
A-P-0386 | A | Power block | Heat-trace circuit 16 (power to the trace junction box) | HTP-1 | HTP-1: heat-trace panel (rack) | HTP-1 | HTP-1: heat-trace panel (rack) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
A-P-0387 | A | Power block | Heat-trace circuit 17 (power to the trace junction box) | HTP-1 | HTP-1: heat-trace panel (rack) | HTP-1 | HTP-1: heat-trace panel (rack) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
A-P-0388 | A | Power block | Heat-trace circuit 18 (power to the trace junction box) | HTP-1 | HTP-1: heat-trace panel (rack) | HTP-1 | HTP-1: heat-trace panel (rack) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
A-P-0389 | A | Power block | Heat-trace circuit 19 (power to the trace junction box) | HTP-1 | HTP-1: heat-trace panel (rack) | HTP-1 | HTP-1: heat-trace panel (rack) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
A-P-0390 | A | Power block | Heat-trace circuit 20 (power to the trace junction box) | HTP-1 | HTP-1: heat-trace panel (rack) | HTP-1 | HTP-1: heat-trace panel (rack) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
A-P-0391 | A | Power block | Heat-trace circuit 21 (power to the trace junction box) | HTP-1 | HTP-1: heat-trace panel (rack) | HTP-1 | HTP-1: heat-trace panel (rack) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
A-P-0392 | A | Power block | Heat-trace circuit 22 (power to the trace junction box) | HTP-1 | HTP-1: heat-trace panel (rack) | HTP-1 | HTP-1: heat-trace panel (rack) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
A-P-0393 | A | Power block | Heat-trace circuit 23 (power to the trace junction box) | HTP-1 | HTP-1: heat-trace panel (rack) | HTP-1 | HTP-1: heat-trace panel (rack) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
A-P-0394 | A | Power block | Heat-trace circuit 24 (power to the trace junction box) | HTP-1 | HTP-1: heat-trace panel (rack) | HTP-1 | HTP-1: heat-trace panel (rack) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
A-P-0395 | A | Power block | Motor 1 of 6, 2 kW | LC-480-B | R1 LC-480-B (480 V switchgear) | LCT-A | LCT-A: 13.8/0.48 kV load-centre transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 51 | 41 |  |  |  |  | VD 0.1 %
A-P-0396 | A | Power block | Motor 2 of 6, 2 kW | LC-480-B | R1 LC-480-B (480 V switchgear) | LCT-A | LCT-A: 13.8/0.48 kV load-centre transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 51 | 41 |  |  |  |  | VD 0.1 %
A-P-0397 | A | Power block | Motor 3 of 6, 2 kW | LC-480-B | R1 LC-480-B (480 V switchgear) | LCT-A | LCT-A: 13.8/0.48 kV load-centre transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 51 | 41 |  |  |  |  | VD 0.1 %
A-P-0398 | A | Power block | Motor 4 of 6, 2 kW | LC-480-B | R1 LC-480-B (480 V switchgear) | LCT-A | LCT-A: 13.8/0.48 kV load-centre transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 51 | 41 |  |  |  |  | VD 0.1 %
A-P-0399 | A | Power block | Motor 5 of 6, 2 kW | LC-480-B | R1 LC-480-B (480 V switchgear) | LCT-A | LCT-A: 13.8/0.48 kV load-centre transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 51 | 41 |  |  |  |  | VD 0.1 %
A-P-0400 | A | Power block | Motor 6 of 6, 2 kW | LC-480-B | R1 LC-480-B (480 V switchgear) | LCT-A | LCT-A: 13.8/0.48 kV load-centre transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 51 | 41 |  |  |  |  | VD 0.1 %
A-P-0401 | A | Power block | Motor 1 of 6, 2 kW | LC-480-B | R1 LC-480-B (480 V switchgear) | LCT-B | LCT-B: 13.8/0.48 kV load-centre transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 51 | 63 |  |  |  |  | VD 0.2 %
A-P-0402 | A | Power block | Motor 2 of 6, 2 kW | LC-480-B | R1 LC-480-B (480 V switchgear) | LCT-B | LCT-B: 13.8/0.48 kV load-centre transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 51 | 63 |  |  |  |  | VD 0.2 %
A-P-0403 | A | Power block | Motor 3 of 6, 2 kW | LC-480-B | R1 LC-480-B (480 V switchgear) | LCT-B | LCT-B: 13.8/0.48 kV load-centre transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 51 | 63 |  |  |  |  | VD 0.2 %
A-P-0404 | A | Power block | Motor 4 of 6, 2 kW | LC-480-B | R1 LC-480-B (480 V switchgear) | LCT-B | LCT-B: 13.8/0.48 kV load-centre transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 51 | 63 |  |  |  |  | VD 0.2 %
A-P-0405 | A | Power block | Motor 5 of 6, 2 kW | LC-480-B | R1 LC-480-B (480 V switchgear) | LCT-B | LCT-B: 13.8/0.48 kV load-centre transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 51 | 63 |  |  |  |  | VD 0.2 %
A-P-0406 | A | Power block | Motor 6 of 6, 2 kW | LC-480-B | R1 LC-480-B (480 V switchgear) | LCT-B | LCT-B: 13.8/0.48 kV load-centre transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 51 | 63 |  |  |  |  | VD 0.2 %
A-P-0407 | A | Power block | EDG-1 480 V output to EMCC | EDG-1 | EDG-1: 3 MW emergency diesel generator (480 V) | EMCC | R1 EMCC (emergency MCC) | LV 600 V | XHHW-2 600 V 1/C Cu (feeder sets in tray / duct) | LV1C¦1/C¦500 | 1/C | 500 kcmil | 13 | 4 | 480 | 3000 | 3609 | Tray | 890 | 194 |  |  |  |  | 13 sets of 4 x 1/C 500 kcmil for 3 % VD (or bus duct)
A-P-0408 | A | Power block | EDG-2 480 V output to EMCC | EDG-2 | EDG-2: 3 MW emergency diesel generator (480 V) | EMCC | R1 EMCC (emergency MCC) | LV 600 V | XHHW-2 600 V 1/C Cu (feeder sets in tray / duct) | LV1C¦1/C¦500 | 1/C | 500 kcmil | 13 | 4 | 480 | 3000 | 3609 | Tray | 972 | 192 |  |  |  |  | 13 sets of 4 x 1/C 500 kcmil for 3 % VD (or bus duct)
A-P-0409 | A | Power block | EMCC normal supply from LC-480-A | LC-480-A | R1 LC-480-A (480 V switchgear) | EMCC | R1 EMCC (emergency MCC) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦500 | 3/C+G | 500 kcmil | 2 | 1 | 480 | 400 | 506.5 | Tray | 0 | 70 |  |  |  |  | VD 0.2 %
A-P-0410 | A | Power block | LV panel / distribution feeder | LC-480-A | R1 LC-480-A (480 V switchgear) | R1 | R1: main electrical building (64 x 180 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 138 | 195.3 | Tray | 627 | 152 |  |  |  |  | VD 2.2 %
A-P-0411 | A | Power block | LV panel / distribution feeder | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Tray | 0 | 72 |  |  |  |  | VD 0.6 %
A-P-0412 | A | Power block | LV panel / distribution feeder | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Tray | 0 | 72 |  |  |  |  | VD 0.6 %
A-P-0413 | A | Power block | LV panel / distribution feeder | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Tray | 0 | 72 |  |  |  |  | VD 0.6 %
A-P-0414 | A | Power block | LV panel / distribution feeder | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4/0 | 3/C+G | 4/0 | 2 | 1 | 480 | 250 | 353.8 | Tray | 0 | 32 |  |  |  |  | VD 0.1 %
A-P-0415 | A | Power block | Motor 1 of 2, 110 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | SCRB-1 | SCRB-1A/B: SCR dilution-air blowers | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦3/0 | 3/C+G | 3/0 | 1 | 1 | 480 | 110 | 155.7 | Tray | 404 | 72 |  |  |  |  | VD 2.3 %
A-P-0416 | A | Power block | Motor 2 of 2, 110 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | SCRB-1 | SCRB-1A/B: SCR dilution-air blowers | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦3/0 | 3/C+G | 3/0 | 1 | 1 | 480 | 110 | 155.7 | Tray | 404 | 72 |  |  |  |  | VD 2.3 %
A-P-0417 | A | Power block | Motor 1 of 2, 110 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | SCRB-2 | SCRB-2A/B: SCR dilution-air blowers | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦3/0 | 3/C+G | 3/0 | 1 | 1 | 480 | 110 | 155.7 | Tray | 404 | 72 |  |  |  |  | VD 2.3 %
A-P-0418 | A | Power block | Motor 2 of 2, 110 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | SCRB-2 | SCRB-2A/B: SCR dilution-air blowers | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦3/0 | 3/C+G | 3/0 | 1 | 1 | 480 | 110 | 155.7 | Tray | 404 | 72 |  |  |  |  | VD 2.3 %
A-P-0419 | A | Power block | Motor 1 of 2, 110 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | SCRB-3 | SCRB-3A/B: SCR dilution-air blowers | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦3/0 | 3/C+G | 3/0 | 1 | 1 | 480 | 110 | 155.7 | Tray | 404 | 72 |  |  |  |  | VD 2.3 %
A-P-0420 | A | Power block | Motor 2 of 2, 110 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | SCRB-3 | SCRB-3A/B: SCR dilution-air blowers | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦3/0 | 3/C+G | 3/0 | 1 | 1 | 480 | 110 | 155.7 | Tray | 404 | 72 |  |  |  |  | VD 2.3 %
A-P-0421 | A | Power block | Motor 1 of 3, 15 kW | MCC-GT1 | R1 MCC-GT1 | SOS-1 | SOS-1: GTG-1 seal-oil and H2 / CO2 gas-control skid | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Tray | 481 | 189 |  |  |  |  | VD 2.8 %
A-P-0422 | A | Power block | Motor 2 of 3, 15 kW | MCC-GT1 | R1 MCC-GT1 | SOS-1 | SOS-1: GTG-1 seal-oil and H2 / CO2 gas-control skid | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Tray | 481 | 189 |  |  |  |  | VD 2.8 %
A-P-0423 | A | Power block | Motor 3 of 3, 15 kW | MCC-GT1 | R1 MCC-GT1 | SOS-1 | SOS-1: GTG-1 seal-oil and H2 / CO2 gas-control skid | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Tray | 481 | 189 |  |  |  |  | VD 2.8 %
A-P-0424 | A | Power block | Motor 1 of 3, 15 kW | MCC-GT2 | R1 MCC-GT2 | SOS-2 | SOS-2: GTG-2 seal-oil and H2 / CO2 gas-control skid | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 15 | 21.2 | Tray | 661 | 169 |  |  |  |  | VD 2.2 %
A-P-0425 | A | Power block | Motor 2 of 3, 15 kW | MCC-GT2 | R1 MCC-GT2 | SOS-2 | SOS-2: GTG-2 seal-oil and H2 / CO2 gas-control skid | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 15 | 21.2 | Tray | 661 | 169 |  |  |  |  | VD 2.2 %
A-P-0426 | A | Power block | Motor 3 of 3, 15 kW | MCC-GT2 | R1 MCC-GT2 | SOS-2 | SOS-2: GTG-2 seal-oil and H2 / CO2 gas-control skid | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 15 | 21.2 | Tray | 661 | 169 |  |  |  |  | VD 2.2 %
A-P-0427 | A | Power block | Motor 1 of 3, 15 kW | MCC-GT3 | R1 MCC-GT3 | SOS-3 | SOS-3: GTG-3 seal-oil and H2 / CO2 gas-control skid | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 15 | 21.2 | Tray | 829 | 177 |  |  |  |  | VD 2.6 %
A-P-0428 | A | Power block | Motor 2 of 3, 15 kW | MCC-GT3 | R1 MCC-GT3 | SOS-3 | SOS-3: GTG-3 seal-oil and H2 / CO2 gas-control skid | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 15 | 21.2 | Tray | 829 | 177 |  |  |  |  | VD 2.6 %
A-P-0429 | A | Power block | Motor 3 of 3, 15 kW | MCC-GT3 | R1 MCC-GT3 | SOS-3 | SOS-3: GTG-3 seal-oil and H2 / CO2 gas-control skid | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 15 | 21.2 | Tray | 829 | 177 |  |  |  |  | VD 2.6 %
A-P-0430 | A | Power block | Motor 1 of 10, 40 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST aux | ST aux: lube oil, turning gear, EHC | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 40 | 56.6 | Tray | 67 | 84 |  |  |  |  | VD 1.0 %
A-P-0431 | A | Power block | Motor 2 of 10, 40 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST aux | ST aux: lube oil, turning gear, EHC | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 40 | 56.6 | Tray | 67 | 84 |  |  |  |  | VD 1.0 %
A-P-0432 | A | Power block | Motor 3 of 10, 40 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST aux | ST aux: lube oil, turning gear, EHC | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 40 | 56.6 | Tray | 67 | 84 |  |  |  |  | VD 1.0 %
A-P-0433 | A | Power block | Motor 4 of 10, 40 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST aux | ST aux: lube oil, turning gear, EHC | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 40 | 56.6 | Tray | 67 | 84 |  |  |  |  | VD 1.0 %
A-P-0434 | A | Power block | Motor 5 of 10, 40 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST aux | ST aux: lube oil, turning gear, EHC | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 40 | 56.6 | Tray | 67 | 84 |  |  |  |  | VD 1.0 %
A-P-0435 | A | Power block | Motor 6 of 10, 40 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST aux | ST aux: lube oil, turning gear, EHC | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 40 | 56.6 | Tray | 67 | 84 |  |  |  |  | VD 1.0 %
A-P-0436 | A | Power block | Motor 7 of 10, 40 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST aux | ST aux: lube oil, turning gear, EHC | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 40 | 56.6 | Tray | 67 | 84 |  |  |  |  | VD 1.0 %
A-P-0437 | A | Power block | Motor 8 of 10, 40 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST aux | ST aux: lube oil, turning gear, EHC | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 40 | 56.6 | Tray | 67 | 84 |  |  |  |  | VD 1.0 %
A-P-0438 | A | Power block | Motor 9 of 10, 40 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST aux | ST aux: lube oil, turning gear, EHC | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 40 | 56.6 | Tray | 67 | 84 |  |  |  |  | VD 1.0 %
A-P-0439 | A | Power block | Motor 10 of 10, 40 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST aux | ST aux: lube oil, turning gear, EHC | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 40 | 56.6 | Tray | 67 | 84 |  |  |  |  | VD 1.0 %
A-P-0440 | A | Power block | MOV 1: power | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 12 | 50 |  |  |  |  | VD 0.1 %
A-P-0441 | A | Power block | MOV 2: power | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 12 | 50 |  |  |  |  | VD 0.1 %
A-P-0442 | A | Power block | MOV 3: power | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 12 | 50 |  |  |  |  | VD 0.1 %
A-P-0443 | A | Power block | MOV 4: power | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 12 | 50 |  |  |  |  | VD 0.1 %
A-P-0444 | A | Power block | MOV 5: power | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 12 | 50 |  |  |  |  | VD 0.1 %
A-P-0445 | A | Power block | MOV 6: power | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 12 | 50 |  |  |  |  | VD 0.1 %
A-P-0446 | A | Power block | MOV 7: power | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 12 | 50 |  |  |  |  | VD 0.1 %
A-P-0447 | A | Power block | MOV 8: power | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 12 | 50 |  |  |  |  | VD 0.1 %
A-P-0448 | A | Power block | MOV 9: power | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 12 | 50 |  |  |  |  | VD 0.1 %
A-P-0449 | A | Power block | MOV 10: power | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 12 | 50 |  |  |  |  | VD 0.1 %
A-P-0450 | A | Power block | MOV 11: power | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 12 | 50 |  |  |  |  | VD 0.1 %
A-P-0451 | A | Power block | MOV 12: power | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 12 | 50 |  |  |  |  | VD 0.1 %
A-P-0452 | A | Power block | MOV 13: power | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 12 | 50 |  |  |  |  | VD 0.1 %
A-P-0453 | A | Power block | MOV 14: power | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 12 | 50 |  |  |  |  | VD 0.1 %
A-P-0454 | A | Power block | MOV 15: power | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 12 | 50 |  |  |  |  | VD 0.1 %
A-P-0455 | A | Power block | MOV 16: power | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 12 | 50 |  |  |  |  | VD 0.1 %
A-P-0456 | A | Power block | MOV 17: power | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 12 | 50 |  |  |  |  | VD 0.1 %
A-P-0457 | A | Power block | MOV 18: power | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 12 | 50 |  |  |  |  | VD 0.1 %
A-P-0458 | A | Power block | MOV 19: power | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 12 | 50 |  |  |  |  | VD 0.1 %
A-P-0459 | A | Power block | MOV 20: power | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 12 | 50 |  |  |  |  | VD 0.1 %
A-P-0460 | A | Power block | LV power feeder | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 12 | 50 |  |  |  |  | VD 0.6 %
A-P-0461 | A | Power block | 480 V welding receptacle 1 | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Duct bank | 12 | 50 |  |  |  |  | VD 0.4 %
A-P-0462 | A | Power block | 480 V welding receptacle 2 | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Duct bank | 12 | 50 |  |  |  |  | VD 0.4 %
A-P-0463 | A | Power block | 480 V welding receptacle 3 | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Duct bank | 12 | 50 |  |  |  |  | VD 0.4 %
A-P-0464 | A | Power block | 480 V welding receptacle 4 | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | ST | ST: steam turbine (HP/IP + LP), ACC plant | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Duct bank | 12 | 50 |  |  |  |  | VD 0.4 %
A-P-0465 | A | Power block | Motor 1 of 4, 2 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | STG | STG: steam-turbine generator | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 517 | 35 |  |  |  |  | VD 0.8 %
A-P-0466 | A | Power block | Motor 2 of 4, 2 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | STG | STG: steam-turbine generator | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 517 | 35 |  |  |  |  | VD 0.8 %
A-P-0467 | A | Power block | Motor 3 of 4, 2 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | STG | STG: steam-turbine generator | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 517 | 35 |  |  |  |  | VD 0.8 %
A-P-0468 | A | Power block | Motor 4 of 4, 2 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | STG | STG: steam-turbine generator | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 517 | 35 |  |  |  |  | VD 0.8 %
A-P-0469 | A | Power block | LV power feeder | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | SWAS | SWAS: steam and water analysis | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 258 | 32 |  |  |  |  | VD 3.0 %
A-P-0470 | A | Power block | Motor 1 of 6, 2 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2A: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 0 | 86 |  |  |  |  | VD 0.1 %
A-P-0471 | A | Power block | Motor 2 of 6, 2 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2A: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 0 | 86 |  |  |  |  | VD 0.1 %
A-P-0472 | A | Power block | Motor 3 of 6, 2 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2A: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 0 | 86 |  |  |  |  | VD 0.1 %
A-P-0473 | A | Power block | Motor 4 of 6, 2 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2A: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 0 | 86 |  |  |  |  | VD 0.1 %
A-P-0474 | A | Power block | Motor 5 of 6, 2 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2A: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 0 | 86 |  |  |  |  | VD 0.1 %
A-P-0475 | A | Power block | Motor 6 of 6, 2 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2A: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 0 | 86 |  |  |  |  | VD 0.1 %
A-P-0476 | A | Power block | Motor 1 of 6, 2 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2B: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 0 | 97 |  |  |  |  | VD 0.1 %
A-P-0477 | A | Power block | Motor 2 of 6, 2 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2B: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 0 | 97 |  |  |  |  | VD 0.1 %
A-P-0478 | A | Power block | Motor 3 of 6, 2 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2B: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 0 | 97 |  |  |  |  | VD 0.1 %
A-P-0479 | A | Power block | Motor 4 of 6, 2 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2B: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 0 | 97 |  |  |  |  | VD 0.1 %
A-P-0480 | A | Power block | Motor 5 of 6, 2 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2B: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 0 | 97 |  |  |  |  | VD 0.1 %
A-P-0481 | A | Power block | Motor 6 of 6, 2 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2B: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 0 | 97 |  |  |  |  | VD 0.1 %
A-P-0482 | A | Power block | Motor 1 of 6, 2 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2C: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 0 | 97 |  |  |  |  | VD 0.1 %
A-P-0483 | A | Power block | Motor 2 of 6, 2 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2C: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 0 | 97 |  |  |  |  | VD 0.1 %
A-P-0484 | A | Power block | Motor 3 of 6, 2 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2C: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 0 | 97 |  |  |  |  | VD 0.1 %
A-P-0485 | A | Power block | Motor 4 of 6, 2 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2C: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 0 | 97 |  |  |  |  | VD 0.1 %
A-P-0486 | A | Power block | Motor 5 of 6, 2 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2C: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 0 | 97 |  |  |  |  | VD 0.1 %
A-P-0487 | A | Power block | Motor 6 of 6, 2 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) |  | T-R2C: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 0 | 97 |  |  |  |  | VD 0.1 %
A-P-0488 | A | Power block | Motor 1 of 6, 2 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) |  | T-R3: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 0 | 71 |  |  |  |  | VD 0.1 %
A-P-0489 | A | Power block | Motor 2 of 6, 2 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) |  | T-R3: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 0 | 71 |  |  |  |  | VD 0.1 %
A-P-0490 | A | Power block | Motor 3 of 6, 2 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) |  | T-R3: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 0 | 71 |  |  |  |  | VD 0.1 %
A-P-0491 | A | Power block | Motor 4 of 6, 2 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) |  | T-R3: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 0 | 71 |  |  |  |  | VD 0.1 %
A-P-0492 | A | Power block | Motor 5 of 6, 2 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) |  | T-R3: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 0 | 71 |  |  |  |  | VD 0.1 %
A-P-0493 | A | Power block | Motor 6 of 6, 2 kW | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) |  | T-R3: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 0 | 71 |  |  |  |  | VD 0.1 %
A-P-0494 | A | Power block | Motor 1 of 6, 2 kW | LC-480-B | R1 LC-480-B (480 V switchgear) | T4-A | T4-A: 13.8/4.16 kV station transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 63 | 41 |  |  |  |  | VD 0.1 %
A-P-0495 | A | Power block | Motor 2 of 6, 2 kW | LC-480-B | R1 LC-480-B (480 V switchgear) | T4-A | T4-A: 13.8/4.16 kV station transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 63 | 41 |  |  |  |  | VD 0.1 %
A-P-0496 | A | Power block | Motor 3 of 6, 2 kW | LC-480-B | R1 LC-480-B (480 V switchgear) | T4-A | T4-A: 13.8/4.16 kV station transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 63 | 41 |  |  |  |  | VD 0.1 %
A-P-0497 | A | Power block | Motor 4 of 6, 2 kW | LC-480-B | R1 LC-480-B (480 V switchgear) | T4-A | T4-A: 13.8/4.16 kV station transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 63 | 41 |  |  |  |  | VD 0.1 %
A-P-0498 | A | Power block | Motor 5 of 6, 2 kW | LC-480-B | R1 LC-480-B (480 V switchgear) | T4-A | T4-A: 13.8/4.16 kV station transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 63 | 41 |  |  |  |  | VD 0.1 %
A-P-0499 | A | Power block | Motor 6 of 6, 2 kW | LC-480-B | R1 LC-480-B (480 V switchgear) | T4-A | T4-A: 13.8/4.16 kV station transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 63 | 41 |  |  |  |  | VD 0.1 %
A-P-0500 | A | Power block | Motor 1 of 6, 2 kW | LC-480-B | R1 LC-480-B (480 V switchgear) | T4-B | T4-B: 13.8/4.16 kV station transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 85 | 41 |  |  |  |  | VD 0.2 %
A-P-0501 | A | Power block | Motor 2 of 6, 2 kW | LC-480-B | R1 LC-480-B (480 V switchgear) | T4-B | T4-B: 13.8/4.16 kV station transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 85 | 41 |  |  |  |  | VD 0.2 %
A-P-0502 | A | Power block | Motor 3 of 6, 2 kW | LC-480-B | R1 LC-480-B (480 V switchgear) | T4-B | T4-B: 13.8/4.16 kV station transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 85 | 41 |  |  |  |  | VD 0.2 %
A-P-0503 | A | Power block | Motor 4 of 6, 2 kW | LC-480-B | R1 LC-480-B (480 V switchgear) | T4-B | T4-B: 13.8/4.16 kV station transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 85 | 41 |  |  |  |  | VD 0.2 %
A-P-0504 | A | Power block | Motor 5 of 6, 2 kW | LC-480-B | R1 LC-480-B (480 V switchgear) | T4-B | T4-B: 13.8/4.16 kV station transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 85 | 41 |  |  |  |  | VD 0.2 %
A-P-0505 | A | Power block | Motor 6 of 6, 2 kW | LC-480-B | R1 LC-480-B (480 V switchgear) | T4-B | T4-B: 13.8/4.16 kV station transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 85 | 41 |  |  |  |  | VD 0.2 %
A-P-0506 | A | Power block | LV power feeder | MCC-GT1 | R1 MCC-GT1 | TCP-1 | TCP-1: GT1 turbine control and protection cabinets | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 15 | 21.2 | Tray | 256 | 145 |  |  |  |  | VD 2.6 %
A-P-0507 | A | Power block | LV power feeder | MCC-GT2 | R1 MCC-GT2 | TCP-2 | TCP-2: GT2 turbine control and protection cabinets | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Tray | 436 | 125 |  |  |  |  | VD 2.3 %
A-P-0508 | A | Power block | LV power feeder | MCC-GT3 | R1 MCC-GT3 | TCP-3 | TCP-3: GT3 turbine control and protection cabinets | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 15 | 21.2 | Tray | 604 | 133 |  |  |  |  | VD 1.9 %
A-P-0509 | A | Power block | LV power feeder | R3 | R3: ST auxiliary electrical e-house (40 x 65 ft) | TCP-ST | TCP-ST: ST turbine control and protection cabinets | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Tray | 408 | 183 |  |  |  |  | VD 2.4 %
A-P-0510 | A | Power block | Turbine hall roof exhausters / louvres / exterior lighting panel | LC-480-A | R1 LC-480-A (480 V switchgear) |  | Turbine hall exterior electrical: MC-cable risers, roof exhausters, wa | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦3/0 | 3/C+G | 3/0 | 1 | 1 | 480 | 120 | 151.9 | Tray | 506 | 136 |  |  |  |  | VD 3.0 %
A-P-0511 | A | Power block | Motor 1 of 6, 2 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | UAT-1 | UAT-1: 21/13.8 kV unit auxiliary transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 566 | 158 |  |  |  |  | VD 1.0 %
A-P-0512 | A | Power block | Motor 2 of 6, 2 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | UAT-1 | UAT-1: 21/13.8 kV unit auxiliary transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 566 | 158 |  |  |  |  | VD 1.0 %
A-P-0513 | A | Power block | Motor 3 of 6, 2 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | UAT-1 | UAT-1: 21/13.8 kV unit auxiliary transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 566 | 158 |  |  |  |  | VD 1.0 %
A-P-0514 | A | Power block | Motor 4 of 6, 2 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | UAT-1 | UAT-1: 21/13.8 kV unit auxiliary transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 566 | 158 |  |  |  |  | VD 1.0 %
A-P-0515 | A | Power block | Motor 5 of 6, 2 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | UAT-1 | UAT-1: 21/13.8 kV unit auxiliary transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 566 | 158 |  |  |  |  | VD 1.0 %
A-P-0516 | A | Power block | Motor 6 of 6, 2 kW | R2A | R2A: unit / HRSG electrical e-house (32 x 40 ft) | UAT-1 | UAT-1: 21/13.8 kV unit auxiliary transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 566 | 158 |  |  |  |  | VD 1.0 %
A-P-0517 | A | Power block | Motor 1 of 6, 2 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | UAT-2 | UAT-2: 21/13.8 kV unit auxiliary transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 1423 | 96 |  |  |  |  | VD 2.1 %
A-P-0518 | A | Power block | Motor 2 of 6, 2 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | UAT-2 | UAT-2: 21/13.8 kV unit auxiliary transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 1423 | 96 |  |  |  |  | VD 2.1 %
A-P-0519 | A | Power block | Motor 3 of 6, 2 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | UAT-2 | UAT-2: 21/13.8 kV unit auxiliary transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 1423 | 96 |  |  |  |  | VD 2.1 %
A-P-0520 | A | Power block | Motor 4 of 6, 2 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | UAT-2 | UAT-2: 21/13.8 kV unit auxiliary transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 1423 | 96 |  |  |  |  | VD 2.1 %
A-P-0521 | A | Power block | Motor 5 of 6, 2 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | UAT-2 | UAT-2: 21/13.8 kV unit auxiliary transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 1423 | 96 |  |  |  |  | VD 2.1 %
A-P-0522 | A | Power block | Motor 6 of 6, 2 kW | R2B | R2B: unit / HRSG electrical e-house (32 x 40 ft) | UAT-2 | UAT-2: 21/13.8 kV unit auxiliary transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 1423 | 96 |  |  |  |  | VD 2.1 %
A-P-0523 | A | Power block | Motor 1 of 6, 2 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | UAT-3 | UAT-3: 21/13.8 kV unit auxiliary transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 1103 | 96 |  |  |  |  | VD 1.6 %
A-P-0524 | A | Power block | Motor 2 of 6, 2 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | UAT-3 | UAT-3: 21/13.8 kV unit auxiliary transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 1103 | 96 |  |  |  |  | VD 1.6 %
A-P-0525 | A | Power block | Motor 3 of 6, 2 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | UAT-3 | UAT-3: 21/13.8 kV unit auxiliary transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 1103 | 96 |  |  |  |  | VD 1.6 %
A-P-0526 | A | Power block | Motor 4 of 6, 2 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | UAT-3 | UAT-3: 21/13.8 kV unit auxiliary transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 1103 | 96 |  |  |  |  | VD 1.6 %
A-P-0527 | A | Power block | Motor 5 of 6, 2 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | UAT-3 | UAT-3: 21/13.8 kV unit auxiliary transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 1103 | 96 |  |  |  |  | VD 1.6 %
A-P-0528 | A | Power block | Motor 6 of 6, 2 kW | R2C | R2C: unit / HRSG electrical e-house (32 x 40 ft) | UAT-3 | UAT-3: 21/13.8 kV unit auxiliary transformer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 1103 | 96 |  |  |  |  | VD 1.6 %
A-P-0529 | A | Power block | Motor 1 of 2, 22 kW | MCC-GT1 | R1 MCC-GT1 | WASH-GT1 | WASH-GT1: compressor water-wash skid | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 22 | 31.1 | Tray | 261 | 145 |  |  |  |  | VD 2.5 %
A-P-0530 | A | Power block | Motor 2 of 2, 22 kW | MCC-GT1 | R1 MCC-GT1 | WASH-GT1 | WASH-GT1: compressor water-wash skid | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 22 | 31.1 | Tray | 261 | 145 |  |  |  |  | VD 2.5 %
A-P-0531 | A | Power block | Motor 1 of 2, 22 kW | MCC-GT2 | R1 MCC-GT2 | WASH-GT2 | WASH-GT2: compressor water-wash skid | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Tray | 441 | 125 |  |  |  |  | VD 2.2 %
A-P-0532 | A | Power block | Motor 2 of 2, 22 kW | MCC-GT2 | R1 MCC-GT2 | WASH-GT2 | WASH-GT2: compressor water-wash skid | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Tray | 441 | 125 |  |  |  |  | VD 2.2 %
A-P-0533 | A | Power block | Motor 1 of 2, 22 kW | MCC-GT3 | R1 MCC-GT3 | WASH-GT3 | WASH-GT3: compressor water-wash skid | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Tray | 609 | 133 |  |  |  |  | VD 2.8 %
A-P-0534 | A | Power block | Motor 2 of 2, 22 kW | MCC-GT3 | R1 MCC-GT3 | WASH-GT3 | WASH-GT3: compressor water-wash skid | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Tray | 609 | 133 |  |  |  |  | VD 2.8 %
A-MV-0001 | A | Power block | Boiler feed pump BFP-1A / 1B | SWGR-13.8-1 | R1 SWGR-13.8-1 (11 x 36 in cubicles, 15 kV metal-clad) | BFP-1 | BFP-1A/B: boiler feed pumps (13.8 kV DOL) | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦250 | 1/C | 250 kcmil | 1 | 3 | 13800 | 5000 | 232 | Tray | 1041 | 206 |  |  |  |  | 2 x 100 %, ~5 MW each (typ.)
A-MV-0002 | A | Power block | Boiler feed pump BFP-1A / 1B | SWGR-13.8-1 | R1 SWGR-13.8-1 (11 x 36 in cubicles, 15 kV metal-clad) | BFP-1 | BFP-1A/B: boiler feed pumps (13.8 kV DOL) | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦250 | 1/C | 250 kcmil | 1 | 3 | 13800 | 5000 | 232 | Tray | 1041 | 206 |  |  |  |  | 2 x 100 %, ~5 MW each (typ.)
A-MV-0003 | A | Power block | Boiler feed pump BFP-2A / 2B | SWGR-13.8-2 | R1 SWGR-13.8-2 (11 x 36 in cubicles, 15 kV metal-clad) | BFP-2 | BFP-2A/B: boiler feed pumps (13.8 kV DOL) | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦250 | 1/C | 250 kcmil | 1 | 3 | 13800 | 5000 | 232 | Tray | 673 | 130 |  |  |  |  | 2 x 100 %, ~5 MW each (typ.)
A-MV-0004 | A | Power block | Boiler feed pump BFP-2A / 2B | SWGR-13.8-2 | R1 SWGR-13.8-2 (11 x 36 in cubicles, 15 kV metal-clad) | BFP-2 | BFP-2A/B: boiler feed pumps (13.8 kV DOL) | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦250 | 1/C | 250 kcmil | 1 | 3 | 13800 | 5000 | 232 | Tray | 673 | 130 |  |  |  |  | 2 x 100 %, ~5 MW each (typ.)
A-MV-0005 | A | Power block | Boiler feed pump BFP-3A / 3B | SWGR-13.8-3 | R1 SWGR-13.8-3 (11 x 36 in cubicles, 15 kV metal-clad) | BFP-3 | BFP-3A/B: boiler feed pumps (13.8 kV DOL) | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦250 | 1/C | 250 kcmil | 1 | 3 | 13800 | 5000 | 232 | Tray | 823 | 112 |  |  |  |  | 2 x 100 %, ~5 MW each (typ.)
A-MV-0006 | A | Power block | Boiler feed pump BFP-3A / 3B | SWGR-13.8-3 | R1 SWGR-13.8-3 (11 x 36 in cubicles, 15 kV metal-clad) | BFP-3 | BFP-3A/B: boiler feed pumps (13.8 kV DOL) | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦250 | 1/C | 250 kcmil | 1 | 3 | 13800 | 5000 | 232 | Tray | 823 | 112 |  |  |  |  | 2 x 100 %, ~5 MW each (typ.)
A-MV-0007 | A | Power block | LCT-A unit / load-centre transformer primary | SWGR-13.8-1 | R1 SWGR-13.8-1 (11 x 36 in cubicles, 15 kV metal-clad) | LCT-A | LCT-A: 13.8/0.48 kV load-centre transformer | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦1/0 | 1/C | 1/0 | 1 | 3 | 13800 | 3000 | 126 | Tray | 620 | 130
A-MV-0008 | A | Power block | LCT-B unit / load-centre transformer primary | SWGR-13.8-3 | R1 SWGR-13.8-3 (11 x 36 in cubicles, 15 kV metal-clad) | LCT-B | LCT-B: 13.8/0.48 kV load-centre transformer | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦1/0 | 1/C | 1/0 | 1 | 3 | 13800 | 3000 | 126 | Duct bank | 67 | 58
A-MV-0009 | A | Power block | UAT-1 secondary to SWGR-13.8-1 incomer | UAT-1 | UAT-1: 21/13.8 kV unit auxiliary transformer | SWGR-13.8-1 | R1 SWGR-13.8-1 (11 x 36 in cubicles, 15 kV metal-clad) | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦750 | 1/C | 750 kcmil | 4 | 3 | 13800 | 40000 | 1674 | Tray | 644 | 170 |  |  |  |  | 40 MVA UAT (typ.); often non-segregated bus duct instead of cable
A-MV-0010 | A | Power block | UAT-2 secondary to SWGR-13.8-2 incomer | UAT-2 | UAT-2: 21/13.8 kV unit auxiliary transformer | SWGR-13.8-2 | R1 SWGR-13.8-2 (11 x 36 in cubicles, 15 kV metal-clad) | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦750 | 1/C | 750 kcmil | 4 | 3 | 13800 | 40000 | 1674 | Tray | 804 | 215 |  |  |  |  | 40 MVA UAT (typ.); often non-segregated bus duct instead of cable
A-MV-0011 | A | Power block | UAT-3 secondary to SWGR-13.8-3 incomer | UAT-3 | UAT-3: 21/13.8 kV unit auxiliary transformer | SWGR-13.8-3 | R1 SWGR-13.8-3 (11 x 36 in cubicles, 15 kV metal-clad) | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦750 | 1/C | 750 kcmil | 4 | 3 | 13800 | 40000 | 1674 | Tray | 976 | 124 |  |  |  |  | 40 MVA UAT (typ.); often non-segregated bus duct instead of cable
A-MV-0012 | A | Power block | Static starter LCI-1 input transformer | SWGR-13.8-1 | R1 SWGR-13.8-1 (11 x 36 in cubicles, 15 kV metal-clad) | TX-LCI-1 | R1 TX-LCI-1 dry-type input transformer | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦750 | 1/C | 750 kcmil | 1 | 3 | 13800 | 9000 | 377 | Duct bank | 82 | 79
A-MV-0013 | A | Power block | Static starter LCI-2 input transformer | SWGR-13.8-2 | R1 SWGR-13.8-2 (11 x 36 in cubicles, 15 kV metal-clad) | TX-LCI-2 | R1 TX-LCI-2 dry-type input transformer | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦750 | 1/C | 750 kcmil | 1 | 3 | 13800 | 9000 | 377 | Tray | 0 | 126
A-MV-0014 | A | Power block | Static starter LCI-3 input transformer | SWGR-13.8-3 | R1 SWGR-13.8-3 (11 x 36 in cubicles, 15 kV metal-clad) | TX-LCI-3 | R1 TX-LCI-3 dry-type input transformer | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦750 | 1/C | 750 kcmil | 1 | 3 | 13800 | 9000 | 377 | Duct bank | 16 | 56
A-MV-0015 | A | Power block | T-R2A unit / load-centre transformer primary | SWGR-13.8-1 | R1 SWGR-13.8-1 (11 x 36 in cubicles, 15 kV metal-clad) |  | T-R2A: 13.8/0.48 kV | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦2 | 1/C | 2 | 1 | 3 | 13800 | 2500 | 105 | Tray | 104 | 72
A-MV-0016 | A | Power block | T-R2B unit / load-centre transformer primary | SWGR-13.8-2 | R1 SWGR-13.8-2 (11 x 36 in cubicles, 15 kV metal-clad) |  | T-R2B: 13.8/0.48 kV | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦2 | 1/C | 2 | 1 | 3 | 13800 | 2500 | 105 | Tray | 523 | 130
A-MV-0017 | A | Power block | T-R2C unit / load-centre transformer primary | SWGR-13.8-3 | R1 SWGR-13.8-3 (11 x 36 in cubicles, 15 kV metal-clad) |  | T-R2C: 13.8/0.48 kV | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦2 | 1/C | 2 | 1 | 3 | 13800 | 2500 | 105 | Tray | 671 | 112
A-MV-0018 | A | Power block | T-R3 unit / load-centre transformer primary | SWGR-13.8-2 | R1 SWGR-13.8-2 (11 x 36 in cubicles, 15 kV metal-clad) |  | T-R3: 13.8/0.48 kV | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦1/0 | 1/C | 1/0 | 1 | 3 | 13800 | 3000 | 126 | Tray | 897 | 249
A-MV-0019 | A | Power block | T4-A station transformer primary | SWGR-13.8-1 | R1 SWGR-13.8-1 (11 x 36 in cubicles, 15 kV metal-clad) | T4-A | T4-A: 13.8/4.16 kV station transformer | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦750 | 1/C | 750 kcmil | 1 | 3 | 13800 | 10000 | 418 | Tray | 632 | 130
A-MV-0020 | A | Power block | T4-B station transformer primary | SWGR-13.8-3 | R1 SWGR-13.8-3 (11 x 36 in cubicles, 15 kV metal-clad) | T4-B | T4-B: 13.8/4.16 kV station transformer | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦750 | 1/C | 750 kcmil | 1 | 3 | 13800 | 10000 | 418 | Duct bank | 101 | 36
A-MV-0021 | A | Power block | Excitation transformer ET-1 from the IPB tap | GSU-1 | GSU-1: 21/230 kV generator step-up transformer | ET-1 | ET-1: excitation transformer (dry type, GTG-1 terminals) | MV 25 kV | MV-105 25 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket | MV25¦1/C¦2 | 1/C | 2 | 1 | 3 | 21000 | 3000 | 82 | Duct bank | 21 | 38 |  |  |  |  | 21 kV from the generator terminals (IPB tap)
A-MV-0022 | A | Power block | Excitation transformer ET-2 from the IPB tap | GSU-2 | GSU-2: 21/230 kV generator step-up transformer | ET-2 | ET-2: excitation transformer (dry type, GTG-2 terminals) | MV 25 kV | MV-105 25 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket | MV25¦1/C¦2 | 1/C | 2 | 1 | 3 | 21000 | 3000 | 82 | Duct bank | 21 | 38 |  |  |  |  | 21 kV from the generator terminals (IPB tap)
A-MV-0023 | A | Power block | Excitation transformer ET-3 from the IPB tap | GSU-3 | GSU-3: 21/230 kV generator step-up transformer | ET-3 | ET-3: excitation transformer (dry type, GTG-3 terminals) | MV 25 kV | MV-105 25 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket | MV25¦1/C¦2 | 1/C | 2 | 1 | 3 | 21000 | 3000 | 82 | Duct bank | 21 | 38 |  |  |  |  | 21 kV from the generator terminals (IPB tap)
A-MV-0024 | A | Power block | T4-A secondary to SWGR-4.16-A incomer | T4-A | T4-A: 13.8/4.16 kV station transformer | SWGR-4.16-A | R1 SWGR-4.16-A (9 x 36 in cubicles, 5 kV metal-clad) | MV 5 kV | MV-105 5 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV5S¦1/C¦1000 | 1/C | 1000 kcmil | 3 | 3 | 4160 | 10000 | 1388 | Tray | 644 | 134
A-MV-0025 | A | Power block | T4-B secondary to SWGR-4.16-B incomer | T4-B | T4-B: 13.8/4.16 kV station transformer | SWGR-4.16-B | R1 SWGR-4.16-B (5 kV metal-clad) | MV 5 kV | MV-105 5 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV5S¦1/C¦1000 | 1/C | 1000 kcmil | 3 | 3 | 4160 | 10000 | 1388 | Duct bank | 85 | 79
B-L-0001 | B | ACC | Lighting, receptacles and small power branch circuits (allowance) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | THHN¦1/C¦12 | 1/C | 12 | 1 | 1 | 277 |  |  | Conduit | 11520 | 0 |  |  |  |  | allowance: 1.6 ft of conductor per ft2 of floor
B-C-0001 | B | ACC | ACC fan F01 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F01 | ACC fan motor F01 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 389 | 44
B-C-0002 | B | ACC | ACC fan F02 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F02 | ACC fan motor F02 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 357 | 44
B-C-0003 | B | ACC | ACC fan F03 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F03 | ACC fan motor F03 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 325 | 44
B-C-0004 | B | ACC | ACC fan F04 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F04 | ACC fan motor F04 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 293 | 44
B-C-0005 | B | ACC | ACC fan F05 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F05 | ACC fan motor F05 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 261 | 44
B-C-0006 | B | ACC | ACC fan F06 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F06 | ACC fan motor F06 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 261 | 44
B-C-0007 | B | ACC | ACC fan F07 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F07 | ACC fan motor F07 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 293 | 44
B-C-0008 | B | ACC | ACC fan F08 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F08 | ACC fan motor F08 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 325 | 44
B-C-0009 | B | ACC | ACC fan F09 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F09 | ACC fan motor F09 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 357 | 44
B-C-0010 | B | ACC | ACC fan F10 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F10 | ACC fan motor F10 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 389 | 44
B-C-0011 | B | ACC | ACC fan F11 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F11 | ACC fan motor F11 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 339 | 44
B-C-0012 | B | ACC | ACC fan F12 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F12 | ACC fan motor F12 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 307 | 44
B-C-0013 | B | ACC | ACC fan F13 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F13 | ACC fan motor F13 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 275 | 44
B-C-0014 | B | ACC | ACC fan F14 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F14 | ACC fan motor F14 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 243 | 44
B-C-0015 | B | ACC | ACC fan F15 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F15 | ACC fan motor F15 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 211 | 44
B-C-0016 | B | ACC | ACC fan F16 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F16 | ACC fan motor F16 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 211 | 44
B-C-0017 | B | ACC | ACC fan F17 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F17 | ACC fan motor F17 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 243 | 44
B-C-0018 | B | ACC | ACC fan F18 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F18 | ACC fan motor F18 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 275 | 44
B-C-0019 | B | ACC | ACC fan F19 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F19 | ACC fan motor F19 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 307 | 44
B-C-0020 | B | ACC | ACC fan F20 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F20 | ACC fan motor F20 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 339 | 44
B-C-0021 | B | ACC | ACC fan F21 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F21 | ACC fan motor F21 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 289 | 44
B-C-0022 | B | ACC | ACC fan F22 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F22 | ACC fan motor F22 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 257 | 44
B-C-0023 | B | ACC | ACC fan F23 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F23 | ACC fan motor F23 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 225 | 44
B-C-0024 | B | ACC | ACC fan F24 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F24 | ACC fan motor F24 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 193 | 44
B-C-0025 | B | ACC | ACC fan F25 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F25 | ACC fan motor F25 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 161 | 44
B-C-0026 | B | ACC | ACC fan F26 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F26 | ACC fan motor F26 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 161 | 44
B-C-0027 | B | ACC | ACC fan F27 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F27 | ACC fan motor F27 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 193 | 44
B-C-0028 | B | ACC | ACC fan F28 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F28 | ACC fan motor F28 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 225 | 44
B-C-0029 | B | ACC | ACC fan F29 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F29 | ACC fan motor F29 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 257 | 44
B-C-0030 | B | ACC | ACC fan F30 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F30 | ACC fan motor F30 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 289 | 44
B-C-0031 | B | ACC | ACC fan F31 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F31 | ACC fan motor F31 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 239 | 44
B-C-0032 | B | ACC | ACC fan F32 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F32 | ACC fan motor F32 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 207 | 44
B-C-0033 | B | ACC | ACC fan F33 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F33 | ACC fan motor F33 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 175 | 44
B-C-0034 | B | ACC | ACC fan F34 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F34 | ACC fan motor F34 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 143 | 44
B-C-0035 | B | ACC | ACC fan F35 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F35 | ACC fan motor F35 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 111 | 44
B-C-0036 | B | ACC | ACC fan F36 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F36 | ACC fan motor F36 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 111 | 44
B-C-0037 | B | ACC | ACC fan F37 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F37 | ACC fan motor F37 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 143 | 44
B-C-0038 | B | ACC | ACC fan F38 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F38 | ACC fan motor F38 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 175 | 44
B-C-0039 | B | ACC | ACC fan F39 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F39 | ACC fan motor F39 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 207 | 44
B-C-0040 | B | ACC | ACC fan F40 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F40 | ACC fan motor F40 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 239 | 44
B-C-0041 | B | ACC | ACC fan F41 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F41 | ACC fan motor F41 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 239 | 44
B-C-0042 | B | ACC | ACC fan F42 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F42 | ACC fan motor F42 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 207 | 44
B-C-0043 | B | ACC | ACC fan F43 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F43 | ACC fan motor F43 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 175 | 44
B-C-0044 | B | ACC | ACC fan F44 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F44 | ACC fan motor F44 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 143 | 44
B-C-0045 | B | ACC | ACC fan F45 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F45 | ACC fan motor F45 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 111 | 44
B-C-0046 | B | ACC | ACC fan F46 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F46 | ACC fan motor F46 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 111 | 44
B-C-0047 | B | ACC | ACC fan F47 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F47 | ACC fan motor F47 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 143 | 44
B-C-0048 | B | ACC | ACC fan F48 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F48 | ACC fan motor F48 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 175 | 44
B-C-0049 | B | ACC | ACC fan F49 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F49 | ACC fan motor F49 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 207 | 44
B-C-0050 | B | ACC | ACC fan F50 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F50 | ACC fan motor F50 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 239 | 44
B-C-0051 | B | ACC | ACC fan F51 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F51 | ACC fan motor F51 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 289 | 44
B-C-0052 | B | ACC | ACC fan F52 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F52 | ACC fan motor F52 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 257 | 44
B-C-0053 | B | ACC | ACC fan F53 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F53 | ACC fan motor F53 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 225 | 44
B-C-0054 | B | ACC | ACC fan F54 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F54 | ACC fan motor F54 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 193 | 44
B-C-0055 | B | ACC | ACC fan F55 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F55 | ACC fan motor F55 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 161 | 44
B-C-0056 | B | ACC | ACC fan F56 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F56 | ACC fan motor F56 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 161 | 44
B-C-0057 | B | ACC | ACC fan F57 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F57 | ACC fan motor F57 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 193 | 44
B-C-0058 | B | ACC | ACC fan F58 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F58 | ACC fan motor F58 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 225 | 44
B-C-0059 | B | ACC | ACC fan F59 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F59 | ACC fan motor F59 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 257 | 44
B-C-0060 | B | ACC | ACC fan F60 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F60 | ACC fan motor F60 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 289 | 44
B-C-0061 | B | ACC | ACC fan F61 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F61 | ACC fan motor F61 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 339 | 44
B-C-0062 | B | ACC | ACC fan F62 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F62 | ACC fan motor F62 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 307 | 44
B-C-0063 | B | ACC | ACC fan F63 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F63 | ACC fan motor F63 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 275 | 44
B-C-0064 | B | ACC | ACC fan F64 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F64 | ACC fan motor F64 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 243 | 44
B-C-0065 | B | ACC | ACC fan F65 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F65 | ACC fan motor F65 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 211 | 44
B-C-0066 | B | ACC | ACC fan F66 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F66 | ACC fan motor F66 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 211 | 44
B-C-0067 | B | ACC | ACC fan F67 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F67 | ACC fan motor F67 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 243 | 44
B-C-0068 | B | ACC | ACC fan F68 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F68 | ACC fan motor F68 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 275 | 44
B-C-0069 | B | ACC | ACC fan F69 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F69 | ACC fan motor F69 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 307 | 44
B-C-0070 | B | ACC | ACC fan F70 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F70 | ACC fan motor F70 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 339 | 44
B-C-0071 | B | ACC | ACC fan F71 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F71 | ACC fan motor F71 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 389 | 44
B-C-0072 | B | ACC | ACC fan F72 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F72 | ACC fan motor F72 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 357 | 44
B-C-0073 | B | ACC | ACC fan F73 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F73 | ACC fan motor F73 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 325 | 44
B-C-0074 | B | ACC | ACC fan F74 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F74 | ACC fan motor F74 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 293 | 44
B-C-0075 | B | ACC | ACC fan F75 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F75 | ACC fan motor F75 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 261 | 44
B-C-0076 | B | ACC | ACC fan F76 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F76 | ACC fan motor F76 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 261 | 44
B-C-0077 | B | ACC | ACC fan F77 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F77 | ACC fan motor F77 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 293 | 44
B-C-0078 | B | ACC | ACC fan F78 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F78 | ACC fan motor F78 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 325 | 44
B-C-0079 | B | ACC | ACC fan F79 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F79 | ACC fan motor F79 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 357 | 44
B-C-0080 | B | ACC | ACC fan F80 vibration / RTD / local station | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F80 | ACC fan motor F80 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 389 | 44
B-C-0081 | B | ACC | MOV 1: control |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 52
B-C-0082 | B | ACC | MOV 2: control |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 52
B-C-0083 | B | ACC | MOV 3: control |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 52
B-C-0084 | B | ACC | MOV 4: control |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 52
B-C-0085 | B | ACC | MOV 5: control |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 52
B-C-0086 | B | ACC | MOV 6: control |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 52
B-C-0087 | B | ACC | MOV 7: control |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 52
B-C-0088 | B | ACC | MOV 8: control |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 52
B-C-0089 | B | ACC | MOV 9: control |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 52
B-C-0090 | B | ACC | MOV 10: control |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 52
B-C-0091 | B | ACC | MOV 11: control |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 52
B-C-0092 | B | ACC | MOV 12: control |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 52
B-C-0093 | B | ACC | MOV 13: control |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 52
B-C-0094 | B | ACC | MOV 14: control |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 52
B-C-0095 | B | ACC | MOV 15: control |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 52
B-C-0096 | B | ACC | MOV 16: control |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 52
B-C-0097 | B | ACC | MOV 17: control |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 52
B-C-0098 | B | ACC | MOV 18: control |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 52
B-C-0099 | B | ACC | MOV 19: control |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 52
B-C-0100 | B | ACC | MOV 20: control |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 52
B-C-0101 | B | ACC | MOV 21: control |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 52
B-C-0102 | B | ACC | MOV 22: control |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 52
B-C-0103 | B | ACC | MOV 23: control |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 52
B-C-0104 | B | ACC | MOV 24: control |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 52
B-C-0105 | B | ACC | MOV 25: control |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 52
B-C-0106 | B | ACC | MOV 26: control |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 52
B-C-0107 | B | ACC | MOV 27: control |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 52
B-C-0108 | B | ACC | MOV 28: control |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 52
B-C-0109 | B | ACC | MOV 29: control |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 52
B-C-0110 | B | ACC | MOV 30: control |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 52
B-C-0111 | B | ACC | Motor 1 of 12: control / local station |  | R4 480 V switchgear + vacuum-pump MCC | AUXC | Aux dry coolers AUXC-F01..12 (closed cooling water) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 655 | 211
B-C-0112 | B | ACC | Motor 2 of 12: control / local station |  | R4 480 V switchgear + vacuum-pump MCC | AUXC | Aux dry coolers AUXC-F01..12 (closed cooling water) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 655 | 211
B-C-0113 | B | ACC | Motor 3 of 12: control / local station |  | R4 480 V switchgear + vacuum-pump MCC | AUXC | Aux dry coolers AUXC-F01..12 (closed cooling water) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 655 | 211
B-C-0114 | B | ACC | Motor 4 of 12: control / local station |  | R4 480 V switchgear + vacuum-pump MCC | AUXC | Aux dry coolers AUXC-F01..12 (closed cooling water) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 655 | 211
B-C-0115 | B | ACC | Motor 5 of 12: control / local station |  | R4 480 V switchgear + vacuum-pump MCC | AUXC | Aux dry coolers AUXC-F01..12 (closed cooling water) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 655 | 211
B-C-0116 | B | ACC | Motor 6 of 12: control / local station |  | R4 480 V switchgear + vacuum-pump MCC | AUXC | Aux dry coolers AUXC-F01..12 (closed cooling water) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 655 | 211
B-C-0117 | B | ACC | Motor 7 of 12: control / local station |  | R4 480 V switchgear + vacuum-pump MCC | AUXC | Aux dry coolers AUXC-F01..12 (closed cooling water) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 655 | 211
B-C-0118 | B | ACC | Motor 8 of 12: control / local station |  | R4 480 V switchgear + vacuum-pump MCC | AUXC | Aux dry coolers AUXC-F01..12 (closed cooling water) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 655 | 211
B-C-0119 | B | ACC | Motor 9 of 12: control / local station |  | R4 480 V switchgear + vacuum-pump MCC | AUXC | Aux dry coolers AUXC-F01..12 (closed cooling water) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 655 | 211
B-C-0120 | B | ACC | Motor 10 of 12: control / local station |  | R4 480 V switchgear + vacuum-pump MCC | AUXC | Aux dry coolers AUXC-F01..12 (closed cooling water) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 655 | 211
B-C-0121 | B | ACC | Motor 11 of 12: control / local station |  | R4 480 V switchgear + vacuum-pump MCC | AUXC | Aux dry coolers AUXC-F01..12 (closed cooling water) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 655 | 211
B-C-0122 | B | ACC | Motor 12 of 12: control / local station |  | R4 480 V switchgear + vacuum-pump MCC | AUXC | Aux dry coolers AUXC-F01..12 (closed cooling water) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 655 | 211
B-C-0123 | B | ACC | Motor 1 of 2: control / local station |  | R4 480 V switchgear + vacuum-pump MCC | CCW-A/B | CCW-A/B: closed cooling water pumps | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 664 | 175
B-C-0124 | B | ACC | Motor 2 of 2: control / local station |  | R4 480 V switchgear + vacuum-pump MCC | CCW-A/B | CCW-A/B: closed cooling water pumps | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 664 | 175
B-C-0125 | B | ACC | Control | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | VFD-L1 | R4 VFD lineup 1 (23 drives, fed from T-R4-1) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 18 | 81
B-C-0126 | B | ACC | Control | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | VFD-L1 | R4 VFD lineup 1 (23 drives, fed from T-R4-1) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 18 | 81
B-C-0127 | B | ACC | CT / VT | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | VFD-L1 | R4 VFD lineup 1 (23 drives, fed from T-R4-1) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 18 | 81
B-C-0128 | B | ACC | CT / VT | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | VFD-L1 | R4 VFD lineup 1 (23 drives, fed from T-R4-1) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 18 | 81
B-C-0129 | B | ACC | Control | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | VFD-L2 | R4 VFD lineup 2 (23 drives, fed from T-R4-2) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 91
B-C-0130 | B | ACC | Control | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | VFD-L2 | R4 VFD lineup 2 (23 drives, fed from T-R4-2) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 91
B-C-0131 | B | ACC | CT / VT | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | VFD-L2 | R4 VFD lineup 2 (23 drives, fed from T-R4-2) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 0 | 91
B-C-0132 | B | ACC | CT / VT | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | VFD-L2 | R4 VFD lineup 2 (23 drives, fed from T-R4-2) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 0 | 91
B-C-0133 | B | ACC | Control | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | VFD-L3 | R4 VFD lineup 3 (23 drives, fed from T-R4-3) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 73
B-C-0134 | B | ACC | Control | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | VFD-L3 | R4 VFD lineup 3 (23 drives, fed from T-R4-3) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 73
B-C-0135 | B | ACC | CT / VT | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | VFD-L3 | R4 VFD lineup 3 (23 drives, fed from T-R4-3) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 0 | 73
B-C-0136 | B | ACC | CT / VT | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | VFD-L3 | R4 VFD lineup 3 (23 drives, fed from T-R4-3) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 0 | 73
B-C-0137 | B | ACC | Control | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | VFD-L4 | R4 VFD lineup 4 (23 drives, fed from T-R4-4) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 61
B-C-0138 | B | ACC | Control | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | VFD-L4 | R4 VFD lineup 4 (23 drives, fed from T-R4-4) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 61
B-C-0139 | B | ACC | CT / VT | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | VFD-L4 | R4 VFD lineup 4 (23 drives, fed from T-R4-4) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 0 | 61
B-C-0140 | B | ACC | CT / VT | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | VFD-L4 | R4 VFD lineup 4 (23 drives, fed from T-R4-4) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 0 | 61
B-C-0141 | B | ACC | Control | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 46
B-C-0142 | B | ACC | Control | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 46
B-C-0143 | B | ACC | Control | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 46
B-C-0144 | B | ACC | Control | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 46
B-C-0145 | B | ACC | Control | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 46
B-C-0146 | B | ACC | Control | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 46
B-C-0147 | B | ACC | Control | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 46
B-C-0148 | B | ACC | Control | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 46
B-C-0149 | B | ACC | Motor 1 of 6: control / local station |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-1: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 160 | 64
B-C-0150 | B | ACC | Motor 2 of 6: control / local station |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-1: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 160 | 64
B-C-0151 | B | ACC | Motor 3 of 6: control / local station |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-1: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 160 | 64
B-C-0152 | B | ACC | Motor 4 of 6: control / local station |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-1: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 160 | 64
B-C-0153 | B | ACC | Motor 5 of 6: control / local station |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-1: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 160 | 64
B-C-0154 | B | ACC | Motor 6 of 6: control / local station |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-1: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 160 | 64
B-C-0155 | B | ACC | Motor 1 of 6: control / local station |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-2: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 186 | 64
B-C-0156 | B | ACC | Motor 2 of 6: control / local station |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-2: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 186 | 64
B-C-0157 | B | ACC | Motor 3 of 6: control / local station |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-2: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 186 | 64
B-C-0158 | B | ACC | Motor 4 of 6: control / local station |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-2: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 186 | 64
B-C-0159 | B | ACC | Motor 5 of 6: control / local station |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-2: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 186 | 64
B-C-0160 | B | ACC | Motor 6 of 6: control / local station |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-2: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 186 | 64
B-C-0161 | B | ACC | Motor 1 of 6: control / local station |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-3: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 215 | 51
B-C-0162 | B | ACC | Motor 2 of 6: control / local station |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-3: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 215 | 51
B-C-0163 | B | ACC | Motor 3 of 6: control / local station |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-3: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 215 | 51
B-C-0164 | B | ACC | Motor 4 of 6: control / local station |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-3: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 215 | 51
B-C-0165 | B | ACC | Motor 5 of 6: control / local station |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-3: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 215 | 51
B-C-0166 | B | ACC | Motor 6 of 6: control / local station |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-3: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 215 | 51
B-C-0167 | B | ACC | Motor 1 of 6: control / local station |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-4: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 209 | 77
B-C-0168 | B | ACC | Motor 2 of 6: control / local station |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-4: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 209 | 77
B-C-0169 | B | ACC | Motor 3 of 6: control / local station |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-4: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 209 | 77
B-C-0170 | B | ACC | Motor 4 of 6: control / local station |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-4: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 209 | 77
B-C-0171 | B | ACC | Motor 5 of 6: control / local station |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-4: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 209 | 77
B-C-0172 | B | ACC | Motor 6 of 6: control / local station |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-4: 13.8/0.48 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 209 | 77
B-C-0173 | B | ACC | Motor 1 of 2: control / local station |  | R4 480 V switchgear + vacuum-pump MCC | VAC-A/B | VAC-A/B: ACC air-removal vacuum pumps | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 520 | 99
B-C-0174 | B | ACC | Motor 2 of 2: control / local station |  | R4 480 V switchgear + vacuum-pump MCC | VAC-A/B | VAC-A/B: ACC air-removal vacuum pumps | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 520 | 99
B-F-0001 | B | ACC | Plant network / DCS fibre | CR | Control / admin building (main control room) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Duct bank | 1408 | 57
B-FA-0001 | B | ACC | Fire alarm / F&G loop (to the local FACP / F&G node) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) |  | R4 480 V switchgear + vacuum-pump MCC | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 54
B-FA-0002 | B | ACC | Fire alarm / F&G loop (to the local FACP / F&G node) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 46
B-I-0001 | B | ACC | Analog instrument to JB JB-ACC-AI01: 20 x 1 pr (field cables) | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | JB-ACC-AI01 | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 250 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0002 | B | ACC | Home run JB-ACC-AI01 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-ACC-AI01 | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 44
B-I-0003 | B | ACC | Analog instrument to JB JB-ACC-AI02: 20 x 1 pr (field cables) | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | JB-ACC-AI02 | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 250 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0004 | B | ACC | Home run JB-ACC-AI02 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-ACC-AI02 | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 44
B-I-0005 | B | ACC | Analog instrument to JB JB-ACC-AI03: 20 x 1 pr (field cables) | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | JB-ACC-AI03 | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 250 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0006 | B | ACC | Home run JB-ACC-AI03 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-ACC-AI03 | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 44
B-I-0007 | B | ACC | Analog instrument to JB JB-ACC-AI04: 20 x 1 pr (field cables) | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | JB-ACC-AI04 | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 250 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0008 | B | ACC | Home run JB-ACC-AI04 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-ACC-AI04 | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 44
B-I-0009 | B | ACC | Analog instrument to JB JB-ACC-AI05: 20 x 1 pr (field cables) | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | JB-ACC-AI05 | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 250 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0010 | B | ACC | Home run JB-ACC-AI05 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-ACC-AI05 | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 44
B-I-0011 | B | ACC | Discrete device to JB JB-ACC-DI01: 20 x 1 pr (field cables) | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | JB-ACC-DI01 | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 250 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0012 | B | ACC | Home run JB-ACC-DI01 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-ACC-DI01 | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 44
B-I-0013 | B | ACC | Discrete device to JB JB-ACC-DI02: 20 x 1 pr (field cables) | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | JB-ACC-DI02 | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 250 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0014 | B | ACC | Home run JB-ACC-DI02 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-ACC-DI02 | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 44
B-I-0015 | B | ACC | Discrete device to JB JB-ACC-DI03: 20 x 1 pr (field cables) | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | JB-ACC-DI03 | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 250 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0016 | B | ACC | Home run JB-ACC-DI03 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-ACC-DI03 | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 44
B-I-0017 | B | ACC | Discrete device to JB JB-ACC-DI04: 20 x 1 pr (field cables) | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | JB-ACC-DI04 | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 250 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0018 | B | ACC | Home run JB-ACC-DI04 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-ACC-DI04 | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 44
B-I-0019 | B | ACC | Discrete device to JB JB-ACC-DI05: 20 x 1 pr (field cables) | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | JB-ACC-DI05 | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 250 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0020 | B | ACC | Home run JB-ACC-DI05 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-ACC-DI05 | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 44
B-I-0021 | B | ACC | Discrete device to JB JB-ACC-DI06: 20 x 1 pr (field cables) | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | JB-ACC-DI06 | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 250 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0022 | B | ACC | Home run JB-ACC-DI06 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-ACC-DI06 | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 44
B-I-0023 | B | ACC | Discrete device to JB JB-ACC-DI07: 20 x 1 pr (field cables) | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | JB-ACC-DI07 | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 250 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0024 | B | ACC | Home run JB-ACC-DI07 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-ACC-DI07 | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 44
B-I-0025 | B | ACC | Discrete device to JB JB-ACC-DI08: 20 x 1 pr (field cables) | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | JB-ACC-DI08 | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 250 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0026 | B | ACC | Home run JB-ACC-DI08 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-ACC-DI08 | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 44
B-I-0027 | B | ACC | Analog instrument to JB JB-AUXC-AI01: 12 x 1 pr (field cables) | AUXC | Aux dry coolers AUXC-F01..12 (closed cooling water) | JB-AUXC-AI01 | Aux dry coolers AUXC-F01..12 (closed cooling water) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 110 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0028 | B | ACC | Home run JB-AUXC-AI01 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-AUXC-AI01 | Aux dry coolers AUXC-F01..12 (closed cooling water) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 667 | 203
B-I-0029 | B | ACC | Discrete device to JB JB-AUXC-DI01: 20 x 1 pr (field cables) | AUXC | Aux dry coolers AUXC-F01..12 (closed cooling water) | JB-AUXC-DI01 | Aux dry coolers AUXC-F01..12 (closed cooling water) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 110 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0030 | B | ACC | Home run JB-AUXC-DI01 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-AUXC-DI01 | Aux dry coolers AUXC-F01..12 (closed cooling water) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 667 | 203
B-I-0031 | B | ACC | Discrete device to JB JB-AUXC-DI02: 4 x 1 pr (field cables) | AUXC | Aux dry coolers AUXC-F01..12 (closed cooling water) | JB-AUXC-DI02 | Aux dry coolers AUXC-F01..12 (closed cooling water) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 110 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0032 | B | ACC | Home run JB-AUXC-DI02 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-AUXC-DI02 | Aux dry coolers AUXC-F01..12 (closed cooling water) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 667 | 203
B-I-0033 | B | ACC | Analog instrument to JB JB-CCW-A/B-AI01: 10 x 1 pr (field cables) | CCW-A/B | CCW-A/B: closed cooling water pumps | JB-CCW-A/B-AI01 | CCW-A/B: closed cooling water pumps | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0034 | B | ACC | Home run JB-CCW-A/B-AI01 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-CCW-A/B-AI01 | CCW-A/B: closed cooling water pumps | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 676 | 167
B-I-0035 | B | ACC | Discrete device to JB JB-CCW-A/B-DI01: 10 x 1 pr (field cables) | CCW-A/B | CCW-A/B: closed cooling water pumps | JB-CCW-A/B-DI01 | CCW-A/B: closed cooling water pumps | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0036 | B | ACC | Home run JB-CCW-A/B-DI01 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-CCW-A/B-DI01 | CCW-A/B: closed cooling water pumps | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 676 | 167
B-I-0037 | B | ACC | Analog instrument to JB JB-CP-A/B/C-AI01: 15 x 1 pr (field cables) | CP-A/B/C | CP-A/B/C: condensate pumps (4.16 kV) | JB-CP-A/B/C-AI01 | CP-A/B/C: condensate pumps (4.16 kV) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 15 | 1 |  |  |  | Tray / conduit | 55 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0038 | B | ACC | Home run JB-CP-A/B/C-AI01 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-CP-A/B/C-AI01 | CP-A/B/C: condensate pumps (4.16 kV) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 532 | 135
B-I-0039 | B | ACC | Discrete device to JB JB-CP-A/B/C-DI01: 15 x 1 pr (field cables) | CP-A/B/C | CP-A/B/C: condensate pumps (4.16 kV) | JB-CP-A/B/C-DI01 | CP-A/B/C: condensate pumps (4.16 kV) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 15 | 1 |  |  |  | Tray / conduit | 55 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0040 | B | ACC | Home run JB-CP-A/B/C-DI01 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-CP-A/B/C-DI01 | CP-A/B/C: condensate pumps (4.16 kV) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 532 | 135
B-I-0041 | B | ACC | RTD to JB JB-CP-A/B/C-RTD01: 10 x 1 tri (field cables) | CP-A/B/C | CP-A/B/C: condensate pumps (4.16 kV) | JB-CP-A/B/C-RTD01 | CP-A/B/C: condensate pumps (4.16 kV) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 55 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0042 | B | ACC | Home run JB-CP-A/B/C-RTD01 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-CP-A/B/C-RTD01 | CP-A/B/C: condensate pumps (4.16 kV) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Tray | 532 | 135
B-I-0043 | B | ACC | RTD to JB JB-CP-A/B/C-RTD02: 8 x 1 tri (field cables) | CP-A/B/C | CP-A/B/C: condensate pumps (4.16 kV) | JB-CP-A/B/C-RTD02 | CP-A/B/C: condensate pumps (4.16 kV) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 8 | 1 |  |  |  | Tray / conduit | 55 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0044 | B | ACC | Home run JB-CP-A/B/C-RTD02 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-CP-A/B/C-RTD02 | CP-A/B/C: condensate pumps (4.16 kV) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Tray | 532 | 135
B-I-0045 | B | ACC | Analog instrument to JB JB-Condensate storage-AI01: 4 x 1 pr (field cables) |  | Condensate storage tank | JB-Condensate storage-AI01 | Condensate storage tank | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 66 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0046 | B | ACC | Home run JB-Condensate storage-AI01 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-Condensate storage-AI01 | Condensate storage tank | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 410 | 105
B-I-0047 | B | ACC | Discrete device to JB JB-Condensate storage-DI01: 4 x 1 pr (field cables) |  | Condensate storage tank | JB-Condensate storage-DI01 | Condensate storage tank | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 66 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0048 | B | ACC | Home run JB-Condensate storage-DI01 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-Condensate storage-DI01 | Condensate storage tank | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 410 | 105
B-I-0049 | B | ACC | Instrumentation | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | VFD-L1 | R4 VFD lineup 1 (23 drives, fed from T-R4-1) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 18 | 81
B-I-0050 | B | ACC | Instrumentation | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | VFD-L2 | R4 VFD lineup 2 (23 drives, fed from T-R4-2) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 91
B-I-0051 | B | ACC | Instrumentation | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | VFD-L3 | R4 VFD lineup 3 (23 drives, fed from T-R4-3) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 73
B-I-0052 | B | ACC | Instrumentation | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | VFD-L4 | R4 VFD lineup 4 (23 drives, fed from T-R4-4) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 61
B-I-0053 | B | ACC | Analog instrument to JB JB-T-R4-1: 13.8/0.48 -AI01: 8 x 1 pr (field cables) |  | T-R4-1: 13.8/0.48 kV | JB-T-R4-1: 13.8/0.48 -AI01 | T-R4-1: 13.8/0.48 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 42 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0054 | B | ACC | Home run JB-T-R4-1: 13.8/0.48 -AI01 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-T-R4-1: 13.8/0.48 -AI01 | T-R4-1: 13.8/0.48 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 159 | 56
B-I-0055 | B | ACC | Discrete device to JB JB-T-R4-1: 13.8/0.48 -DI01: 16 x 1 pr (field cables) |  | T-R4-1: 13.8/0.48 kV | JB-T-R4-1: 13.8/0.48 -DI01 | T-R4-1: 13.8/0.48 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 42 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0056 | B | ACC | Home run JB-T-R4-1: 13.8/0.48 -DI01 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-T-R4-1: 13.8/0.48 -DI01 | T-R4-1: 13.8/0.48 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 159 | 56
B-I-0057 | B | ACC | Analog instrument to JB JB-T-R4-2: 13.8/0.48 -AI01: 8 x 1 pr (field cables) |  | T-R4-2: 13.8/0.48 kV | JB-T-R4-2: 13.8/0.48 -AI01 | T-R4-2: 13.8/0.48 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 42 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0058 | B | ACC | Home run JB-T-R4-2: 13.8/0.48 -AI01 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-T-R4-2: 13.8/0.48 -AI01 | T-R4-2: 13.8/0.48 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 185 | 56
B-I-0059 | B | ACC | Discrete device to JB JB-T-R4-2: 13.8/0.48 -DI01: 16 x 1 pr (field cables) |  | T-R4-2: 13.8/0.48 kV | JB-T-R4-2: 13.8/0.48 -DI01 | T-R4-2: 13.8/0.48 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 42 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0060 | B | ACC | Home run JB-T-R4-2: 13.8/0.48 -DI01 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-T-R4-2: 13.8/0.48 -DI01 | T-R4-2: 13.8/0.48 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 185 | 56
B-I-0061 | B | ACC | Analog instrument to JB JB-T-R4-3: 13.8/0.48 -AI01: 8 x 1 pr (field cables) |  | T-R4-3: 13.8/0.48 kV | JB-T-R4-3: 13.8/0.48 -AI01 | T-R4-3: 13.8/0.48 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 42 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0062 | B | ACC | Home run JB-T-R4-3: 13.8/0.48 -AI01 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-T-R4-3: 13.8/0.48 -AI01 | T-R4-3: 13.8/0.48 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 214 | 43
B-I-0063 | B | ACC | Discrete device to JB JB-T-R4-3: 13.8/0.48 -DI01: 16 x 1 pr (field cables) |  | T-R4-3: 13.8/0.48 kV | JB-T-R4-3: 13.8/0.48 -DI01 | T-R4-3: 13.8/0.48 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 42 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0064 | B | ACC | Home run JB-T-R4-3: 13.8/0.48 -DI01 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-T-R4-3: 13.8/0.48 -DI01 | T-R4-3: 13.8/0.48 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 214 | 43
B-I-0065 | B | ACC | Analog instrument to JB JB-T-R4-4: 13.8/0.48 -AI01: 8 x 1 pr (field cables) |  | T-R4-4: 13.8/0.48 kV | JB-T-R4-4: 13.8/0.48 -AI01 | T-R4-4: 13.8/0.48 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 42 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0066 | B | ACC | Home run JB-T-R4-4: 13.8/0.48 -AI01 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-T-R4-4: 13.8/0.48 -AI01 | T-R4-4: 13.8/0.48 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 208 | 69
B-I-0067 | B | ACC | Discrete device to JB JB-T-R4-4: 13.8/0.48 -DI01: 16 x 1 pr (field cables) |  | T-R4-4: 13.8/0.48 kV | JB-T-R4-4: 13.8/0.48 -DI01 | T-R4-4: 13.8/0.48 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 42 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0068 | B | ACC | Home run JB-T-R4-4: 13.8/0.48 -DI01 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-T-R4-4: 13.8/0.48 -DI01 | T-R4-4: 13.8/0.48 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 208 | 69
B-I-0069 | B | ACC | Analog instrument to JB JB-VAC-A/B-AI01: 10 x 1 pr (field cables) | VAC-A/B | VAC-A/B: ACC air-removal vacuum pumps | JB-VAC-A/B-AI01 | VAC-A/B: ACC air-removal vacuum pumps | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0070 | B | ACC | Home run JB-VAC-A/B-AI01 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-VAC-A/B-AI01 | VAC-A/B: ACC air-removal vacuum pumps | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 532 | 91
B-I-0071 | B | ACC | Discrete device to JB JB-VAC-A/B-DI01: 10 x 1 pr (field cables) | VAC-A/B | VAC-A/B: ACC air-removal vacuum pumps | JB-VAC-A/B-DI01 | VAC-A/B: ACC air-removal vacuum pumps | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
B-I-0072 | B | ACC | Home run JB-VAC-A/B-DI01 to the control / marshalling room | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | JB-VAC-A/B-DI01 | VAC-A/B: ACC air-removal vacuum pumps | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 532 | 91
B-P-0001 | B | ACC | ACC fan F01 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F01 | ACC fan motor F01 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 389 | 44 |  |  |  |  | VD 1.3 %
B-P-0002 | B | ACC | ACC fan F02 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F02 | ACC fan motor F02 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 357 | 44 |  |  |  |  | VD 1.2 %
B-P-0003 | B | ACC | ACC fan F03 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F03 | ACC fan motor F03 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 325 | 44 |  |  |  |  | VD 1.1 %
B-P-0004 | B | ACC | ACC fan F04 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F04 | ACC fan motor F04 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 293 | 44 |  |  |  |  | VD 1.0 %
B-P-0005 | B | ACC | ACC fan F05 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F05 | ACC fan motor F05 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 261 | 44 |  |  |  |  | VD 0.9 %
B-P-0006 | B | ACC | ACC fan F06 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F06 | ACC fan motor F06 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 261 | 44 |  |  |  |  | VD 0.9 %
B-P-0007 | B | ACC | ACC fan F07 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F07 | ACC fan motor F07 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 293 | 44 |  |  |  |  | VD 1.0 %
B-P-0008 | B | ACC | ACC fan F08 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F08 | ACC fan motor F08 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 325 | 44 |  |  |  |  | VD 1.1 %
B-P-0009 | B | ACC | ACC fan F09 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F09 | ACC fan motor F09 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 357 | 44 |  |  |  |  | VD 1.2 %
B-P-0010 | B | ACC | ACC fan F10 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F10 | ACC fan motor F10 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 389 | 44 |  |  |  |  | VD 1.3 %
B-P-0011 | B | ACC | ACC fan F11 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F11 | ACC fan motor F11 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 339 | 44 |  |  |  |  | VD 1.2 %
B-P-0012 | B | ACC | ACC fan F12 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F12 | ACC fan motor F12 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 307 | 44 |  |  |  |  | VD 1.1 %
B-P-0013 | B | ACC | ACC fan F13 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F13 | ACC fan motor F13 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 275 | 44 |  |  |  |  | VD 1.0 %
B-P-0014 | B | ACC | ACC fan F14 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F14 | ACC fan motor F14 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 243 | 44 |  |  |  |  | VD 0.9 %
B-P-0015 | B | ACC | ACC fan F15 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F15 | ACC fan motor F15 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 211 | 44 |  |  |  |  | VD 0.8 %
B-P-0016 | B | ACC | ACC fan F16 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F16 | ACC fan motor F16 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 211 | 44 |  |  |  |  | VD 0.8 %
B-P-0017 | B | ACC | ACC fan F17 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F17 | ACC fan motor F17 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 243 | 44 |  |  |  |  | VD 0.9 %
B-P-0018 | B | ACC | ACC fan F18 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F18 | ACC fan motor F18 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 275 | 44 |  |  |  |  | VD 1.0 %
B-P-0019 | B | ACC | ACC fan F19 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F19 | ACC fan motor F19 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 307 | 44 |  |  |  |  | VD 1.1 %
B-P-0020 | B | ACC | ACC fan F20 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F20 | ACC fan motor F20 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 339 | 44 |  |  |  |  | VD 1.2 %
B-P-0021 | B | ACC | ACC fan F21 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F21 | ACC fan motor F21 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 289 | 44 |  |  |  |  | VD 1.0 %
B-P-0022 | B | ACC | ACC fan F22 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F22 | ACC fan motor F22 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 257 | 44 |  |  |  |  | VD 0.9 %
B-P-0023 | B | ACC | ACC fan F23 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F23 | ACC fan motor F23 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 225 | 44 |  |  |  |  | VD 0.8 %
B-P-0024 | B | ACC | ACC fan F24 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F24 | ACC fan motor F24 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 193 | 44 |  |  |  |  | VD 0.7 %
B-P-0025 | B | ACC | ACC fan F25 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F25 | ACC fan motor F25 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 161 | 44 |  |  |  |  | VD 0.6 %
B-P-0026 | B | ACC | ACC fan F26 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F26 | ACC fan motor F26 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 161 | 44 |  |  |  |  | VD 0.6 %
B-P-0027 | B | ACC | ACC fan F27 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F27 | ACC fan motor F27 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 193 | 44 |  |  |  |  | VD 0.7 %
B-P-0028 | B | ACC | ACC fan F28 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F28 | ACC fan motor F28 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 225 | 44 |  |  |  |  | VD 0.8 %
B-P-0029 | B | ACC | ACC fan F29 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F29 | ACC fan motor F29 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 257 | 44 |  |  |  |  | VD 0.9 %
B-P-0030 | B | ACC | ACC fan F30 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F30 | ACC fan motor F30 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 289 | 44 |  |  |  |  | VD 1.0 %
B-P-0031 | B | ACC | ACC fan F31 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F31 | ACC fan motor F31 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 239 | 44 |  |  |  |  | VD 0.9 %
B-P-0032 | B | ACC | ACC fan F32 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F32 | ACC fan motor F32 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 207 | 44 |  |  |  |  | VD 0.8 %
B-P-0033 | B | ACC | ACC fan F33 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F33 | ACC fan motor F33 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 175 | 44 |  |  |  |  | VD 0.7 %
B-P-0034 | B | ACC | ACC fan F34 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F34 | ACC fan motor F34 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 143 | 44 |  |  |  |  | VD 0.6 %
B-P-0035 | B | ACC | ACC fan F35 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F35 | ACC fan motor F35 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 111 | 44 |  |  |  |  | VD 0.5 %
B-P-0036 | B | ACC | ACC fan F36 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F36 | ACC fan motor F36 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 111 | 44 |  |  |  |  | VD 0.5 %
B-P-0037 | B | ACC | ACC fan F37 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F37 | ACC fan motor F37 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 143 | 44 |  |  |  |  | VD 0.6 %
B-P-0038 | B | ACC | ACC fan F38 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F38 | ACC fan motor F38 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 175 | 44 |  |  |  |  | VD 0.7 %
B-P-0039 | B | ACC | ACC fan F39 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F39 | ACC fan motor F39 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 207 | 44 |  |  |  |  | VD 0.8 %
B-P-0040 | B | ACC | ACC fan F40 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F40 | ACC fan motor F40 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 239 | 44 |  |  |  |  | VD 0.9 %
B-P-0041 | B | ACC | ACC fan F41 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F41 | ACC fan motor F41 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 239 | 44 |  |  |  |  | VD 0.9 %
B-P-0042 | B | ACC | ACC fan F42 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F42 | ACC fan motor F42 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 207 | 44 |  |  |  |  | VD 0.8 %
B-P-0043 | B | ACC | ACC fan F43 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F43 | ACC fan motor F43 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 175 | 44 |  |  |  |  | VD 0.7 %
B-P-0044 | B | ACC | ACC fan F44 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F44 | ACC fan motor F44 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 143 | 44 |  |  |  |  | VD 0.6 %
B-P-0045 | B | ACC | ACC fan F45 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F45 | ACC fan motor F45 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 111 | 44 |  |  |  |  | VD 0.5 %
B-P-0046 | B | ACC | ACC fan F46 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F46 | ACC fan motor F46 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 111 | 44 |  |  |  |  | VD 0.5 %
B-P-0047 | B | ACC | ACC fan F47 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F47 | ACC fan motor F47 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 143 | 44 |  |  |  |  | VD 0.6 %
B-P-0048 | B | ACC | ACC fan F48 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F48 | ACC fan motor F48 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 175 | 44 |  |  |  |  | VD 0.7 %
B-P-0049 | B | ACC | ACC fan F49 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F49 | ACC fan motor F49 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 207 | 44 |  |  |  |  | VD 0.8 %
B-P-0050 | B | ACC | ACC fan F50 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F50 | ACC fan motor F50 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 239 | 44 |  |  |  |  | VD 0.9 %
B-P-0051 | B | ACC | ACC fan F51 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F51 | ACC fan motor F51 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 289 | 44 |  |  |  |  | VD 1.0 %
B-P-0052 | B | ACC | ACC fan F52 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F52 | ACC fan motor F52 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 257 | 44 |  |  |  |  | VD 0.9 %
B-P-0053 | B | ACC | ACC fan F53 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F53 | ACC fan motor F53 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 225 | 44 |  |  |  |  | VD 0.8 %
B-P-0054 | B | ACC | ACC fan F54 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F54 | ACC fan motor F54 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 193 | 44 |  |  |  |  | VD 0.7 %
B-P-0055 | B | ACC | ACC fan F55 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F55 | ACC fan motor F55 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 161 | 44 |  |  |  |  | VD 0.6 %
B-P-0056 | B | ACC | ACC fan F56 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F56 | ACC fan motor F56 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 161 | 44 |  |  |  |  | VD 0.6 %
B-P-0057 | B | ACC | ACC fan F57 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F57 | ACC fan motor F57 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 193 | 44 |  |  |  |  | VD 0.7 %
B-P-0058 | B | ACC | ACC fan F58 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F58 | ACC fan motor F58 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 225 | 44 |  |  |  |  | VD 0.8 %
B-P-0059 | B | ACC | ACC fan F59 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F59 | ACC fan motor F59 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 257 | 44 |  |  |  |  | VD 0.9 %
B-P-0060 | B | ACC | ACC fan F60 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F60 | ACC fan motor F60 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 289 | 44 |  |  |  |  | VD 1.0 %
B-P-0061 | B | ACC | ACC fan F61 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F61 | ACC fan motor F61 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 339 | 44 |  |  |  |  | VD 1.2 %
B-P-0062 | B | ACC | ACC fan F62 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F62 | ACC fan motor F62 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 307 | 44 |  |  |  |  | VD 1.1 %
B-P-0063 | B | ACC | ACC fan F63 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F63 | ACC fan motor F63 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 275 | 44 |  |  |  |  | VD 1.0 %
B-P-0064 | B | ACC | ACC fan F64 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F64 | ACC fan motor F64 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 243 | 44 |  |  |  |  | VD 0.9 %
B-P-0065 | B | ACC | ACC fan F65 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F65 | ACC fan motor F65 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 211 | 44 |  |  |  |  | VD 0.8 %
B-P-0066 | B | ACC | ACC fan F66 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F66 | ACC fan motor F66 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 211 | 44 |  |  |  |  | VD 0.8 %
B-P-0067 | B | ACC | ACC fan F67 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F67 | ACC fan motor F67 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 243 | 44 |  |  |  |  | VD 0.9 %
B-P-0068 | B | ACC | ACC fan F68 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F68 | ACC fan motor F68 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 275 | 44 |  |  |  |  | VD 1.0 %
B-P-0069 | B | ACC | ACC fan F69 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F69 | ACC fan motor F69 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 307 | 44 |  |  |  |  | VD 1.1 %
B-P-0070 | B | ACC | ACC fan F70 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F70 | ACC fan motor F70 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 339 | 44 |  |  |  |  | VD 1.2 %
B-P-0071 | B | ACC | ACC fan F71 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F71 | ACC fan motor F71 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 389 | 44 |  |  |  |  | VD 1.3 %
B-P-0072 | B | ACC | ACC fan F72 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F72 | ACC fan motor F72 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 357 | 44 |  |  |  |  | VD 1.2 %
B-P-0073 | B | ACC | ACC fan F73 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F73 | ACC fan motor F73 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 325 | 44 |  |  |  |  | VD 1.1 %
B-P-0074 | B | ACC | ACC fan F74 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F74 | ACC fan motor F74 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 293 | 44 |  |  |  |  | VD 1.0 %
B-P-0075 | B | ACC | ACC fan F75 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F75 | ACC fan motor F75 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 261 | 44 |  |  |  |  | VD 0.9 %
B-P-0076 | B | ACC | ACC fan F76 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F76 | ACC fan motor F76 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 261 | 44 |  |  |  |  | VD 0.9 %
B-P-0077 | B | ACC | ACC fan F77 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F77 | ACC fan motor F77 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 293 | 44 |  |  |  |  | VD 1.0 %
B-P-0078 | B | ACC | ACC fan F78 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F78 | ACC fan motor F78 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 325 | 44 |  |  |  |  | VD 1.1 %
B-P-0079 | B | ACC | ACC fan F79 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F79 | ACC fan motor F79 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 357 | 44 |  |  |  |  | VD 1.2 %
B-P-0080 | B | ACC | ACC fan F80 motor (VFD output) | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | ACC-F80 | ACC fan motor F80 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦350 | 3/C+3G | 350 kcmil | 1 | 1 | 480 | 150 | 212 | Tray | 389 | 44 |  |  |  |  | VD 1.3 %
B-P-0081 | B | ACC | MOV 1: power |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 52 |  |  |  |  | VD 0.1 %
B-P-0082 | B | ACC | MOV 2: power |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 52 |  |  |  |  | VD 0.1 %
B-P-0083 | B | ACC | MOV 3: power |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 52 |  |  |  |  | VD 0.1 %
B-P-0084 | B | ACC | MOV 4: power |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 52 |  |  |  |  | VD 0.1 %
B-P-0085 | B | ACC | MOV 5: power |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 52 |  |  |  |  | VD 0.1 %
B-P-0086 | B | ACC | MOV 6: power |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 52 |  |  |  |  | VD 0.1 %
B-P-0087 | B | ACC | MOV 7: power |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 52 |  |  |  |  | VD 0.1 %
B-P-0088 | B | ACC | MOV 8: power |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 52 |  |  |  |  | VD 0.1 %
B-P-0089 | B | ACC | MOV 9: power |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 52 |  |  |  |  | VD 0.1 %
B-P-0090 | B | ACC | MOV 10: power |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 52 |  |  |  |  | VD 0.1 %
B-P-0091 | B | ACC | MOV 11: power |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 52 |  |  |  |  | VD 0.1 %
B-P-0092 | B | ACC | MOV 12: power |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 52 |  |  |  |  | VD 0.1 %
B-P-0093 | B | ACC | MOV 13: power |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 52 |  |  |  |  | VD 0.1 %
B-P-0094 | B | ACC | MOV 14: power |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 52 |  |  |  |  | VD 0.1 %
B-P-0095 | B | ACC | MOV 15: power |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 52 |  |  |  |  | VD 0.1 %
B-P-0096 | B | ACC | MOV 16: power |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 52 |  |  |  |  | VD 0.1 %
B-P-0097 | B | ACC | MOV 17: power |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 52 |  |  |  |  | VD 0.1 %
B-P-0098 | B | ACC | MOV 18: power |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 52 |  |  |  |  | VD 0.1 %
B-P-0099 | B | ACC | MOV 19: power |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 52 |  |  |  |  | VD 0.1 %
B-P-0100 | B | ACC | MOV 20: power |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 52 |  |  |  |  | VD 0.1 %
B-P-0101 | B | ACC | MOV 21: power |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 52 |  |  |  |  | VD 0.1 %
B-P-0102 | B | ACC | MOV 22: power |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 52 |  |  |  |  | VD 0.1 %
B-P-0103 | B | ACC | MOV 23: power |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 52 |  |  |  |  | VD 0.1 %
B-P-0104 | B | ACC | MOV 24: power |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 52 |  |  |  |  | VD 0.1 %
B-P-0105 | B | ACC | MOV 25: power |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 52 |  |  |  |  | VD 0.1 %
B-P-0106 | B | ACC | MOV 26: power |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 52 |  |  |  |  | VD 0.1 %
B-P-0107 | B | ACC | MOV 27: power |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 52 |  |  |  |  | VD 0.1 %
B-P-0108 | B | ACC | MOV 28: power |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 52 |  |  |  |  | VD 0.1 %
B-P-0109 | B | ACC | MOV 29: power |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 52 |  |  |  |  | VD 0.1 %
B-P-0110 | B | ACC | MOV 30: power |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 0 | 52 |  |  |  |  | VD 0.1 %
B-P-0111 | B | ACC | Area / platform lighting circuit 1 (12 fixtures) |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 300 | 52 |  |  |  |  | fixture-to-fixture run included
B-P-0112 | B | ACC | Area / platform lighting circuit 2 (12 fixtures) |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 300 | 52 |  |  |  |  | fixture-to-fixture run included
B-P-0113 | B | ACC | Area / platform lighting circuit 3 (12 fixtures) |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 300 | 52 |  |  |  |  | fixture-to-fixture run included
B-P-0114 | B | ACC | Area / platform lighting circuit 4 (12 fixtures) |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 300 | 52 |  |  |  |  | fixture-to-fixture run included
B-P-0115 | B | ACC | Area / platform lighting circuit 5 (12 fixtures) |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 300 | 52 |  |  |  |  | fixture-to-fixture run included
B-P-0116 | B | ACC | Area / platform lighting circuit 6 (12 fixtures) |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 300 | 52 |  |  |  |  | fixture-to-fixture run included
B-P-0117 | B | ACC | Area / platform lighting circuit 7 (8 fixtures) |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 300 | 52 |  |  |  |  | fixture-to-fixture run included
B-P-0118 | B | ACC | 480 V welding receptacle 1 |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 0 | 52 |  |  |  |  | VD 0.3 %
B-P-0119 | B | ACC | 480 V welding receptacle 2 |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 0 | 52 |  |  |  |  | VD 0.3 %
B-P-0120 | B | ACC | 480 V welding receptacle 3 |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 0 | 52 |  |  |  |  | VD 0.3 %
B-P-0121 | B | ACC | 480 V welding receptacle 4 |  | R4 480 V switchgear + vacuum-pump MCC | ACC | Air-cooled condenser, 80 cells (steam-cycle heat rejection) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 0 | 52 |  |  |  |  | VD 0.3 %
B-P-0122 | B | ACC | Motor 1 of 12, 22 kW (VFD output) |  | R4 480 V switchgear + vacuum-pump MCC | AUXC | Aux dry coolers AUXC-F01..12 (closed cooling water) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦2 | 3/C+3G | 2 | 1 | 1 | 480 | 22 | 31 | Tray | 765 | 211 |  |  |  |  | VD 2.3 %
B-P-0123 | B | ACC | Motor 2 of 12, 22 kW (VFD output) |  | R4 480 V switchgear + vacuum-pump MCC | AUXC | Aux dry coolers AUXC-F01..12 (closed cooling water) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦2 | 3/C+3G | 2 | 1 | 1 | 480 | 22 | 31 | Tray | 765 | 211 |  |  |  |  | VD 2.3 %
B-P-0124 | B | ACC | Motor 3 of 12, 22 kW (VFD output) |  | R4 480 V switchgear + vacuum-pump MCC | AUXC | Aux dry coolers AUXC-F01..12 (closed cooling water) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦2 | 3/C+3G | 2 | 1 | 1 | 480 | 22 | 31 | Tray | 765 | 211 |  |  |  |  | VD 2.3 %
B-P-0125 | B | ACC | Motor 4 of 12, 22 kW (VFD output) |  | R4 480 V switchgear + vacuum-pump MCC | AUXC | Aux dry coolers AUXC-F01..12 (closed cooling water) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦2 | 3/C+3G | 2 | 1 | 1 | 480 | 22 | 31 | Tray | 765 | 211 |  |  |  |  | VD 2.3 %
B-P-0126 | B | ACC | Motor 5 of 12, 22 kW (VFD output) |  | R4 480 V switchgear + vacuum-pump MCC | AUXC | Aux dry coolers AUXC-F01..12 (closed cooling water) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦2 | 3/C+3G | 2 | 1 | 1 | 480 | 22 | 31 | Tray | 765 | 211 |  |  |  |  | VD 2.3 %
B-P-0127 | B | ACC | Motor 6 of 12, 22 kW (VFD output) |  | R4 480 V switchgear + vacuum-pump MCC | AUXC | Aux dry coolers AUXC-F01..12 (closed cooling water) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦2 | 3/C+3G | 2 | 1 | 1 | 480 | 22 | 31 | Tray | 765 | 211 |  |  |  |  | VD 2.3 %
B-P-0128 | B | ACC | Motor 7 of 12, 22 kW (VFD output) |  | R4 480 V switchgear + vacuum-pump MCC | AUXC | Aux dry coolers AUXC-F01..12 (closed cooling water) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦2 | 3/C+3G | 2 | 1 | 1 | 480 | 22 | 31 | Tray | 765 | 211 |  |  |  |  | VD 2.3 %
B-P-0129 | B | ACC | Motor 8 of 12, 22 kW (VFD output) |  | R4 480 V switchgear + vacuum-pump MCC | AUXC | Aux dry coolers AUXC-F01..12 (closed cooling water) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦2 | 3/C+3G | 2 | 1 | 1 | 480 | 22 | 31 | Tray | 765 | 211 |  |  |  |  | VD 2.3 %
B-P-0130 | B | ACC | Motor 9 of 12, 22 kW (VFD output) |  | R4 480 V switchgear + vacuum-pump MCC | AUXC | Aux dry coolers AUXC-F01..12 (closed cooling water) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦2 | 3/C+3G | 2 | 1 | 1 | 480 | 22 | 31 | Tray | 765 | 211 |  |  |  |  | VD 2.3 %
B-P-0131 | B | ACC | Motor 10 of 12, 22 kW (VFD output) |  | R4 480 V switchgear + vacuum-pump MCC | AUXC | Aux dry coolers AUXC-F01..12 (closed cooling water) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦2 | 3/C+3G | 2 | 1 | 1 | 480 | 22 | 31 | Tray | 765 | 211 |  |  |  |  | VD 2.3 %
B-P-0132 | B | ACC | Motor 11 of 12, 22 kW (VFD output) |  | R4 480 V switchgear + vacuum-pump MCC | AUXC | Aux dry coolers AUXC-F01..12 (closed cooling water) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦2 | 3/C+3G | 2 | 1 | 1 | 480 | 22 | 31 | Tray | 765 | 211 |  |  |  |  | VD 2.3 %
B-P-0133 | B | ACC | Motor 12 of 12, 22 kW (VFD output) |  | R4 480 V switchgear + vacuum-pump MCC | AUXC | Aux dry coolers AUXC-F01..12 (closed cooling water) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦2 | 3/C+3G | 2 | 1 | 1 | 480 | 22 | 31 | Tray | 765 | 211 |  |  |  |  | VD 2.3 %
B-P-0134 | B | ACC | Motor 1 of 2, 150 kW |  | R4 480 V switchgear + vacuum-pump MCC | CCW-A/B | CCW-A/B: closed cooling water pumps | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 150 | 212.3 | Tray | 664 | 175 |  |  |  |  | VD 2.6 %
B-P-0135 | B | ACC | Motor 2 of 2, 150 kW |  | R4 480 V switchgear + vacuum-pump MCC | CCW-A/B | CCW-A/B: closed cooling water pumps | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 150 | 212.3 | Tray | 664 | 175 |  |  |  |  | VD 2.6 %
B-P-0136 | B | ACC | LV power feeder |  | R4 480 V switchgear + vacuum-pump MCC |  | Condensate storage tank | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 10 | 14.2 | Tray | 398 | 113 |  |  |  |  | VD 2.2 %
B-P-0137 | B | ACC | LV panel / distribution feeder |  | R4 480 V switchgear + vacuum-pump MCC | R4 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2/0 | 3/C+G | 2/0 | 1 | 1 | 480 | 86 | 121.7 | Tray | 0 | 54 |  |  |  |  | VD 0.3 %
B-P-0138 | B | ACC | Motor 1 of 6, 2 kW |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-1: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 160 | 64 |  |  |  |  | VD 0.3 %
B-P-0139 | B | ACC | Motor 2 of 6, 2 kW |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-1: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 160 | 64 |  |  |  |  | VD 0.3 %
B-P-0140 | B | ACC | Motor 3 of 6, 2 kW |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-1: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 160 | 64 |  |  |  |  | VD 0.3 %
B-P-0141 | B | ACC | Motor 4 of 6, 2 kW |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-1: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 160 | 64 |  |  |  |  | VD 0.3 %
B-P-0142 | B | ACC | Motor 5 of 6, 2 kW |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-1: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 160 | 64 |  |  |  |  | VD 0.3 %
B-P-0143 | B | ACC | Motor 6 of 6, 2 kW |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-1: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 160 | 64 |  |  |  |  | VD 0.3 %
B-P-0144 | B | ACC | Motor 1 of 6, 2 kW |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-2: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 186 | 64 |  |  |  |  | VD 0.3 %
B-P-0145 | B | ACC | Motor 2 of 6, 2 kW |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-2: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 186 | 64 |  |  |  |  | VD 0.3 %
B-P-0146 | B | ACC | Motor 3 of 6, 2 kW |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-2: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 186 | 64 |  |  |  |  | VD 0.3 %
B-P-0147 | B | ACC | Motor 4 of 6, 2 kW |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-2: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 186 | 64 |  |  |  |  | VD 0.3 %
B-P-0148 | B | ACC | Motor 5 of 6, 2 kW |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-2: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 186 | 64 |  |  |  |  | VD 0.3 %
B-P-0149 | B | ACC | Motor 6 of 6, 2 kW |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-2: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 186 | 64 |  |  |  |  | VD 0.3 %
B-P-0150 | B | ACC | Motor 1 of 6, 2 kW |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-3: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 215 | 51 |  |  |  |  | VD 0.4 %
B-P-0151 | B | ACC | Motor 2 of 6, 2 kW |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-3: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 215 | 51 |  |  |  |  | VD 0.4 %
B-P-0152 | B | ACC | Motor 3 of 6, 2 kW |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-3: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 215 | 51 |  |  |  |  | VD 0.4 %
B-P-0153 | B | ACC | Motor 4 of 6, 2 kW |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-3: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 215 | 51 |  |  |  |  | VD 0.4 %
B-P-0154 | B | ACC | Motor 5 of 6, 2 kW |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-3: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 215 | 51 |  |  |  |  | VD 0.4 %
B-P-0155 | B | ACC | Motor 6 of 6, 2 kW |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-3: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 215 | 51 |  |  |  |  | VD 0.4 %
B-P-0156 | B | ACC | Motor 1 of 6, 2 kW |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-4: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 209 | 77 |  |  |  |  | VD 0.4 %
B-P-0157 | B | ACC | Motor 2 of 6, 2 kW |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-4: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 209 | 77 |  |  |  |  | VD 0.4 %
B-P-0158 | B | ACC | Motor 3 of 6, 2 kW |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-4: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 209 | 77 |  |  |  |  | VD 0.4 %
B-P-0159 | B | ACC | Motor 4 of 6, 2 kW |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-4: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 209 | 77 |  |  |  |  | VD 0.4 %
B-P-0160 | B | ACC | Motor 5 of 6, 2 kW |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-4: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 209 | 77 |  |  |  |  | VD 0.4 %
B-P-0161 | B | ACC | Motor 6 of 6, 2 kW |  | R4 480 V switchgear + vacuum-pump MCC |  | T-R4-4: 13.8/0.48 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 209 | 77 |  |  |  |  | VD 0.4 %
B-P-0162 | B | ACC | Motor 1 of 2, 75 kW |  | R4 480 V switchgear + vacuum-pump MCC | VAC-A/B | VAC-A/B: ACC air-removal vacuum pumps | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2/0 | 3/C+G | 2/0 | 1 | 1 | 480 | 75 | 106.1 | Tray | 520 | 99 |  |  |  |  | VD 2.5 %
B-P-0163 | B | ACC | Motor 2 of 2, 75 kW |  | R4 480 V switchgear + vacuum-pump MCC | VAC-A/B | VAC-A/B: ACC air-removal vacuum pumps | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2/0 | 3/C+G | 2/0 | 1 | 1 | 480 | 75 | 106.1 | Tray | 520 | 99 |  |  |  |  | VD 2.5 %
B-MV-0001 | B | ACC | T-R4-1 ACC VFD transformer primary | SWGR-13.8-1 | R1 SWGR-13.8-1 (11 x 36 in cubicles, 15 kV metal-clad) |  | T-R4-1: 13.8/0.48 kV | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦2/0 | 1/C | 2/0 | 1 | 3 | 13800 | 3750 | 157 | Tray | 1173 | 147
B-MV-0002 | B | ACC | T-R4-2 ACC VFD transformer primary | SWGR-13.8-2 | R1 SWGR-13.8-2 (11 x 36 in cubicles, 15 kV metal-clad) |  | T-R4-2: 13.8/0.48 kV | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦2/0 | 1/C | 2/0 | 1 | 3 | 13800 | 3750 | 157 | Tray | 1228 | 163
B-MV-0003 | B | ACC | T-R4-3 ACC VFD transformer primary | SWGR-13.8-3 | R1 SWGR-13.8-3 (11 x 36 in cubicles, 15 kV metal-clad) |  | T-R4-3: 13.8/0.48 kV | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦2/0 | 1/C | 2/0 | 1 | 3 | 13800 | 3750 | 157 | Tray | 1310 | 128
B-MV-0004 | B | ACC | T-R4-4 ACC VFD transformer primary | SWGR-13.8-1 | R1 SWGR-13.8-1 (11 x 36 in cubicles, 15 kV metal-clad) |  | T-R4-4: 13.8/0.48 kV | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦2/0 | 1/C | 2/0 | 1 | 3 | 13800 | 3750 | 157 | Tray | 1222 | 160
B-MV-0005 | B | ACC | Condensate pump CP-A | SWGR-4.16-A | R1 SWGR-4.16-A (9 x 36 in cubicles, 5 kV metal-clad) | CP-A/B/C | CP-A/B/C: condensate pumps (4.16 kV) | MV 5 kV | MV-105 5 kV 3/C Cu, EPR 133%, tape shield, gnd, PVC jacket | MV5¦3/C¦1/0 | 3/C | 1/0 | 1 | 1 | 4160 | 900 | 139 | Tray | 1215 | 274
B-MV-0006 | B | ACC | Condensate pump CP-B | SWGR-4.16-B | R1 SWGR-4.16-B (5 kV metal-clad) | CP-A/B/C | CP-A/B/C: condensate pumps (4.16 kV) | MV 5 kV | MV-105 5 kV 3/C Cu, EPR 133%, tape shield, gnd, PVC jacket | MV5¦3/C¦1/0 | 3/C | 1/0 | 1 | 1 | 4160 | 900 | 139 | Tray | 855 | 155
B-MV-0007 | B | ACC | Condensate pump CP-C | SWGR-4.16-A | R1 SWGR-4.16-A (9 x 36 in cubicles, 5 kV metal-clad) | CP-A/B/C | CP-A/B/C: condensate pumps (4.16 kV) | MV 5 kV | MV-105 5 kV 3/C Cu, EPR 133%, tape shield, gnd, PVC jacket | MV5¦3/C¦1/0 | 3/C | 1/0 | 1 | 1 | 4160 | 900 | 139 | Tray | 1215 | 274
C-L-0001 | C | Grid interface | Lighting, receptacles and small power branch circuits (allowance) | RH | RH: switchyard relay / control house (52 x 70 ft) | RH | RH: switchyard relay / control house (52 x 70 ft) | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | THHN¦1/C¦12 | 1/C | 12 | 1 | 1 | 277 |  |  | Conduit | 5824 | 0 |  |  |  |  | allowance: 1.6 ft of conductor per ft2 of floor
C-C-0001 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D1-CB1 | D1 230 kV breaker 1 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 274 | 40
C-C-0002 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D1-CB1 | D1 230 kV breaker 1 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 274 | 40
C-C-0003 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D1-CB1 | D1 230 kV breaker 1 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 274 | 40
C-C-0004 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D1-CB1 | D1 230 kV breaker 1 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 274 | 40
C-C-0005 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D1-CB1 | D1 230 kV breaker 1 | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 274 | 40
C-C-0006 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D1-CB1 | D1 230 kV breaker 1 | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 274 | 40
C-C-0007 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D1-CB1 | D1 230 kV breaker 1 | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 274 | 40
C-C-0008 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D1-CB2 | D1 230 kV breaker 2 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 274 | 52
C-C-0009 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D1-CB2 | D1 230 kV breaker 2 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 274 | 52
C-C-0010 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D1-CB2 | D1 230 kV breaker 2 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 274 | 52
C-C-0011 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D1-CB2 | D1 230 kV breaker 2 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 274 | 52
C-C-0012 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D1-CB2 | D1 230 kV breaker 2 | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 274 | 52
C-C-0013 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D1-CB2 | D1 230 kV breaker 2 | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 274 | 52
C-C-0014 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D1-CB2 | D1 230 kV breaker 2 | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 274 | 52
C-C-0015 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D1-CB3 | D1 230 kV breaker 3 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 274 | 92
C-C-0016 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D1-CB3 | D1 230 kV breaker 3 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 274 | 92
C-C-0017 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D1-CB3 | D1 230 kV breaker 3 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 274 | 92
C-C-0018 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D1-CB3 | D1 230 kV breaker 3 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 274 | 92
C-C-0019 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D1-CB3 | D1 230 kV breaker 3 | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 274 | 92
C-C-0020 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D1-CB3 | D1 230 kV breaker 3 | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 274 | 92
C-C-0021 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D1-CB3 | D1 230 kV breaker 3 | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 274 | 92
C-C-0022 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D2-CB1 | D2 230 kV breaker 1 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 474 | 40
C-C-0023 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D2-CB1 | D2 230 kV breaker 1 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 474 | 40
C-C-0024 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D2-CB1 | D2 230 kV breaker 1 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 474 | 40
C-C-0025 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D2-CB1 | D2 230 kV breaker 1 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 474 | 40
C-C-0026 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D2-CB1 | D2 230 kV breaker 1 | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 474 | 40
C-C-0027 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D2-CB1 | D2 230 kV breaker 1 | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 474 | 40
C-C-0028 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D2-CB1 | D2 230 kV breaker 1 | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 474 | 40
C-C-0029 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D2-CB2 | D2 230 kV breaker 2 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 474 | 52
C-C-0030 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D2-CB2 | D2 230 kV breaker 2 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 474 | 52
C-C-0031 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D2-CB2 | D2 230 kV breaker 2 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 474 | 52
C-C-0032 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D2-CB2 | D2 230 kV breaker 2 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 474 | 52
C-C-0033 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D2-CB2 | D2 230 kV breaker 2 | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 474 | 52
C-C-0034 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D2-CB2 | D2 230 kV breaker 2 | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 474 | 52
C-C-0035 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D2-CB2 | D2 230 kV breaker 2 | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 474 | 52
C-C-0036 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D2-CB3 | D2 230 kV breaker 3 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 474 | 92
C-C-0037 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D2-CB3 | D2 230 kV breaker 3 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 474 | 92
C-C-0038 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D2-CB3 | D2 230 kV breaker 3 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 474 | 92
C-C-0039 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D2-CB3 | D2 230 kV breaker 3 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 474 | 92
C-C-0040 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D2-CB3 | D2 230 kV breaker 3 | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 474 | 92
C-C-0041 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D2-CB3 | D2 230 kV breaker 3 | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 474 | 92
C-C-0042 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D2-CB3 | D2 230 kV breaker 3 | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 474 | 92
C-C-0043 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D3-CB1 | D3 230 kV breaker 1 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 674 | 40
C-C-0044 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D3-CB1 | D3 230 kV breaker 1 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 674 | 40
C-C-0045 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D3-CB1 | D3 230 kV breaker 1 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 674 | 40
C-C-0046 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D3-CB1 | D3 230 kV breaker 1 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 674 | 40
C-C-0047 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D3-CB1 | D3 230 kV breaker 1 | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 674 | 40
C-C-0048 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D3-CB1 | D3 230 kV breaker 1 | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 674 | 40
C-C-0049 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D3-CB1 | D3 230 kV breaker 1 | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 674 | 40
C-C-0050 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D3-CB2 | D3 230 kV breaker 2 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 674 | 52
C-C-0051 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D3-CB2 | D3 230 kV breaker 2 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 674 | 52
C-C-0052 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D3-CB2 | D3 230 kV breaker 2 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 674 | 52
C-C-0053 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D3-CB2 | D3 230 kV breaker 2 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 674 | 52
C-C-0054 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D3-CB2 | D3 230 kV breaker 2 | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 674 | 52
C-C-0055 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D3-CB2 | D3 230 kV breaker 2 | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 674 | 52
C-C-0056 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D3-CB2 | D3 230 kV breaker 2 | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 674 | 52
C-C-0057 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D3-CB3 | D3 230 kV breaker 3 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 674 | 92
C-C-0058 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D3-CB3 | D3 230 kV breaker 3 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 674 | 92
C-C-0059 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D3-CB3 | D3 230 kV breaker 3 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 674 | 92
C-C-0060 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D3-CB3 | D3 230 kV breaker 3 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 674 | 92
C-C-0061 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D3-CB3 | D3 230 kV breaker 3 | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 674 | 92
C-C-0062 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D3-CB3 | D3 230 kV breaker 3 | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 674 | 92
C-C-0063 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D3-CB3 | D3 230 kV breaker 3 | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 674 | 92
C-C-0064 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D4-CB1 | D4 230 kV breaker 1 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1294 | 40
C-C-0065 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D4-CB1 | D4 230 kV breaker 1 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1294 | 40
C-C-0066 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D4-CB1 | D4 230 kV breaker 1 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1294 | 40
C-C-0067 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D4-CB1 | D4 230 kV breaker 1 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1294 | 40
C-C-0068 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D4-CB1 | D4 230 kV breaker 1 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 1294 | 40
C-C-0069 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D4-CB1 | D4 230 kV breaker 1 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 1294 | 40
C-C-0070 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D4-CB1 | D4 230 kV breaker 1 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 1294 | 40
C-C-0071 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D4-CB2 | D4 230 kV breaker 2 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1294 | 52
C-C-0072 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D4-CB2 | D4 230 kV breaker 2 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1294 | 52
C-C-0073 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D4-CB2 | D4 230 kV breaker 2 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1294 | 52
C-C-0074 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D4-CB2 | D4 230 kV breaker 2 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1294 | 52
C-C-0075 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D4-CB2 | D4 230 kV breaker 2 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 1294 | 52
C-C-0076 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D4-CB2 | D4 230 kV breaker 2 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 1294 | 52
C-C-0077 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D4-CB2 | D4 230 kV breaker 2 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 1294 | 52
C-C-0078 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D4-CB3 | D4 230 kV breaker 3 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1340 | 46
C-C-0079 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D4-CB3 | D4 230 kV breaker 3 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1340 | 46
C-C-0080 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D4-CB3 | D4 230 kV breaker 3 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1340 | 46
C-C-0081 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D4-CB3 | D4 230 kV breaker 3 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1340 | 46
C-C-0082 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D4-CB3 | D4 230 kV breaker 3 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 1340 | 46
C-C-0083 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D4-CB3 | D4 230 kV breaker 3 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 1340 | 46
C-C-0084 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D4-CB3 | D4 230 kV breaker 3 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 1340 | 46
C-C-0085 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D5-CB1 | D5 230 kV breaker 1 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1434 | 40
C-C-0086 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D5-CB1 | D5 230 kV breaker 1 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1434 | 40
C-C-0087 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D5-CB1 | D5 230 kV breaker 1 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1434 | 40
C-C-0088 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D5-CB1 | D5 230 kV breaker 1 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1434 | 40
C-C-0089 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D5-CB1 | D5 230 kV breaker 1 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 1434 | 40
C-C-0090 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D5-CB1 | D5 230 kV breaker 1 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 1434 | 40
C-C-0091 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D5-CB1 | D5 230 kV breaker 1 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 1434 | 40
C-C-0092 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D5-CB2 | D5 230 kV breaker 2 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1434 | 52
C-C-0093 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D5-CB2 | D5 230 kV breaker 2 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1434 | 52
C-C-0094 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D5-CB2 | D5 230 kV breaker 2 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1434 | 52
C-C-0095 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D5-CB2 | D5 230 kV breaker 2 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1434 | 52
C-C-0096 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D5-CB2 | D5 230 kV breaker 2 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 1434 | 52
C-C-0097 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D5-CB2 | D5 230 kV breaker 2 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 1434 | 52
C-C-0098 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D5-CB2 | D5 230 kV breaker 2 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 1434 | 52
C-C-0099 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D5-CB3 | D5 230 kV breaker 3 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1434 | 92
C-C-0100 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D5-CB3 | D5 230 kV breaker 3 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1434 | 92
C-C-0101 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D5-CB3 | D5 230 kV breaker 3 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1434 | 92
C-C-0102 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D5-CB3 | D5 230 kV breaker 3 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1434 | 92
C-C-0103 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D5-CB3 | D5 230 kV breaker 3 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 1434 | 92
C-C-0104 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D5-CB3 | D5 230 kV breaker 3 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 1434 | 92
C-C-0105 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D5-CB3 | D5 230 kV breaker 3 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 1434 | 92
C-C-0106 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D6-CB1 | D6 230 kV breaker 1 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1584 | 40
C-C-0107 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D6-CB1 | D6 230 kV breaker 1 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1584 | 40
C-C-0108 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D6-CB1 | D6 230 kV breaker 1 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1584 | 40
C-C-0109 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D6-CB1 | D6 230 kV breaker 1 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1584 | 40
C-C-0110 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D6-CB1 | D6 230 kV breaker 1 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 1584 | 40
C-C-0111 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D6-CB1 | D6 230 kV breaker 1 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 1584 | 40
C-C-0112 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D6-CB1 | D6 230 kV breaker 1 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 1584 | 40
C-C-0113 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D6-CB2 | D6 230 kV breaker 2 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1584 | 52
C-C-0114 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D6-CB2 | D6 230 kV breaker 2 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1584 | 52
C-C-0115 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D6-CB2 | D6 230 kV breaker 2 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1584 | 52
C-C-0116 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D6-CB2 | D6 230 kV breaker 2 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1584 | 52
C-C-0117 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D6-CB2 | D6 230 kV breaker 2 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 1584 | 52
C-C-0118 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D6-CB2 | D6 230 kV breaker 2 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 1584 | 52
C-C-0119 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D6-CB2 | D6 230 kV breaker 2 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 1584 | 52
C-C-0120 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D6-CB3 | D6 230 kV breaker 3 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1584 | 92
C-C-0121 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D6-CB3 | D6 230 kV breaker 3 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1584 | 92
C-C-0122 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D6-CB3 | D6 230 kV breaker 3 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1584 | 92
C-C-0123 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | D6-CB3 | D6 230 kV breaker 3 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Trench | 1584 | 92
C-C-0124 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D6-CB3 | D6 230 kV breaker 3 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 1584 | 92
C-C-0125 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D6-CB3 | D6 230 kV breaker 3 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 1584 | 92
C-C-0126 | C | Grid interface | CT / VT | RH | RH: switchyard relay / control house (52 x 70 ft) | D6-CB3 | D6 230 kV breaker 3 (build-out) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Trench | 1584 | 92
C-C-0127 | C | Grid interface | Control | RH | RH: switchyard relay / control house (52 x 70 ft) | RH | RH: switchyard relay / control house (52 x 70 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 30
C-F-0001 | C | Grid interface | Plant network / DCS fibre | CR | Control / admin building (main control room) | RH | RH: switchyard relay / control house (52 x 70 ft) | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Duct bank | 809 | 32
C-FA-0001 | C | Grid interface | Fire alarm / F&G loop (to the local FACP / F&G node) | RH | RH: switchyard relay / control house (52 x 70 ft) | RH | RH: switchyard relay / control house (52 x 70 ft) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 30
C-G-0001 | C | Grid interface | Equipment ground leads: 1138 items x 2 leads x 30 ft |  | Equipment grounding |  | Equipment grounding | Grounding | Bare Cu 4/0 AWG, 19 strand (ground grid and equipment grounds) | BARE¦1/C¦4/0 | 1/C | 4/0 | 1 | 1 |  |  |  | Buried | 68280 | 0 |  |  |  |  | allowance
C-G-0002 | C | Grid interface | Station ground grid, rods and risers (from the model) |  | Underground: station ground grid (bare 4/0 Cu mesh, rods, risers) |  | Underground: station ground grid (bare 4/0 Cu mesh, rods, risers) | Grounding | Bare Cu 4/0 AWG, 19 strand (ground grid and equipment grounds) | BARE¦1/C¦4/0 | 1/C | 4/0 | 1 | 1 |  |  |  | Buried | 68700 | 0 |  |  |  |  | measured from the modelled grid
C-HV-0001 | C | Grid interface | 230 kV underground circuit (BESS) | BESS-230-A | 230 kV BESS tie: switchyard end | BESS-230-B | 230 kV BESS tie: plant end | HV 230 kV | HV XLPE 230 kV 1/C 2500 kcmil Cu, Cu wire shield, Al laminate, HDPE jacket | HV230¦1/C¦2500 | 1/C | 2500 kcmil | 1 | 3 | 230000 |  |  | HV duct bank | 182 | 80 |  |  |  |  | route length from the model + 2 x 40 ft risers
C-HV-0002 | C | Grid interface | 230 kV underground circuit (CCS) | CCS-230-A | 230 kV CCS tie: switchyard end | CCS-230-B | 230 kV CCS tie: plant end | HV 230 kV | HV XLPE 230 kV 1/C 2500 kcmil Cu, Cu wire shield, Al laminate, HDPE jacket | HV230¦1/C¦2500 | 1/C | 2500 kcmil | 1 | 3 | 230000 |  |  | HV duct bank | 1486 | 80 |  |  |  |  | route length from the model + 2 x 40 ft risers
C-HV-0003 | C | Grid interface | 230 kV underground circuit (CCS) | CCS-230-A | 230 kV CCS tie: switchyard end | CCS-230-B | 230 kV CCS tie: plant end | HV 230 kV | HV XLPE 230 kV 1/C 2500 kcmil Cu, Cu wire shield, Al laminate, HDPE jacket | HV230¦1/C¦2500 | 1/C | 2500 kcmil | 1 | 3 | 230000 |  |  | HV duct bank | 1536 | 80 |  |  |  |  | route length from the model + 2 x 40 ft risers
C-HV-0004 | C | Grid interface | 230 kV underground circuit (H2) | H2-230-A | 230 kV H2 tie: switchyard end | H2-230-B | 230 kV H2 tie: plant end | HV 230 kV | HV XLPE 230 kV 1/C 2500 kcmil Cu, Cu wire shield, Al laminate, HDPE jacket | HV230¦1/C¦2500 | 1/C | 2500 kcmil | 1 | 3 | 230000 |  |  | HV duct bank | 1720 | 80 |  |  |  |  | route length from the model + 2 x 40 ft risers
C-HV-0005 | C | Grid interface | 230 kV underground circuit (H2) | H2-230-A | 230 kV H2 tie: switchyard end | H2-230-B | 230 kV H2 tie: plant end | HV 230 kV | HV XLPE 230 kV 1/C 2500 kcmil Cu, Cu wire shield, Al laminate, HDPE jacket | HV230¦1/C¦2500 | 1/C | 2500 kcmil | 1 | 3 | 230000 |  |  | HV duct bank | 12 | 80 |  |  |  |  | route length from the model + 2 x 40 ft risers
C-HV-0006 | C | Grid interface | 230 kV underground circuit (MOD) | MOD-230-A | 230 kV MOD tie: switchyard end | MOD-230-B | 230 kV MOD tie: plant end | HV 230 kV | HV XLPE 230 kV 1/C 2500 kcmil Cu, Cu wire shield, Al laminate, HDPE jacket | HV230¦1/C¦2500 | 1/C | 2500 kcmil | 1 | 3 | 230000 |  |  | HV duct bank | 10 | 80 |  |  |  |  | route length from the model + 2 x 40 ft risers
C-I-0001 | C | Grid interface | Analog instrument to JB JB-D1-CB1-AI01: 2 x 1 pr (field cables) | D1-CB1 | D1 230 kV breaker 1 | JB-D1-CB1-AI01 | D1 230 kV breaker 1 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 2 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0002 | C | Grid interface | Home run JB-D1-CB1-AI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D1-CB1-AI01 | D1 230 kV breaker 1 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 274 | 40
C-I-0003 | C | Grid interface | Discrete device to JB JB-D1-CB1-DI01: 20 x 1 pr (field cables) | D1-CB1 | D1 230 kV breaker 1 | JB-D1-CB1-DI01 | D1 230 kV breaker 1 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0004 | C | Grid interface | Home run JB-D1-CB1-DI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D1-CB1-DI01 | D1 230 kV breaker 1 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 274 | 40
C-I-0005 | C | Grid interface | Analog instrument to JB JB-D1-CB2-AI01: 2 x 1 pr (field cables) | D1-CB2 | D1 230 kV breaker 2 | JB-D1-CB2-AI01 | D1 230 kV breaker 2 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 2 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0006 | C | Grid interface | Home run JB-D1-CB2-AI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D1-CB2-AI01 | D1 230 kV breaker 2 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 274 | 52
C-I-0007 | C | Grid interface | Discrete device to JB JB-D1-CB2-DI01: 20 x 1 pr (field cables) | D1-CB2 | D1 230 kV breaker 2 | JB-D1-CB2-DI01 | D1 230 kV breaker 2 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0008 | C | Grid interface | Home run JB-D1-CB2-DI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D1-CB2-DI01 | D1 230 kV breaker 2 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 274 | 52
C-I-0009 | C | Grid interface | Analog instrument to JB JB-D1-CB3-AI01: 2 x 1 pr (field cables) | D1-CB3 | D1 230 kV breaker 3 | JB-D1-CB3-AI01 | D1 230 kV breaker 3 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 2 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0010 | C | Grid interface | Home run JB-D1-CB3-AI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D1-CB3-AI01 | D1 230 kV breaker 3 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 274 | 92
C-I-0011 | C | Grid interface | Discrete device to JB JB-D1-CB3-DI01: 20 x 1 pr (field cables) | D1-CB3 | D1 230 kV breaker 3 | JB-D1-CB3-DI01 | D1 230 kV breaker 3 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0012 | C | Grid interface | Home run JB-D1-CB3-DI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D1-CB3-DI01 | D1 230 kV breaker 3 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 274 | 92
C-I-0013 | C | Grid interface | Analog instrument to JB JB-D2-CB1-AI01: 2 x 1 pr (field cables) | D2-CB1 | D2 230 kV breaker 1 | JB-D2-CB1-AI01 | D2 230 kV breaker 1 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 2 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0014 | C | Grid interface | Home run JB-D2-CB1-AI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D2-CB1-AI01 | D2 230 kV breaker 1 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 474 | 40
C-I-0015 | C | Grid interface | Discrete device to JB JB-D2-CB1-DI01: 20 x 1 pr (field cables) | D2-CB1 | D2 230 kV breaker 1 | JB-D2-CB1-DI01 | D2 230 kV breaker 1 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0016 | C | Grid interface | Home run JB-D2-CB1-DI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D2-CB1-DI01 | D2 230 kV breaker 1 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 474 | 40
C-I-0017 | C | Grid interface | Analog instrument to JB JB-D2-CB2-AI01: 2 x 1 pr (field cables) | D2-CB2 | D2 230 kV breaker 2 | JB-D2-CB2-AI01 | D2 230 kV breaker 2 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 2 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0018 | C | Grid interface | Home run JB-D2-CB2-AI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D2-CB2-AI01 | D2 230 kV breaker 2 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 474 | 52
C-I-0019 | C | Grid interface | Discrete device to JB JB-D2-CB2-DI01: 20 x 1 pr (field cables) | D2-CB2 | D2 230 kV breaker 2 | JB-D2-CB2-DI01 | D2 230 kV breaker 2 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0020 | C | Grid interface | Home run JB-D2-CB2-DI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D2-CB2-DI01 | D2 230 kV breaker 2 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 474 | 52
C-I-0021 | C | Grid interface | Analog instrument to JB JB-D2-CB3-AI01: 2 x 1 pr (field cables) | D2-CB3 | D2 230 kV breaker 3 | JB-D2-CB3-AI01 | D2 230 kV breaker 3 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 2 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0022 | C | Grid interface | Home run JB-D2-CB3-AI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D2-CB3-AI01 | D2 230 kV breaker 3 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 474 | 92
C-I-0023 | C | Grid interface | Discrete device to JB JB-D2-CB3-DI01: 20 x 1 pr (field cables) | D2-CB3 | D2 230 kV breaker 3 | JB-D2-CB3-DI01 | D2 230 kV breaker 3 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0024 | C | Grid interface | Home run JB-D2-CB3-DI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D2-CB3-DI01 | D2 230 kV breaker 3 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 474 | 92
C-I-0025 | C | Grid interface | Analog instrument to JB JB-D3-CB1-AI01: 2 x 1 pr (field cables) | D3-CB1 | D3 230 kV breaker 1 | JB-D3-CB1-AI01 | D3 230 kV breaker 1 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 2 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0026 | C | Grid interface | Home run JB-D3-CB1-AI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D3-CB1-AI01 | D3 230 kV breaker 1 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 674 | 40
C-I-0027 | C | Grid interface | Discrete device to JB JB-D3-CB1-DI01: 20 x 1 pr (field cables) | D3-CB1 | D3 230 kV breaker 1 | JB-D3-CB1-DI01 | D3 230 kV breaker 1 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0028 | C | Grid interface | Home run JB-D3-CB1-DI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D3-CB1-DI01 | D3 230 kV breaker 1 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 674 | 40
C-I-0029 | C | Grid interface | Analog instrument to JB JB-D3-CB2-AI01: 2 x 1 pr (field cables) | D3-CB2 | D3 230 kV breaker 2 | JB-D3-CB2-AI01 | D3 230 kV breaker 2 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 2 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0030 | C | Grid interface | Home run JB-D3-CB2-AI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D3-CB2-AI01 | D3 230 kV breaker 2 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 674 | 52
C-I-0031 | C | Grid interface | Discrete device to JB JB-D3-CB2-DI01: 20 x 1 pr (field cables) | D3-CB2 | D3 230 kV breaker 2 | JB-D3-CB2-DI01 | D3 230 kV breaker 2 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0032 | C | Grid interface | Home run JB-D3-CB2-DI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D3-CB2-DI01 | D3 230 kV breaker 2 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 674 | 52
C-I-0033 | C | Grid interface | Analog instrument to JB JB-D3-CB3-AI01: 2 x 1 pr (field cables) | D3-CB3 | D3 230 kV breaker 3 | JB-D3-CB3-AI01 | D3 230 kV breaker 3 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 2 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0034 | C | Grid interface | Home run JB-D3-CB3-AI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D3-CB3-AI01 | D3 230 kV breaker 3 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 674 | 92
C-I-0035 | C | Grid interface | Discrete device to JB JB-D3-CB3-DI01: 20 x 1 pr (field cables) | D3-CB3 | D3 230 kV breaker 3 | JB-D3-CB3-DI01 | D3 230 kV breaker 3 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0036 | C | Grid interface | Home run JB-D3-CB3-DI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D3-CB3-DI01 | D3 230 kV breaker 3 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 674 | 92
C-I-0037 | C | Grid interface | Analog instrument to JB JB-D4-CB1-AI01: 2 x 1 pr (field cables) | D4-CB1 | D4 230 kV breaker 1 (build-out) | JB-D4-CB1-AI01 | D4 230 kV breaker 1 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 2 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0038 | C | Grid interface | Home run JB-D4-CB1-AI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D4-CB1-AI01 | D4 230 kV breaker 1 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 1294 | 40
C-I-0039 | C | Grid interface | Discrete device to JB JB-D4-CB1-DI01: 20 x 1 pr (field cables) | D4-CB1 | D4 230 kV breaker 1 (build-out) | JB-D4-CB1-DI01 | D4 230 kV breaker 1 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0040 | C | Grid interface | Home run JB-D4-CB1-DI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D4-CB1-DI01 | D4 230 kV breaker 1 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 1294 | 40
C-I-0041 | C | Grid interface | Analog instrument to JB JB-D4-CB2-AI01: 2 x 1 pr (field cables) | D4-CB2 | D4 230 kV breaker 2 (build-out) | JB-D4-CB2-AI01 | D4 230 kV breaker 2 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 2 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0042 | C | Grid interface | Home run JB-D4-CB2-AI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D4-CB2-AI01 | D4 230 kV breaker 2 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 1294 | 52
C-I-0043 | C | Grid interface | Discrete device to JB JB-D4-CB2-DI01: 20 x 1 pr (field cables) | D4-CB2 | D4 230 kV breaker 2 (build-out) | JB-D4-CB2-DI01 | D4 230 kV breaker 2 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0044 | C | Grid interface | Home run JB-D4-CB2-DI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D4-CB2-DI01 | D4 230 kV breaker 2 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 1294 | 52
C-I-0045 | C | Grid interface | Analog instrument to JB JB-D4-CB3-AI01: 2 x 1 pr (field cables) | D4-CB3 | D4 230 kV breaker 3 (build-out) | JB-D4-CB3-AI01 | D4 230 kV breaker 3 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 2 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0046 | C | Grid interface | Home run JB-D4-CB3-AI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D4-CB3-AI01 | D4 230 kV breaker 3 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 1340 | 46
C-I-0047 | C | Grid interface | Discrete device to JB JB-D4-CB3-DI01: 20 x 1 pr (field cables) | D4-CB3 | D4 230 kV breaker 3 (build-out) | JB-D4-CB3-DI01 | D4 230 kV breaker 3 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0048 | C | Grid interface | Home run JB-D4-CB3-DI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D4-CB3-DI01 | D4 230 kV breaker 3 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 1340 | 46
C-I-0049 | C | Grid interface | Analog instrument to JB JB-D5-CB1-AI01: 2 x 1 pr (field cables) | D5-CB1 | D5 230 kV breaker 1 (build-out) | JB-D5-CB1-AI01 | D5 230 kV breaker 1 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 2 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0050 | C | Grid interface | Home run JB-D5-CB1-AI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D5-CB1-AI01 | D5 230 kV breaker 1 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 1434 | 40
C-I-0051 | C | Grid interface | Discrete device to JB JB-D5-CB1-DI01: 20 x 1 pr (field cables) | D5-CB1 | D5 230 kV breaker 1 (build-out) | JB-D5-CB1-DI01 | D5 230 kV breaker 1 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0052 | C | Grid interface | Home run JB-D5-CB1-DI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D5-CB1-DI01 | D5 230 kV breaker 1 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 1434 | 40
C-I-0053 | C | Grid interface | Analog instrument to JB JB-D5-CB2-AI01: 2 x 1 pr (field cables) | D5-CB2 | D5 230 kV breaker 2 (build-out) | JB-D5-CB2-AI01 | D5 230 kV breaker 2 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 2 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0054 | C | Grid interface | Home run JB-D5-CB2-AI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D5-CB2-AI01 | D5 230 kV breaker 2 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 1434 | 52
C-I-0055 | C | Grid interface | Discrete device to JB JB-D5-CB2-DI01: 20 x 1 pr (field cables) | D5-CB2 | D5 230 kV breaker 2 (build-out) | JB-D5-CB2-DI01 | D5 230 kV breaker 2 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0056 | C | Grid interface | Home run JB-D5-CB2-DI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D5-CB2-DI01 | D5 230 kV breaker 2 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 1434 | 52
C-I-0057 | C | Grid interface | Analog instrument to JB JB-D5-CB3-AI01: 2 x 1 pr (field cables) | D5-CB3 | D5 230 kV breaker 3 (build-out) | JB-D5-CB3-AI01 | D5 230 kV breaker 3 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 2 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0058 | C | Grid interface | Home run JB-D5-CB3-AI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D5-CB3-AI01 | D5 230 kV breaker 3 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 1434 | 92
C-I-0059 | C | Grid interface | Discrete device to JB JB-D5-CB3-DI01: 20 x 1 pr (field cables) | D5-CB3 | D5 230 kV breaker 3 (build-out) | JB-D5-CB3-DI01 | D5 230 kV breaker 3 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0060 | C | Grid interface | Home run JB-D5-CB3-DI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D5-CB3-DI01 | D5 230 kV breaker 3 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 1434 | 92
C-I-0061 | C | Grid interface | Analog instrument to JB JB-D6-CB1-AI01: 2 x 1 pr (field cables) | D6-CB1 | D6 230 kV breaker 1 (build-out) | JB-D6-CB1-AI01 | D6 230 kV breaker 1 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 2 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0062 | C | Grid interface | Home run JB-D6-CB1-AI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D6-CB1-AI01 | D6 230 kV breaker 1 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 1584 | 40
C-I-0063 | C | Grid interface | Discrete device to JB JB-D6-CB1-DI01: 20 x 1 pr (field cables) | D6-CB1 | D6 230 kV breaker 1 (build-out) | JB-D6-CB1-DI01 | D6 230 kV breaker 1 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0064 | C | Grid interface | Home run JB-D6-CB1-DI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D6-CB1-DI01 | D6 230 kV breaker 1 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 1584 | 40
C-I-0065 | C | Grid interface | Analog instrument to JB JB-D6-CB2-AI01: 2 x 1 pr (field cables) | D6-CB2 | D6 230 kV breaker 2 (build-out) | JB-D6-CB2-AI01 | D6 230 kV breaker 2 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 2 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0066 | C | Grid interface | Home run JB-D6-CB2-AI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D6-CB2-AI01 | D6 230 kV breaker 2 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 1584 | 52
C-I-0067 | C | Grid interface | Discrete device to JB JB-D6-CB2-DI01: 20 x 1 pr (field cables) | D6-CB2 | D6 230 kV breaker 2 (build-out) | JB-D6-CB2-DI01 | D6 230 kV breaker 2 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0068 | C | Grid interface | Home run JB-D6-CB2-DI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D6-CB2-DI01 | D6 230 kV breaker 2 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 1584 | 52
C-I-0069 | C | Grid interface | Analog instrument to JB JB-D6-CB3-AI01: 2 x 1 pr (field cables) | D6-CB3 | D6 230 kV breaker 3 (build-out) | JB-D6-CB3-AI01 | D6 230 kV breaker 3 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 2 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0070 | C | Grid interface | Home run JB-D6-CB3-AI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D6-CB3-AI01 | D6 230 kV breaker 3 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 1584 | 92
C-I-0071 | C | Grid interface | Discrete device to JB JB-D6-CB3-DI01: 20 x 1 pr (field cables) | D6-CB3 | D6 230 kV breaker 3 (build-out) | JB-D6-CB3-DI01 | D6 230 kV breaker 3 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 52 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0072 | C | Grid interface | Home run JB-D6-CB3-DI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-D6-CB3-DI01 | D6 230 kV breaker 3 (build-out) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 1584 | 92
C-I-0073 | C | Grid interface | Discrete device to JB JB-Line-1-DI01: 4 x 1 pr (field cables) | Line-1 | Line 1 230 kV terminal tower | JB-Line-1-DI01 | Line 1 230 kV terminal tower | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 77 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0074 | C | Grid interface | Home run JB-Line-1-DI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-Line-1-DI01 | Line 1 230 kV terminal tower | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 91 | 285
C-I-0075 | C | Grid interface | Discrete device to JB JB-Line 1 entrance: s-DI01: 4 x 1 pr (field cables) |  | Line 1 entrance: surge arresters, CCVTs and line traps | JB-Line 1 entrance: s-DI01 | Line 1 entrance: surge arresters, CCVTs and line traps | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 55 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0076 | C | Grid interface | Home run JB-Line 1 entrance: s-DI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-Line 1 entrance: s-DI01 | Line 1 entrance: surge arresters, CCVTs and line traps | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 91 | 226
C-I-0077 | C | Grid interface | Discrete device to JB JB-Line-2-DI01: 4 x 1 pr (field cables) | Line-2 | Line 2 230 kV terminal tower | JB-Line-2-DI01 | Line 2 230 kV terminal tower | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 77 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0078 | C | Grid interface | Home run JB-Line-2-DI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-Line-2-DI01 | Line 2 230 kV terminal tower | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 526 | 86
C-I-0079 | C | Grid interface | Discrete device to JB JB-Line 2 entrance: s-DI01: 4 x 1 pr (field cables) |  | Line 2 entrance: surge arresters, CCVTs and line traps | JB-Line 2 entrance: s-DI01 | Line 2 entrance: surge arresters, CCVTs and line traps | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 55 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0080 | C | Grid interface | Home run JB-Line 2 entrance: s-DI01 to the control / marshalling room | RH | RH: switchyard relay / control house (52 x 70 ft) | JB-Line 2 entrance: s-DI01 | Line 2 entrance: surge arresters, CCVTs and line traps | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Trench | 474 | 78
C-P-0001 | C | Grid interface | Yard lighting circuit 1 (10 floodlights) | RH | RH: switchyard relay / control house (52 x 70 ft) |  | 230 kV switchyard (gravel) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 4 | 6 | Buried | 900 | 30 |  |  |  |  | pole to pole, buried
C-P-0002 | C | Grid interface | Yard lighting circuit 2 (10 floodlights) | RH | RH: switchyard relay / control house (52 x 70 ft) |  | 230 kV switchyard (gravel) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 4 | 6 | Buried | 900 | 30 |  |  |  |  | pole to pole, buried
C-P-0003 | C | Grid interface | Yard lighting circuit 3 (10 floodlights) | RH | RH: switchyard relay / control house (52 x 70 ft) |  | 230 kV switchyard (gravel) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 4 | 6 | Buried | 900 | 30 |  |  |  |  | pole to pole, buried
C-P-0004 | C | Grid interface | Yard lighting circuit 4 (10 floodlights) | RH | RH: switchyard relay / control house (52 x 70 ft) |  | 230 kV switchyard (gravel) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 4 | 6 | Buried | 900 | 30 |  |  |  |  | pole to pole, buried
C-P-0005 | C | Grid interface | LV panel / distribution feeder | RH | RH: switchyard relay / control house (52 x 70 ft) | RH | RH: switchyard relay / control house (52 x 70 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 44 | 62.3 | Tray | 0 | 30 |  |  |  |  | VD 0.2 %
C-OH-0001 | C | Grid interface | 230 kV overhead GSU / line conductors | OH-1-A | 230 kV overhead span start | OH-1-B | 230 kV overhead span end | Overhead | Overhead conductor ACSR 1590 kcmil 'Falcon' (typ.) | ACSR¦1/C¦1590 | 1/C | 1590 kcmil | 1 | 3 | 230000 |  |  | Overhead | 115 | 0 |  |  |  |  | plus 3 % sag
C-OH-0002 | C | Grid interface | 230 kV overhead GSU / line conductors | OH-2-A | 230 kV overhead span start | OH-2-B | 230 kV overhead span end | Overhead | Overhead conductor ACSR 1590 kcmil 'Falcon' (typ.) | ACSR¦1/C¦1590 | 1/C | 1590 kcmil | 1 | 3 | 230000 |  |  | Overhead | 115 | 0 |  |  |  |  | plus 3 % sag
C-OH-0003 | C | Grid interface | 230 kV overhead GSU / line conductors | OH-3-A | 230 kV overhead span start | OH-3-B | 230 kV overhead span end | Overhead | Overhead conductor ACSR 1590 kcmil 'Falcon' (typ.) | ACSR¦1/C¦1590 | 1/C | 1590 kcmil | 1 | 3 | 230000 |  |  | Overhead | 263 | 0 |  |  |  |  | plus 3 % sag
C-OH-0004 | C | Grid interface | 230 kV overhead GSU / line conductors | OH-4-A | 230 kV overhead span start | OH-4-B | 230 kV overhead span end | Overhead | Overhead conductor ACSR 1590 kcmil 'Falcon' (typ.) | ACSR¦1/C¦1590 | 1/C | 1590 kcmil | 1 | 3 | 230000 |  |  | Overhead | 304 | 0 |  |  |  |  | plus 3 % sag
C-OH-0005 | C | Grid interface | 230 kV overhead GSU / line conductors | OH-5-A | 230 kV overhead span start | OH-5-B | 230 kV overhead span end | Overhead | Overhead conductor ACSR 1590 kcmil 'Falcon' (typ.) | ACSR¦1/C¦1590 | 1/C | 1590 kcmil | 1 | 3 | 230000 |  |  | Overhead | 324 | 0 |  |  |  |  | plus 3 % sag
C-OH-0006 | C | Grid interface | 230 kV overhead GSU / line conductors | OH-6-A | 230 kV overhead span start | OH-6-B | 230 kV overhead span end | Overhead | Overhead conductor ACSR 1590 kcmil 'Falcon' (typ.) | ACSR¦1/C¦1590 | 1/C | 1590 kcmil | 1 | 3 | 230000 |  |  | Overhead | 236 | 0 |  |  |  |  | plus 3 % sag
C-OH-0007 | C | Grid interface | 230 kV overhead H-MOD tie conductors | OH-7-A | 230 kV overhead span start | OH-7-B | 230 kV overhead span end | Overhead | Overhead conductor ACSR 1590 kcmil 'Falcon' (typ.) | ACSR¦1/C¦1590 | 1/C | 1590 kcmil | 1 | 3 | 230000 |  |  | Overhead | 1544 | 0 |  |  |  |  | plus 3 % sag
D-C-0001 | D | Fuel gas | Control |  | Gas yard local control enclosure |  | CONDITIONAL: ULSD truck unloading station (canopy, spill containment) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 65 | 132
D-C-0002 | D | Fuel gas | Control |  | Gas yard local control enclosure |  | CONDITIONAL: ULSD unloading and forwarding pumps, duplex filters | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 65 | 59
D-C-0003 | D | Fuel gas | Control |  | Gas yard local control enclosure |  | CONDITIONAL: backup fuel oil (ULSD) unloading and forwarding area | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 65 | 42
D-C-0004 | D | Fuel gas | Motor 1 of 6: control / local station | MCC-C1 | R1 MCC-C1 |  | CONDITIONAL: fuel-gas compressors | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 2412 | 157
D-C-0005 | D | Fuel gas | Motor 2 of 6: control / local station | MCC-C1 | R1 MCC-C1 |  | CONDITIONAL: fuel-gas compressors | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 2412 | 157
D-C-0006 | D | Fuel gas | Motor 3 of 6: control / local station | MCC-C1 | R1 MCC-C1 |  | CONDITIONAL: fuel-gas compressors | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 2412 | 157
D-C-0007 | D | Fuel gas | Motor 4 of 6: control / local station | MCC-C1 | R1 MCC-C1 |  | CONDITIONAL: fuel-gas compressors | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 2412 | 157
D-C-0008 | D | Fuel gas | Motor 5 of 6: control / local station | MCC-C1 | R1 MCC-C1 |  | CONDITIONAL: fuel-gas compressors | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 2412 | 157
D-C-0009 | D | Fuel gas | Motor 6 of 6: control / local station | MCC-C1 | R1 MCC-C1 |  | CONDITIONAL: fuel-gas compressors | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 2412 | 157
D-C-0010 | D | Fuel gas | Control |  | Gas yard local control enclosure | CPR-1 | CPR-1: cathodic-protection rectifier | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 84
D-C-0011 | D | Fuel gas | Solenoid to JB JB-Gas pressure regul-SOL01: 6 x 2/C (field cables) |  | Gas pressure regulation skid | JB-Gas pressure regul-SOL01 | Gas pressure regulation skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 6 | 1 |  |  |  | Tray / conduit | 60 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
D-C-0012 | D | Fuel gas | Home run JB-Gas pressure regul-SOL01 to the control / marshalling room |  | Gas yard local control enclosure | JB-Gas pressure regul-SOL01 | Gas pressure regulation skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 193 | 32
D-C-0013 | D | Fuel gas | Solenoid to JB JB-Gas yard filter-se-SOL01: 4 x 2/C (field cables) |  | Gas yard filter-separators | JB-Gas yard filter-se-SOL01 | Gas yard filter-separators | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 4 | 1 |  |  |  | Tray / conduit | 60 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
D-C-0014 | D | Fuel gas | Home run JB-Gas yard filter-se-SOL01 to the control / marshalling room |  | Gas yard local control enclosure | JB-Gas yard filter-se-SOL01 | Gas yard filter-separators | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 83 | 32
D-C-0015 | D | Fuel gas | Solenoid to JB JB-Gas yard inlet: ES-SOL01: 4 x 2/C (field cables) |  | Gas yard inlet: ESD valve, block valve and insulating joint | JB-Gas yard inlet: ES-SOL01 | Gas yard inlet: ESD valve, block valve and insulating joint | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 4 | 1 |  |  |  | Tray / conduit | 46 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
D-C-0016 | D | Fuel gas | Home run JB-Gas yard inlet: ES-SOL01 to the control / marshalling room |  | Gas yard local control enclosure | JB-Gas yard inlet: ES-SOL01 | Gas yard inlet: ESD valve, block valve and insulating joint | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 193 | 129
D-C-0017 | D | Fuel gas | Control |  | Gas yard local control enclosure |  | Gas yard local control enclosure | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 32
D-C-0018 | D | Fuel gas | Control |  | Gas yard local control enclosure | HTP-4 | HTP-4: heat-trace panel (gas) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 15 | 32
D-I-0001 | D | Fuel gas | Analog instrument to JB JB-CONDITIONAL: ULSD -AI01: 4 x 1 pr (field cables) |  | CONDITIONAL: ULSD backup fuel-oil tank | JB-CONDITIONAL: ULSD -AI01 | CONDITIONAL: ULSD backup fuel-oil tank | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 134 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
D-I-0002 | D | Fuel gas | Home run JB-CONDITIONAL: ULSD -AI01 to the control / marshalling room |  | Gas yard local control enclosure | JB-CONDITIONAL: ULSD -AI01 | CONDITIONAL: ULSD backup fuel-oil tank | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 199 | 32
D-I-0003 | D | Fuel gas | Discrete device to JB JB-CONDITIONAL: ULSD -DI01: 4 x 1 pr (field cables) |  | CONDITIONAL: ULSD backup fuel-oil tank | JB-CONDITIONAL: ULSD -DI01 | CONDITIONAL: ULSD backup fuel-oil tank | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 134 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
D-I-0004 | D | Fuel gas | Home run JB-CONDITIONAL: ULSD -DI01 to the control / marshalling room |  | Gas yard local control enclosure | JB-CONDITIONAL: ULSD -DI01 | CONDITIONAL: ULSD backup fuel-oil tank | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 199 | 32
D-I-0005 | D | Fuel gas | Analog instrument to JB JB-CONDITIONAL: ULSD -AI01: 4 x 1 pr (field cables) |  | CONDITIONAL: ULSD tank containment dike | JB-CONDITIONAL: ULSD -AI01 | CONDITIONAL: ULSD tank containment dike | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 137 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
D-I-0006 | D | Fuel gas | Home run JB-CONDITIONAL: ULSD -AI01 to the control / marshalling room |  | Gas yard local control enclosure | JB-CONDITIONAL: ULSD -AI01 | CONDITIONAL: ULSD tank containment dike | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 154 | 67
D-I-0007 | D | Fuel gas | Discrete device to JB JB-CONDITIONAL: ULSD -DI01: 4 x 1 pr (field cables) |  | CONDITIONAL: ULSD tank containment dike | JB-CONDITIONAL: ULSD -DI01 | CONDITIONAL: ULSD tank containment dike | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 137 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
D-I-0008 | D | Fuel gas | Home run JB-CONDITIONAL: ULSD -DI01 to the control / marshalling room |  | Gas yard local control enclosure | JB-CONDITIONAL: ULSD -DI01 | CONDITIONAL: ULSD tank containment dike | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 154 | 67
D-I-0009 | D | Fuel gas | Instrumentation |  | Gas yard local control enclosure |  | CONDITIONAL: ULSD truck unloading station (canopy, spill containment) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 65 | 132
D-I-0010 | D | Fuel gas | Instrumentation |  | Gas yard local control enclosure |  | CONDITIONAL: ULSD unloading and forwarding pumps, duplex filters | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 65 | 59
D-I-0011 | D | Fuel gas | Instrumentation |  | Gas yard local control enclosure |  | CONDITIONAL: ULSD unloading and forwarding pumps, duplex filters | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Tray | 65 | 59
D-I-0012 | D | Fuel gas | Instrumentation |  | Gas yard local control enclosure |  | CONDITIONAL: backup fuel oil (ULSD) unloading and forwarding area | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 65 | 42
D-I-0013 | D | Fuel gas | Analog instrument to JB JB-CONDITIONAL: fuel--AI01: 20 x 1 pr (field cables) |  | CONDITIONAL: fuel-gas compressors | JB-CONDITIONAL: fuel--AI01 | CONDITIONAL: fuel-gas compressors | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 133 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
D-I-0014 | D | Fuel gas | Home run JB-CONDITIONAL: fuel--AI01 to the control / marshalling room |  | Gas yard local control enclosure | JB-CONDITIONAL: fuel--AI01 | CONDITIONAL: fuel-gas compressors | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 553 | 32
D-I-0015 | D | Fuel gas | Analog instrument to JB JB-CONDITIONAL: fuel--AI02: 10 x 1 pr (field cables) |  | CONDITIONAL: fuel-gas compressors | JB-CONDITIONAL: fuel--AI02 | CONDITIONAL: fuel-gas compressors | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 133 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
D-I-0016 | D | Fuel gas | Home run JB-CONDITIONAL: fuel--AI02 to the control / marshalling room |  | Gas yard local control enclosure | JB-CONDITIONAL: fuel--AI02 | CONDITIONAL: fuel-gas compressors | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 553 | 32
D-I-0017 | D | Fuel gas | Discrete device to JB JB-CONDITIONAL: fuel--DI01: 20 x 1 pr (field cables) |  | CONDITIONAL: fuel-gas compressors | JB-CONDITIONAL: fuel--DI01 | CONDITIONAL: fuel-gas compressors | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 133 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
D-I-0018 | D | Fuel gas | Home run JB-CONDITIONAL: fuel--DI01 to the control / marshalling room |  | Gas yard local control enclosure | JB-CONDITIONAL: fuel--DI01 | CONDITIONAL: fuel-gas compressors | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 553 | 32
D-I-0019 | D | Fuel gas | RTD to JB JB-CONDITIONAL: fuel--RTD01: 10 x 1 tri (field cables) |  | CONDITIONAL: fuel-gas compressors | JB-CONDITIONAL: fuel--RTD01 | CONDITIONAL: fuel-gas compressors | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 133 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
D-I-0020 | D | Fuel gas | Home run JB-CONDITIONAL: fuel--RTD01 to the control / marshalling room |  | Gas yard local control enclosure | JB-CONDITIONAL: fuel--RTD01 | CONDITIONAL: fuel-gas compressors | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 553 | 32
D-I-0021 | D | Fuel gas | RTD to JB JB-CONDITIONAL: fuel--RTD02: 2 x 1 tri (field cables) |  | CONDITIONAL: fuel-gas compressors | JB-CONDITIONAL: fuel--RTD02 | CONDITIONAL: fuel-gas compressors | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 2 | 1 |  |  |  | Tray / conduit | 133 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
D-I-0022 | D | Fuel gas | Home run JB-CONDITIONAL: fuel--RTD02 to the control / marshalling room |  | Gas yard local control enclosure | JB-CONDITIONAL: fuel--RTD02 | CONDITIONAL: fuel-gas compressors | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 553 | 32
D-I-0023 | D | Fuel gas | Instrumentation |  | Gas yard local control enclosure | CPR-1 | CPR-1: cathodic-protection rectifier | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 84
D-I-0024 | D | Fuel gas | Analog instrument to JB JB-Fuel-gas performan-AI01: 10 x 1 pr (field cables) |  | Fuel-gas performance heater | JB-Fuel-gas performan-AI01 | Fuel-gas performance heater | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 61 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
D-I-0025 | D | Fuel gas | Home run JB-Fuel-gas performan-AI01 to the control / marshalling room |  | Gas yard local control enclosure | JB-Fuel-gas performan-AI01 | Fuel-gas performance heater | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 143 | 32
D-I-0026 | D | Fuel gas | Discrete device to JB JB-Fuel-gas performan-DI01: 10 x 1 pr (field cables) |  | Fuel-gas performance heater | JB-Fuel-gas performan-DI01 | Fuel-gas performance heater | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 61 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
D-I-0027 | D | Fuel gas | Home run JB-Fuel-gas performan-DI01 to the control / marshalling room |  | Gas yard local control enclosure | JB-Fuel-gas performan-DI01 | Fuel-gas performance heater | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 143 | 32
D-I-0028 | D | Fuel gas | Analog instrument to JB JB-Gas metering skid-AI01: 20 x 1 pr (field cables) |  | Gas metering skid | JB-Gas metering skid-AI01 | Gas metering skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 64 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
D-I-0029 | D | Fuel gas | Home run JB-Gas metering skid-AI01 to the control / marshalling room |  | Gas yard local control enclosure | JB-Gas metering skid-AI01 | Gas metering skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 83 | 72
D-I-0030 | D | Fuel gas | Discrete device to JB JB-Gas metering skid-DI01: 8 x 1 pr (field cables) |  | Gas metering skid | JB-Gas metering skid-DI01 | Gas metering skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 64 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
D-I-0031 | D | Fuel gas | Home run JB-Gas metering skid-DI01 to the control / marshalling room |  | Gas yard local control enclosure | JB-Gas metering skid-DI01 | Gas metering skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 83 | 72
D-I-0032 | D | Fuel gas | Analog instrument to JB JB-Gas pressure regul-AI01: 12 x 1 pr (field cables) |  | Gas pressure regulation skid | JB-Gas pressure regul-AI01 | Gas pressure regulation skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 60 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
D-I-0033 | D | Fuel gas | Home run JB-Gas pressure regul-AI01 to the control / marshalling room |  | Gas yard local control enclosure | JB-Gas pressure regul-AI01 | Gas pressure regulation skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 193 | 32
D-I-0034 | D | Fuel gas | Discrete device to JB JB-Gas pressure regul-DI01: 12 x 1 pr (field cables) |  | Gas pressure regulation skid | JB-Gas pressure regul-DI01 | Gas pressure regulation skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 60 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
D-I-0035 | D | Fuel gas | Home run JB-Gas pressure regul-DI01 to the control / marshalling room |  | Gas yard local control enclosure | JB-Gas pressure regul-DI01 | Gas pressure regulation skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 193 | 32
D-I-0036 | D | Fuel gas | Analog instrument to JB JB-Gas yard drains / -AI01: 4 x 1 pr (field cables) |  | Gas yard drains / condensate tank in a bund | JB-Gas yard drains / -AI01 | Gas yard drains / condensate tank in a bund | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 56 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
D-I-0037 | D | Fuel gas | Home run JB-Gas yard drains / -AI01 to the control / marshalling room |  | Gas yard local control enclosure | JB-Gas yard drains / -AI01 | Gas yard drains / condensate tank in a bund | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 4 | 114
D-I-0038 | D | Fuel gas | Discrete device to JB JB-Gas yard drains / -DI01: 4 x 1 pr (field cables) |  | Gas yard drains / condensate tank in a bund | JB-Gas yard drains / -DI01 | Gas yard drains / condensate tank in a bund | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 56 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
D-I-0039 | D | Fuel gas | Home run JB-Gas yard drains / -DI01 to the control / marshalling room |  | Gas yard local control enclosure | JB-Gas yard drains / -DI01 | Gas yard drains / condensate tank in a bund | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 4 | 114
D-I-0040 | D | Fuel gas | Analog instrument to JB JB-Gas yard filter-se-AI01: 8 x 1 pr (field cables) |  | Gas yard filter-separators | JB-Gas yard filter-se-AI01 | Gas yard filter-separators | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 60 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
D-I-0041 | D | Fuel gas | Home run JB-Gas yard filter-se-AI01 to the control / marshalling room |  | Gas yard local control enclosure | JB-Gas yard filter-se-AI01 | Gas yard filter-separators | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 83 | 32
D-I-0042 | D | Fuel gas | Discrete device to JB JB-Gas yard filter-se-DI01: 12 x 1 pr (field cables) |  | Gas yard filter-separators | JB-Gas yard filter-se-DI01 | Gas yard filter-separators | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 60 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
D-I-0043 | D | Fuel gas | Home run JB-Gas yard filter-se-DI01 to the control / marshalling room |  | Gas yard local control enclosure | JB-Gas yard filter-se-DI01 | Gas yard filter-separators | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 83 | 32
D-I-0044 | D | Fuel gas | Discrete device to JB JB-Gas yard inlet: ES-DI01: 8 x 1 pr (field cables) |  | Gas yard inlet: ESD valve, block valve and insulating joint | JB-Gas yard inlet: ES-DI01 | Gas yard inlet: ESD valve, block valve and insulating joint | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 46 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
D-I-0045 | D | Fuel gas | Home run JB-Gas yard inlet: ES-DI01 to the control / marshalling room |  | Gas yard local control enclosure | JB-Gas yard inlet: ES-DI01 | Gas yard inlet: ESD valve, block valve and insulating joint | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 193 | 129
D-I-0046 | D | Fuel gas | Instrumentation |  | Gas yard local control enclosure |  | Gas yard local control enclosure | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 32
D-P-0001 | D | Fuel gas | LV power feeder | MCC-C1 | R1 MCC-C1 |  | CONDITIONAL: ULSD backup fuel-oil tank | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 10 | 14.2 | Duct bank | 1902 | 157 |  |  |  |  | VD 2.2 %
D-P-0002 | D | Fuel gas | LV power feeder | MCC-C1 | R1 MCC-C1 |  | CONDITIONAL: ULSD truck unloading station (canopy, spill containment) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 15 | 21.2 | Tray | 1768 | 257 |  |  |  |  | VD 2.6 %
D-P-0003 | D | Fuel gas | LV power feeder | MCC-C1 | R1 MCC-C1 |  | CONDITIONAL: ULSD unloading and forwarding pumps, duplex filters | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦350 | 3/C+G | 350 kcmil | 2 | 1 | 480 | 110 | 155.7 | Tray | 1768 | 184 |  |  |  |  | VD 2.2 %
D-P-0004 | D | Fuel gas | LV power feeder | MCC-C1 | R1 MCC-C1 |  | CONDITIONAL: backup fuel oil (ULSD) unloading and forwarding area | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 15 | 21.2 | Tray | 1768 | 167 |  |  |  |  | VD 2.5 %
D-P-0005 | D | Fuel gas | Motor 1 of 6, 15 kW | MCC-C1 | R1 MCC-C1 |  | CONDITIONAL: fuel-gas compressors | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 2412 | 157 |  |  |  |  | VD 2.6 %
D-P-0006 | D | Fuel gas | Motor 2 of 6, 15 kW | MCC-C1 | R1 MCC-C1 |  | CONDITIONAL: fuel-gas compressors | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 2412 | 157 |  |  |  |  | VD 2.6 %
D-P-0007 | D | Fuel gas | Motor 3 of 6, 15 kW | MCC-C1 | R1 MCC-C1 |  | CONDITIONAL: fuel-gas compressors | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 2412 | 157 |  |  |  |  | VD 2.6 %
D-P-0008 | D | Fuel gas | Motor 4 of 6, 15 kW | MCC-C1 | R1 MCC-C1 |  | CONDITIONAL: fuel-gas compressors | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 2412 | 157 |  |  |  |  | VD 2.6 %
D-P-0009 | D | Fuel gas | Motor 5 of 6, 15 kW | MCC-C1 | R1 MCC-C1 |  | CONDITIONAL: fuel-gas compressors | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 2412 | 157 |  |  |  |  | VD 2.6 %
D-P-0010 | D | Fuel gas | Motor 6 of 6, 15 kW | MCC-C1 | R1 MCC-C1 |  | CONDITIONAL: fuel-gas compressors | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 2412 | 157 |  |  |  |  | VD 2.6 %
D-P-0011 | D | Fuel gas | Cathodic-protection rectifier supply | MCC-C1 | R1 MCC-C1 | CPR-1 | CPR-1: cathodic-protection rectifier | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 10 | 12.7 | Tray | 1833 | 209 |  |  |  |  | VD 2.0 %
D-P-0012 | D | Fuel gas | CP anode / structure leads (allowance) | CPR-1 | CPR-1: cathodic-protection rectifier | CPR-1 | CPR-1: cathodic-protection rectifier | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦1/C¦8 | 1/C | 8 | 1 | 1 |  |  |  | Buried | 1500 | 0 |  |  |  |  | HMWPE anode lead cable by CP vendor; allowance
D-P-0013 | D | Fuel gas | LV power feeder | MCC-C1 | R1 MCC-C1 |  | Fuel-gas performance heater | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 60 | 84.9 | Tray | 2002 | 157 |  |  |  |  | VD 2.7 %
D-P-0014 | D | Fuel gas | LV power feeder | MCC-C1 | R1 MCC-C1 |  | Gas metering skid | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 10 | 14.2 | Tray | 1942 | 197 |  |  |  |  | VD 2.3 %
D-P-0015 | D | Fuel gas | LV power feeder | MCC-C1 | R1 MCC-C1 |  | Gas pressure regulation skid | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 10 | 14.2 | Duct bank | 2052 | 157 |  |  |  |  | VD 2.4 %
D-P-0016 | D | Fuel gas | LV power feeder | MCC-C1 | R1 MCC-C1 |  | Gas yard filter-separators | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 10 | 14.2 | Tray | 1942 | 157 |  |  |  |  | VD 2.3 %
D-P-0017 | D | Fuel gas | LV power feeder | MCC-C1 | R1 MCC-C1 |  | Gas yard inlet: ESD valve, block valve and insulating joint | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 10 | 14.2 | Duct bank | 2052 | 254 |  |  |  |  | VD 2.5 %
D-P-0018 | D | Fuel gas | LV power feeder | MCC-C1 | R1 MCC-C1 |  | Gas yard local control enclosure | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 15 | 21.2 | Tray | 1833 | 157 |  |  |  |  | VD 2.6 %
D-P-0019 | D | Fuel gas | LV power feeder | MCC-C1 | R1 MCC-C1 | HTP-4 | HTP-4: heat-trace panel (gas) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 2 | 1 | 480 | 120 | 169.8 | Tray | 1868 | 157 |  |  |  |  | VD 2.5 %
D-P-0020 | D | Fuel gas | Heat-trace circuit 1 (power to the trace junction box) | HTP-4 | HTP-4: heat-trace panel (gas) | HTP-4 | HTP-4: heat-trace panel (gas) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
D-P-0021 | D | Fuel gas | Heat-trace circuit 2 (power to the trace junction box) | HTP-4 | HTP-4: heat-trace panel (gas) | HTP-4 | HTP-4: heat-trace panel (gas) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
D-P-0022 | D | Fuel gas | Heat-trace circuit 3 (power to the trace junction box) | HTP-4 | HTP-4: heat-trace panel (gas) | HTP-4 | HTP-4: heat-trace panel (gas) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
D-P-0023 | D | Fuel gas | Heat-trace circuit 4 (power to the trace junction box) | HTP-4 | HTP-4: heat-trace panel (gas) | HTP-4 | HTP-4: heat-trace panel (gas) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
D-P-0024 | D | Fuel gas | Heat-trace circuit 5 (power to the trace junction box) | HTP-4 | HTP-4: heat-trace panel (gas) | HTP-4 | HTP-4: heat-trace panel (gas) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
D-P-0025 | D | Fuel gas | Heat-trace circuit 6 (power to the trace junction box) | HTP-4 | HTP-4: heat-trace panel (gas) | HTP-4 | HTP-4: heat-trace panel (gas) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
D-P-0026 | D | Fuel gas | Heat-trace circuit 7 (power to the trace junction box) | HTP-4 | HTP-4: heat-trace panel (gas) | HTP-4 | HTP-4: heat-trace panel (gas) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
D-P-0027 | D | Fuel gas | Heat-trace circuit 8 (power to the trace junction box) | HTP-4 | HTP-4: heat-trace panel (gas) | HTP-4 | HTP-4: heat-trace panel (gas) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
D-P-0028 | D | Fuel gas | Heat-trace circuit 9 (power to the trace junction box) | HTP-4 | HTP-4: heat-trace panel (gas) | HTP-4 | HTP-4: heat-trace panel (gas) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
D-P-0029 | D | Fuel gas | Heat-trace circuit 10 (power to the trace junction box) | HTP-4 | HTP-4: heat-trace panel (gas) | HTP-4 | HTP-4: heat-trace panel (gas) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
D-P-0030 | D | Fuel gas | Heat-trace circuit 11 (power to the trace junction box) | HTP-4 | HTP-4: heat-trace panel (gas) | HTP-4 | HTP-4: heat-trace panel (gas) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
D-P-0031 | D | Fuel gas | Heat-trace circuit 12 (power to the trace junction box) | HTP-4 | HTP-4: heat-trace panel (gas) | HTP-4 | HTP-4: heat-trace panel (gas) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
D-P-0032 | D | Fuel gas | Heat-trace circuit 13 (power to the trace junction box) | HTP-4 | HTP-4: heat-trace panel (gas) | HTP-4 | HTP-4: heat-trace panel (gas) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
D-P-0033 | D | Fuel gas | Heat-trace circuit 14 (power to the trace junction box) | HTP-4 | HTP-4: heat-trace panel (gas) | HTP-4 | HTP-4: heat-trace panel (gas) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
D-P-0034 | D | Fuel gas | Heat-trace circuit 15 (power to the trace junction box) | HTP-4 | HTP-4: heat-trace panel (gas) | HTP-4 | HTP-4: heat-trace panel (gas) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
D-P-0035 | D | Fuel gas | Heat-trace circuit 16 (power to the trace junction box) | HTP-4 | HTP-4: heat-trace panel (gas) | HTP-4 | HTP-4: heat-trace panel (gas) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
D-P-0036 | D | Fuel gas | Heat-trace circuit 17 (power to the trace junction box) | HTP-4 | HTP-4: heat-trace panel (gas) | HTP-4 | HTP-4: heat-trace panel (gas) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
D-P-0037 | D | Fuel gas | Heat-trace circuit 18 (power to the trace junction box) | HTP-4 | HTP-4: heat-trace panel (gas) | HTP-4 | HTP-4: heat-trace panel (gas) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
D-P-0038 | D | Fuel gas | Heat-trace circuit 19 (power to the trace junction box) | HTP-4 | HTP-4: heat-trace panel (gas) | HTP-4 | HTP-4: heat-trace panel (gas) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
D-P-0039 | D | Fuel gas | Heat-trace circuit 20 (power to the trace junction box) | HTP-4 | HTP-4: heat-trace panel (gas) | HTP-4 | HTP-4: heat-trace panel (gas) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
D-P-0040 | D | Fuel gas | Heat-trace circuit 21 (power to the trace junction box) | HTP-4 | HTP-4: heat-trace panel (gas) | HTP-4 | HTP-4: heat-trace panel (gas) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
D-P-0041 | D | Fuel gas | Heat-trace circuit 22 (power to the trace junction box) | HTP-4 | HTP-4: heat-trace panel (gas) | HTP-4 | HTP-4: heat-trace panel (gas) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
D-P-0042 | D | Fuel gas | Heat-trace circuit 23 (power to the trace junction box) | HTP-4 | HTP-4: heat-trace panel (gas) | HTP-4 | HTP-4: heat-trace panel (gas) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
D-P-0043 | D | Fuel gas | Heat-trace circuit 24 (power to the trace junction box) | HTP-4 | HTP-4: heat-trace panel (gas) | HTP-4 | HTP-4: heat-trace panel (gas) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
D-MV-0001 | D | Fuel gas | Fuel-gas compressor (conditional) | SWGR-13.8-3 | R1 SWGR-13.8-3 (11 x 36 in cubicles, 15 kV metal-clad) |  | CONDITIONAL: fuel-gas compressors | MV 15 kV | ARMOR-X MC-HL / MV-105 15 kV 3/C Cu, EPR 133%, tape shield, gnd, CWA, red PVC | MV15AX¦3/C¦1/0 | 3/C | 1/0 | 1 | 1 | 13800 | 3000 | 139 | Duct bank | 2380 | 124
D-MV-0002 | D | Fuel gas | Fuel-gas compressor (conditional) | SWGR-13.8-3 | R1 SWGR-13.8-3 (11 x 36 in cubicles, 15 kV metal-clad) |  | CONDITIONAL: fuel-gas compressors | MV 15 kV | ARMOR-X MC-HL / MV-105 15 kV 3/C Cu, EPR 133%, tape shield, gnd, CWA, red PVC | MV15AX¦3/C¦1/0 | 3/C | 1/0 | 1 | 1 | 13800 | 3000 | 139 | Duct bank | 2380 | 124
D-MV-0003 | D | Fuel gas | Fuel-gas compressor (conditional) | SWGR-13.8-3 | R1 SWGR-13.8-3 (11 x 36 in cubicles, 15 kV metal-clad) |  | CONDITIONAL: fuel-gas compressors | MV 15 kV | ARMOR-X MC-HL / MV-105 15 kV 3/C Cu, EPR 133%, tape shield, gnd, CWA, red PVC | MV15AX¦3/C¦1/0 | 3/C | 1/0 | 1 | 1 | 13800 | 3000 | 139 | Duct bank | 2380 | 124
E-L-0001 | E | Water / utilities | Lighting, receptacles and small power branch circuits (allowance) |  | Fire pump house |  | Fire pump house | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | THHN¦1/C¦12 | 1/C | 12 | 1 | 1 | 277 |  |  | Conduit | 1920 | 0 |  |  |  |  | allowance: 1.6 ft of conductor per ft2 of floor
E-L-0002 | E | Water / utilities | Lighting, receptacles and small power branch circuits (allowance) | R-WT | Water treatment building (incl. R-WT electrical room) | R-WT | Water treatment building (incl. R-WT electrical room) | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | THHN¦1/C¦12 | 1/C | 12 | 1 | 1 | 277 |  |  | Conduit | 21760 | 0 |  |  |  |  | allowance: 1.6 ft of conductor per ft2 of floor
E-C-0001 | E | Water / utilities | Motor 1 of 2: control / local station | MCC-C2 | R1 MCC-C2 |  | Ammonia storage (aqueous, SCR reagent) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 2010 | 145
E-C-0002 | E | Water / utilities | Motor 2 of 2: control / local station | MCC-C2 | R1 MCC-C2 |  | Ammonia storage (aqueous, SCR reagent) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 2010 | 145
E-C-0003 | E | Water / utilities | Motor 1 of 3: control / local station | MCC-C2 | R1 MCC-C2 |  | Auxiliary boiler | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 2089 | 165
E-C-0004 | E | Water / utilities | Motor 2 of 3: control / local station | MCC-C2 | R1 MCC-C2 |  | Auxiliary boiler | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 2089 | 165
E-C-0005 | E | Water / utilities | Motor 3 of 3: control / local station | MCC-C2 | R1 MCC-C2 |  | Auxiliary boiler | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 2089 | 165
E-C-0006 | E | Water / utilities | Control | R-WT | Water treatment building (incl. R-WT electrical room) | CPR-2 | CPR-2: cathodic-protection rectifier | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 115 | 96
E-C-0007 | E | Water / utilities | Motor 1 of 1: control / local station | MCC-C2 | R1 MCC-C2 |  | Fire pump house | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 2004 | 209
E-C-0008 | E | Water / utilities | Motor 1 of 1: control / local station | MCC-C2 | R1 MCC-C2 |  | Fire pump house | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 2004 | 209
E-C-0009 | E | Water / utilities | Control | R-WT | Water treatment building (incl. R-WT electrical room) | HTP-2 | HTP-2: heat-trace panel (NH3) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 292 | 108
E-C-0010 | E | Water / utilities | Motor 1 of 2: control / local station | MCC-C2 | R1 MCC-C2 |  | Oil-water separator | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 2002 | 347
E-C-0011 | E | Water / utilities | Motor 2 of 2: control / local station | MCC-C2 | R1 MCC-C2 |  | Oil-water separator | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 2002 | 347
E-C-0012 | E | Water / utilities | Motor 1 of 8: control / local station | MCC-C2 | R1 MCC-C2 |  | Wastewater treatment | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1859 | 212
E-C-0013 | E | Water / utilities | Motor 2 of 8: control / local station | MCC-C2 | R1 MCC-C2 |  | Wastewater treatment | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1859 | 212
E-C-0014 | E | Water / utilities | Motor 3 of 8: control / local station | MCC-C2 | R1 MCC-C2 |  | Wastewater treatment | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1859 | 212
E-C-0015 | E | Water / utilities | Motor 4 of 8: control / local station | MCC-C2 | R1 MCC-C2 |  | Wastewater treatment | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1859 | 212
E-C-0016 | E | Water / utilities | Motor 5 of 8: control / local station | MCC-C2 | R1 MCC-C2 |  | Wastewater treatment | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1859 | 212
E-C-0017 | E | Water / utilities | Motor 6 of 8: control / local station | MCC-C2 | R1 MCC-C2 |  | Wastewater treatment | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1859 | 212
E-C-0018 | E | Water / utilities | Motor 7 of 8: control / local station | MCC-C2 | R1 MCC-C2 |  | Wastewater treatment | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1859 | 212
E-C-0019 | E | Water / utilities | Motor 8 of 8: control / local station | MCC-C2 | R1 MCC-C2 |  | Wastewater treatment | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1859 | 212
E-C-0020 | E | Water / utilities | Motor 1 of 20: control / local station | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1629 | 145
E-C-0021 | E | Water / utilities | Motor 2 of 20: control / local station | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1629 | 145
E-C-0022 | E | Water / utilities | Motor 3 of 20: control / local station | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1629 | 145
E-C-0023 | E | Water / utilities | Motor 4 of 20: control / local station | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1629 | 145
E-C-0024 | E | Water / utilities | Motor 5 of 20: control / local station | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1629 | 145
E-C-0025 | E | Water / utilities | Motor 6 of 20: control / local station | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1629 | 145
E-C-0026 | E | Water / utilities | Motor 7 of 20: control / local station | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1629 | 145
E-C-0027 | E | Water / utilities | Motor 8 of 20: control / local station | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1629 | 145
E-C-0028 | E | Water / utilities | Motor 9 of 20: control / local station | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1629 | 145
E-C-0029 | E | Water / utilities | Motor 10 of 20: control / local station | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1629 | 145
E-C-0030 | E | Water / utilities | Motor 11 of 20: control / local station | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1629 | 145
E-C-0031 | E | Water / utilities | Motor 12 of 20: control / local station | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1629 | 145
E-C-0032 | E | Water / utilities | Motor 13 of 20: control / local station | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1629 | 145
E-C-0033 | E | Water / utilities | Motor 14 of 20: control / local station | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1629 | 145
E-C-0034 | E | Water / utilities | Motor 15 of 20: control / local station | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1629 | 145
E-C-0035 | E | Water / utilities | Motor 16 of 20: control / local station | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1629 | 145
E-C-0036 | E | Water / utilities | Motor 17 of 20: control / local station | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1629 | 145
E-C-0037 | E | Water / utilities | Motor 18 of 20: control / local station | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1629 | 145
E-C-0038 | E | Water / utilities | Motor 19 of 20: control / local station | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1629 | 145
E-C-0039 | E | Water / utilities | Motor 20 of 20: control / local station | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1629 | 145
E-F-0001 | E | Water / utilities | Plant network / DCS fibre | CR | Control / admin building (main control room) | R-WT | Water treatment building (incl. R-WT electrical room) | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Duct bank | 1251 | 32
E-FA-0001 | E | Water / utilities | Fire alarm / F&G loop (to the local FACP / F&G node) | R-WT | Water treatment building (incl. R-WT electrical room) |  | Auxiliary boiler | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 370 | 52
E-FA-0002 | E | Water / utilities | Fire alarm / F&G loop (to the local FACP / F&G node) | R-WT | Water treatment building (incl. R-WT electrical room) |  | Fire pump house | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 160 | 96
E-FA-0003 | E | Water / utilities | Fire alarm / F&G loop (to the local FACP / F&G node) | R-WT | Water treatment building (incl. R-WT electrical room) | R-WT | Water treatment building (incl. R-WT electrical room) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 32
E-I-0001 | E | Water / utilities | Analog instrument to JB JB-Ammonia storage (a-AI01: 8 x 1 pr (field cables) |  | Ammonia storage (aqueous, SCR reagent) | JB-Ammonia storage (a-AI01 | Ammonia storage (aqueous, SCR reagent) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 90 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
E-I-0002 | E | Water / utilities | Home run JB-Ammonia storage (a-AI01 to the control / marshalling room | R-WT | Water treatment building (incl. R-WT electrical room) | JB-Ammonia storage (a-AI01 | Ammonia storage (aqueous, SCR reagent) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 292 | 32
E-I-0003 | E | Water / utilities | Discrete device to JB JB-Ammonia storage (a-DI01: 10 x 1 pr (field cables) |  | Ammonia storage (aqueous, SCR reagent) | JB-Ammonia storage (a-DI01 | Ammonia storage (aqueous, SCR reagent) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 90 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
E-I-0004 | E | Water / utilities | Home run JB-Ammonia storage (a-DI01 to the control / marshalling room | R-WT | Water treatment building (incl. R-WT electrical room) | JB-Ammonia storage (a-DI01 | Ammonia storage (aqueous, SCR reagent) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 292 | 32
E-I-0005 | E | Water / utilities | Analog instrument to JB JB-Auxiliary boiler-AI01: 20 x 1 pr (field cables) |  | Auxiliary boiler | JB-Auxiliary boiler-AI01 | Auxiliary boiler | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 128 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
E-I-0006 | E | Water / utilities | Home run JB-Auxiliary boiler-AI01 to the control / marshalling room | R-WT | Water treatment building (incl. R-WT electrical room) | JB-Auxiliary boiler-AI01 | Auxiliary boiler | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 370 | 52
E-I-0007 | E | Water / utilities | Analog instrument to JB JB-Auxiliary boiler-AI02: 5 x 1 pr (field cables) |  | Auxiliary boiler | JB-Auxiliary boiler-AI02 | Auxiliary boiler | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 5 | 1 |  |  |  | Tray / conduit | 128 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
E-I-0008 | E | Water / utilities | Home run JB-Auxiliary boiler-AI02 to the control / marshalling room | R-WT | Water treatment building (incl. R-WT electrical room) | JB-Auxiliary boiler-AI02 | Auxiliary boiler | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 370 | 52
E-I-0009 | E | Water / utilities | Discrete device to JB JB-Auxiliary boiler-DI01: 20 x 1 pr (field cables) |  | Auxiliary boiler | JB-Auxiliary boiler-DI01 | Auxiliary boiler | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 128 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
E-I-0010 | E | Water / utilities | Home run JB-Auxiliary boiler-DI01 to the control / marshalling room | R-WT | Water treatment building (incl. R-WT electrical room) | JB-Auxiliary boiler-DI01 | Auxiliary boiler | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 370 | 52
E-I-0011 | E | Water / utilities | Discrete device to JB JB-Auxiliary boiler-DI02: 5 x 1 pr (field cables) |  | Auxiliary boiler | JB-Auxiliary boiler-DI02 | Auxiliary boiler | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 5 | 1 |  |  |  | Tray / conduit | 128 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
E-I-0012 | E | Water / utilities | Home run JB-Auxiliary boiler-DI02 to the control / marshalling room | R-WT | Water treatment building (incl. R-WT electrical room) | JB-Auxiliary boiler-DI02 | Auxiliary boiler | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 370 | 52
E-I-0013 | E | Water / utilities | Instrumentation | R-WT | Water treatment building (incl. R-WT electrical room) | CPR-2 | CPR-2: cathodic-protection rectifier | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Duct bank | 115 | 96
E-I-0014 | E | Water / utilities | Analog instrument to JB JB-Demineralised wate-AI01: 4 x 1 pr (field cables) |  | Demineralised water tank | JB-Demineralised wate-AI01 | Demineralised water tank | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 86 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
E-I-0015 | E | Water / utilities | Home run JB-Demineralised wate-AI01 to the control / marshalling room | R-WT | Water treatment building (incl. R-WT electrical room) | JB-Demineralised wate-AI01 | Demineralised water tank | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 28 | 123
E-I-0016 | E | Water / utilities | Discrete device to JB JB-Demineralised wate-DI01: 4 x 1 pr (field cables) |  | Demineralised water tank | JB-Demineralised wate-DI01 | Demineralised water tank | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 86 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
E-I-0017 | E | Water / utilities | Home run JB-Demineralised wate-DI01 to the control / marshalling room | R-WT | Water treatment building (incl. R-WT electrical room) | JB-Demineralised wate-DI01 | Demineralised water tank | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 28 | 123
E-I-0018 | E | Water / utilities | Analog instrument to JB JB-Fire / service wat-AI01: 4 x 1 pr (field cables) |  | Fire / service water tank | JB-Fire / service wat-AI01 | Fire / service water tank | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 95 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
E-I-0019 | E | Water / utilities | Home run JB-Fire / service wat-AI01 to the control / marshalling room | R-WT | Water treatment building (incl. R-WT electrical room) | JB-Fire / service wat-AI01 | Fire / service water tank | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 0 | 100
E-I-0020 | E | Water / utilities | Discrete device to JB JB-Fire / service wat-DI01: 4 x 1 pr (field cables) |  | Fire / service water tank | JB-Fire / service wat-DI01 | Fire / service water tank | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 95 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
E-I-0021 | E | Water / utilities | Home run JB-Fire / service wat-DI01 to the control / marshalling room | R-WT | Water treatment building (incl. R-WT electrical room) | JB-Fire / service wat-DI01 | Fire / service water tank | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 0 | 100
E-I-0022 | E | Water / utilities | Analog instrument to JB JB-Fire pump house-AI01: 10 x 1 pr (field cables) |  | Fire pump house | JB-Fire pump house-AI01 | Fire pump house | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 66 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
E-I-0023 | E | Water / utilities | Home run JB-Fire pump house-AI01 to the control / marshalling room | R-WT | Water treatment building (incl. R-WT electrical room) | JB-Fire pump house-AI01 | Fire pump house | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 160 | 96
E-I-0024 | E | Water / utilities | Discrete device to JB JB-Fire pump house-DI01: 20 x 1 pr (field cables) |  | Fire pump house | JB-Fire pump house-DI01 | Fire pump house | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 66 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
E-I-0025 | E | Water / utilities | Home run JB-Fire pump house-DI01 to the control / marshalling room | R-WT | Water treatment building (incl. R-WT electrical room) | JB-Fire pump house-DI01 | Fire pump house | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 160 | 96
E-I-0026 | E | Water / utilities | Discrete device to JB JB-Fire pump house-DI02: 10 x 1 pr (field cables) |  | Fire pump house | JB-Fire pump house-DI02 | Fire pump house | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 66 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
E-I-0027 | E | Water / utilities | Home run JB-Fire pump house-DI02 to the control / marshalling room | R-WT | Water treatment building (incl. R-WT electrical room) | JB-Fire pump house-DI02 | Fire pump house | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 160 | 96
E-I-0028 | E | Water / utilities | Analog instrument to JB JB-H2 / CO2 storage (-AI01: 8 x 1 pr (field cables) |  | H2 / CO2 storage (generator gas) | JB-H2 / CO2 storage (-AI01 | H2 / CO2 storage (generator gas) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 82 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
E-I-0029 | E | Water / utilities | Home run JB-H2 / CO2 storage (-AI01 to the control / marshalling room | R-WT | Water treatment building (incl. R-WT electrical room) | JB-H2 / CO2 storage (-AI01 | H2 / CO2 storage (generator gas) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 535 | 32
E-I-0030 | E | Water / utilities | Discrete device to JB JB-H2 / CO2 storage (-DI01: 8 x 1 pr (field cables) |  | H2 / CO2 storage (generator gas) | JB-H2 / CO2 storage (-DI01 | H2 / CO2 storage (generator gas) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 82 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
E-I-0031 | E | Water / utilities | Home run JB-H2 / CO2 storage (-DI01 to the control / marshalling room | R-WT | Water treatment building (incl. R-WT electrical room) | JB-H2 / CO2 storage (-DI01 | H2 / CO2 storage (generator gas) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 535 | 32
E-I-0032 | E | Water / utilities | Analog instrument to JB JB-HTP-3-AI01: 4 x 1 pr (field cables) | HTP-3 | HTP-3: heat-trace panel (tanks) | JB-HTP-3-AI01 | HTP-3: heat-trace panel (tanks) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 40 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
E-I-0033 | E | Water / utilities | Home run JB-HTP-3-AI01 to the control / marshalling room | R-WT | Water treatment building (incl. R-WT electrical room) | JB-HTP-3-AI01 | HTP-3: heat-trace panel (tanks) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 0 | 58
E-I-0034 | E | Water / utilities | Discrete device to JB JB-HTP-3-DI01: 4 x 1 pr (field cables) | HTP-3 | HTP-3: heat-trace panel (tanks) | JB-HTP-3-DI01 | HTP-3: heat-trace panel (tanks) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 40 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
E-I-0035 | E | Water / utilities | Home run JB-HTP-3-DI01 to the control / marshalling room | R-WT | Water treatment building (incl. R-WT electrical room) | JB-HTP-3-DI01 | HTP-3: heat-trace panel (tanks) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 0 | 58
E-I-0036 | E | Water / utilities | Analog instrument to JB JB-Oil-water separato-AI01: 4 x 1 pr (field cables) |  | Oil-water separator | JB-Oil-water separato-AI01 | Oil-water separator | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
E-I-0037 | E | Water / utilities | Home run JB-Oil-water separato-AI01 to the control / marshalling room | R-WT | Water treatment building (incl. R-WT electrical room) | JB-Oil-water separato-AI01 | Oil-water separator | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 655 | 32
E-I-0038 | E | Water / utilities | Discrete device to JB JB-Oil-water separato-DI01: 4 x 1 pr (field cables) |  | Oil-water separator | JB-Oil-water separato-DI01 | Oil-water separator | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
E-I-0039 | E | Water / utilities | Home run JB-Oil-water separato-DI01 to the control / marshalling room | R-WT | Water treatment building (incl. R-WT electrical room) | JB-Oil-water separato-DI01 | Oil-water separator | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 655 | 32
E-I-0040 | E | Water / utilities | Analog instrument to JB JB-Raw water tank-AI01: 4 x 1 pr (field cables) |  | Raw water tank | JB-Raw water tank-AI01 | Raw water tank | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 86 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
E-I-0041 | E | Water / utilities | Home run JB-Raw water tank-AI01 to the control / marshalling room | R-WT | Water treatment building (incl. R-WT electrical room) | JB-Raw water tank-AI01 | Raw water tank | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 125 | 32
E-I-0042 | E | Water / utilities | Discrete device to JB JB-Raw water tank-DI01: 4 x 1 pr (field cables) |  | Raw water tank | JB-Raw water tank-DI01 | Raw water tank | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 86 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
E-I-0043 | E | Water / utilities | Home run JB-Raw water tank-DI01 to the control / marshalling room | R-WT | Water treatment building (incl. R-WT electrical room) | JB-Raw water tank-DI01 | Raw water tank | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 125 | 32
E-I-0044 | E | Water / utilities | Analog instrument to JB JB-Wastewater treatme-AI01: 20 x 1 pr (field cables) |  | Wastewater treatment | JB-Wastewater treatme-AI01 | Wastewater treatment | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 140 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
E-I-0045 | E | Water / utilities | Home run JB-Wastewater treatme-AI01 to the control / marshalling room | R-WT | Water treatment building (incl. R-WT electrical room) | JB-Wastewater treatme-AI01 | Wastewater treatment | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 15 | 99
E-I-0046 | E | Water / utilities | Discrete device to JB JB-Wastewater treatme-DI01: 20 x 1 pr (field cables) |  | Wastewater treatment | JB-Wastewater treatme-DI01 | Wastewater treatment | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 140 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
E-I-0047 | E | Water / utilities | Home run JB-Wastewater treatme-DI01 to the control / marshalling room | R-WT | Water treatment building (incl. R-WT electrical room) | JB-Wastewater treatme-DI01 | Wastewater treatment | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 15 | 99
E-I-0048 | E | Water / utilities | Discrete device to JB JB-Wastewater treatme-DI02: 10 x 1 pr (field cables) |  | Wastewater treatment | JB-Wastewater treatme-DI02 | Wastewater treatment | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 140 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
E-I-0049 | E | Water / utilities | Home run JB-Wastewater treatme-DI02 to the control / marshalling room | R-WT | Water treatment building (incl. R-WT electrical room) | JB-Wastewater treatme-DI02 | Wastewater treatment | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 15 | 99
E-I-0050 | E | Water / utilities | Analog instrument to JB JB-R-WT-AI01: 20 x 1 pr (field cables) | R-WT | Water treatment building (incl. R-WT electrical room) | JB-R-WT-AI01 | Water treatment building (incl. R-WT electrical room) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 160 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
E-I-0051 | E | Water / utilities | Home run JB-R-WT-AI01 to the control / marshalling room | R-WT | Water treatment building (incl. R-WT electrical room) | JB-R-WT-AI01 | Water treatment building (incl. R-WT electrical room) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 32
E-I-0052 | E | Water / utilities | Analog instrument to JB JB-R-WT-AI02: 20 x 1 pr (field cables) | R-WT | Water treatment building (incl. R-WT electrical room) | JB-R-WT-AI02 | Water treatment building (incl. R-WT electrical room) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 160 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
E-I-0053 | E | Water / utilities | Home run JB-R-WT-AI02 to the control / marshalling room | R-WT | Water treatment building (incl. R-WT electrical room) | JB-R-WT-AI02 | Water treatment building (incl. R-WT electrical room) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 32
E-I-0054 | E | Water / utilities | Analog instrument to JB JB-R-WT-AI03: 20 x 1 pr (field cables) | R-WT | Water treatment building (incl. R-WT electrical room) | JB-R-WT-AI03 | Water treatment building (incl. R-WT electrical room) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 160 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
E-I-0055 | E | Water / utilities | Home run JB-R-WT-AI03 to the control / marshalling room | R-WT | Water treatment building (incl. R-WT electrical room) | JB-R-WT-AI03 | Water treatment building (incl. R-WT electrical room) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 32
E-I-0056 | E | Water / utilities | Discrete device to JB JB-R-WT-DI01: 20 x 1 pr (field cables) | R-WT | Water treatment building (incl. R-WT electrical room) | JB-R-WT-DI01 | Water treatment building (incl. R-WT electrical room) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 160 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
E-I-0057 | E | Water / utilities | Home run JB-R-WT-DI01 to the control / marshalling room | R-WT | Water treatment building (incl. R-WT electrical room) | JB-R-WT-DI01 | Water treatment building (incl. R-WT electrical room) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 32
E-I-0058 | E | Water / utilities | Discrete device to JB JB-R-WT-DI02: 20 x 1 pr (field cables) | R-WT | Water treatment building (incl. R-WT electrical room) | JB-R-WT-DI02 | Water treatment building (incl. R-WT electrical room) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 160 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
E-I-0059 | E | Water / utilities | Home run JB-R-WT-DI02 to the control / marshalling room | R-WT | Water treatment building (incl. R-WT electrical room) | JB-R-WT-DI02 | Water treatment building (incl. R-WT electrical room) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 32
E-I-0060 | E | Water / utilities | Discrete device to JB JB-R-WT-DI03: 20 x 1 pr (field cables) | R-WT | Water treatment building (incl. R-WT electrical room) | JB-R-WT-DI03 | Water treatment building (incl. R-WT electrical room) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 160 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
E-I-0061 | E | Water / utilities | Home run JB-R-WT-DI03 to the control / marshalling room | R-WT | Water treatment building (incl. R-WT electrical room) | JB-R-WT-DI03 | Water treatment building (incl. R-WT electrical room) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 32
E-I-0062 | E | Water / utilities | Discrete device to JB JB-R-WT-DI04: 20 x 1 pr (field cables) | R-WT | Water treatment building (incl. R-WT electrical room) | JB-R-WT-DI04 | Water treatment building (incl. R-WT electrical room) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 160 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
E-I-0063 | E | Water / utilities | Home run JB-R-WT-DI04 to the control / marshalling room | R-WT | Water treatment building (incl. R-WT electrical room) | JB-R-WT-DI04 | Water treatment building (incl. R-WT electrical room) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 32
E-P-0001 | E | Water / utilities | Motor 1 of 2, 7 kW | MCC-C2 | R1 MCC-C2 |  | Ammonia storage (aqueous, SCR reagent) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 2010 | 145 |  |  |  |  | VD 2.6 %
E-P-0002 | E | Water / utilities | Motor 2 of 2, 7 kW | MCC-C2 | R1 MCC-C2 |  | Ammonia storage (aqueous, SCR reagent) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 2010 | 145 |  |  |  |  | VD 2.6 %
E-P-0003 | E | Water / utilities | Motor 1 of 3, 30 kW | MCC-C2 | R1 MCC-C2 |  | Auxiliary boiler | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦3/0 | 3/C+G | 3/0 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 2089 | 165 |  |  |  |  | VD 2.9 %
E-P-0004 | E | Water / utilities | Motor 2 of 3, 30 kW | MCC-C2 | R1 MCC-C2 |  | Auxiliary boiler | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦3/0 | 3/C+G | 3/0 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 2089 | 165 |  |  |  |  | VD 2.9 %
E-P-0005 | E | Water / utilities | Motor 3 of 3, 30 kW | MCC-C2 | R1 MCC-C2 |  | Auxiliary boiler | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦3/0 | 3/C+G | 3/0 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 2089 | 165 |  |  |  |  | VD 2.9 %
E-P-0006 | E | Water / utilities | Cathodic-protection rectifier supply | MCC-C2 | R1 MCC-C2 | CPR-2 | CPR-2: cathodic-protection rectifier | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 10 | 12.7 | Duct bank | 1959 | 209 |  |  |  |  | VD 2.1 %
E-P-0007 | E | Water / utilities | CP anode / structure leads (allowance) | CPR-2 | CPR-2: cathodic-protection rectifier | CPR-2 | CPR-2: cathodic-protection rectifier | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦1/C¦8 | 1/C | 8 | 1 | 1 |  |  |  | Buried | 1500 | 0 |  |  |  |  | HMWPE anode lead cable by CP vendor; allowance
E-P-0008 | E | Water / utilities | LV power feeder | MCC-C2 | R1 MCC-C2 |  | Demineralised water tank | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 10 | 14.2 | Duct bank | 1872 | 236 |  |  |  |  | VD 2.3 %
E-P-0009 | E | Water / utilities | LV power feeder | MCC-C2 | R1 MCC-C2 |  | Fire / service water tank | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 10 | 14.2 | Duct bank | 1798 | 145 |  |  |  |  | VD 2.1 %
E-P-0010 | E | Water / utilities | Motor 1 of 1, 250 kW | MCC-C2 | R1 MCC-C2 |  | Fire pump house | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦500 | 3/C+G | 500 kcmil | 3 | 1 | 480 | 250 | 353.8 | Duct bank | 2004 | 209 |  |  |  |  | VD 2.7 %
E-P-0011 | E | Water / utilities | Motor 1 of 1, 15 kW | MCC-C2 | R1 MCC-C2 |  | Fire pump house | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 2004 | 209 |  |  |  |  | VD 2.9 %
E-P-0012 | E | Water / utilities | LV power feeder | MCC-C2 | R1 MCC-C2 |  | H2 / CO2 storage (generator gas) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 2254 | 145 |  |  |  |  | VD 2.5 %
E-P-0013 | E | Water / utilities | LV power feeder | MCC-C2 | R1 MCC-C2 | HTP-2 | HTP-2: heat-trace panel (NH3) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 2 | 1 | 480 | 120 | 169.8 | Duct bank | 2010 | 220 |  |  |  |  | VD 2.8 %
E-P-0014 | E | Water / utilities | Heat-trace circuit 1 (power to the trace junction box) | HTP-2 | HTP-2: heat-trace panel (NH3) | HTP-2 | HTP-2: heat-trace panel (NH3) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0015 | E | Water / utilities | Heat-trace circuit 2 (power to the trace junction box) | HTP-2 | HTP-2: heat-trace panel (NH3) | HTP-2 | HTP-2: heat-trace panel (NH3) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0016 | E | Water / utilities | Heat-trace circuit 3 (power to the trace junction box) | HTP-2 | HTP-2: heat-trace panel (NH3) | HTP-2 | HTP-2: heat-trace panel (NH3) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0017 | E | Water / utilities | Heat-trace circuit 4 (power to the trace junction box) | HTP-2 | HTP-2: heat-trace panel (NH3) | HTP-2 | HTP-2: heat-trace panel (NH3) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0018 | E | Water / utilities | Heat-trace circuit 5 (power to the trace junction box) | HTP-2 | HTP-2: heat-trace panel (NH3) | HTP-2 | HTP-2: heat-trace panel (NH3) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0019 | E | Water / utilities | Heat-trace circuit 6 (power to the trace junction box) | HTP-2 | HTP-2: heat-trace panel (NH3) | HTP-2 | HTP-2: heat-trace panel (NH3) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0020 | E | Water / utilities | Heat-trace circuit 7 (power to the trace junction box) | HTP-2 | HTP-2: heat-trace panel (NH3) | HTP-2 | HTP-2: heat-trace panel (NH3) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0021 | E | Water / utilities | Heat-trace circuit 8 (power to the trace junction box) | HTP-2 | HTP-2: heat-trace panel (NH3) | HTP-2 | HTP-2: heat-trace panel (NH3) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0022 | E | Water / utilities | Heat-trace circuit 9 (power to the trace junction box) | HTP-2 | HTP-2: heat-trace panel (NH3) | HTP-2 | HTP-2: heat-trace panel (NH3) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0023 | E | Water / utilities | Heat-trace circuit 10 (power to the trace junction box) | HTP-2 | HTP-2: heat-trace panel (NH3) | HTP-2 | HTP-2: heat-trace panel (NH3) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0024 | E | Water / utilities | Heat-trace circuit 11 (power to the trace junction box) | HTP-2 | HTP-2: heat-trace panel (NH3) | HTP-2 | HTP-2: heat-trace panel (NH3) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0025 | E | Water / utilities | Heat-trace circuit 12 (power to the trace junction box) | HTP-2 | HTP-2: heat-trace panel (NH3) | HTP-2 | HTP-2: heat-trace panel (NH3) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0026 | E | Water / utilities | Heat-trace circuit 13 (power to the trace junction box) | HTP-2 | HTP-2: heat-trace panel (NH3) | HTP-2 | HTP-2: heat-trace panel (NH3) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0027 | E | Water / utilities | Heat-trace circuit 14 (power to the trace junction box) | HTP-2 | HTP-2: heat-trace panel (NH3) | HTP-2 | HTP-2: heat-trace panel (NH3) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0028 | E | Water / utilities | Heat-trace circuit 15 (power to the trace junction box) | HTP-2 | HTP-2: heat-trace panel (NH3) | HTP-2 | HTP-2: heat-trace panel (NH3) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0029 | E | Water / utilities | Heat-trace circuit 16 (power to the trace junction box) | HTP-2 | HTP-2: heat-trace panel (NH3) | HTP-2 | HTP-2: heat-trace panel (NH3) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0030 | E | Water / utilities | Heat-trace circuit 17 (power to the trace junction box) | HTP-2 | HTP-2: heat-trace panel (NH3) | HTP-2 | HTP-2: heat-trace panel (NH3) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0031 | E | Water / utilities | Heat-trace circuit 18 (power to the trace junction box) | HTP-2 | HTP-2: heat-trace panel (NH3) | HTP-2 | HTP-2: heat-trace panel (NH3) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0032 | E | Water / utilities | Heat-trace circuit 19 (power to the trace junction box) | HTP-2 | HTP-2: heat-trace panel (NH3) | HTP-2 | HTP-2: heat-trace panel (NH3) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0033 | E | Water / utilities | Heat-trace circuit 20 (power to the trace junction box) | HTP-2 | HTP-2: heat-trace panel (NH3) | HTP-2 | HTP-2: heat-trace panel (NH3) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0034 | E | Water / utilities | Heat-trace circuit 21 (power to the trace junction box) | HTP-2 | HTP-2: heat-trace panel (NH3) | HTP-2 | HTP-2: heat-trace panel (NH3) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0035 | E | Water / utilities | Heat-trace circuit 22 (power to the trace junction box) | HTP-2 | HTP-2: heat-trace panel (NH3) | HTP-2 | HTP-2: heat-trace panel (NH3) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0036 | E | Water / utilities | Heat-trace circuit 23 (power to the trace junction box) | HTP-2 | HTP-2: heat-trace panel (NH3) | HTP-2 | HTP-2: heat-trace panel (NH3) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0037 | E | Water / utilities | Heat-trace circuit 24 (power to the trace junction box) | HTP-2 | HTP-2: heat-trace panel (NH3) | HTP-2 | HTP-2: heat-trace panel (NH3) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0038 | E | Water / utilities | LV power feeder | MCC-C2 | R1 MCC-C2 | HTP-3 | HTP-3: heat-trace panel (tanks) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 10 | 14.2 | Duct bank | 1844 | 171 |  |  |  |  | VD 2.2 %
E-P-0039 | E | Water / utilities | Heat-trace circuit 1 (power to the trace junction box) | HTP-3 | HTP-3: heat-trace panel (tanks) | HTP-3 | HTP-3: heat-trace panel (tanks) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0040 | E | Water / utilities | Heat-trace circuit 2 (power to the trace junction box) | HTP-3 | HTP-3: heat-trace panel (tanks) | HTP-3 | HTP-3: heat-trace panel (tanks) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0041 | E | Water / utilities | Heat-trace circuit 3 (power to the trace junction box) | HTP-3 | HTP-3: heat-trace panel (tanks) | HTP-3 | HTP-3: heat-trace panel (tanks) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0042 | E | Water / utilities | Heat-trace circuit 4 (power to the trace junction box) | HTP-3 | HTP-3: heat-trace panel (tanks) | HTP-3 | HTP-3: heat-trace panel (tanks) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0043 | E | Water / utilities | Heat-trace circuit 5 (power to the trace junction box) | HTP-3 | HTP-3: heat-trace panel (tanks) | HTP-3 | HTP-3: heat-trace panel (tanks) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0044 | E | Water / utilities | Heat-trace circuit 6 (power to the trace junction box) | HTP-3 | HTP-3: heat-trace panel (tanks) | HTP-3 | HTP-3: heat-trace panel (tanks) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0045 | E | Water / utilities | Heat-trace circuit 7 (power to the trace junction box) | HTP-3 | HTP-3: heat-trace panel (tanks) | HTP-3 | HTP-3: heat-trace panel (tanks) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0046 | E | Water / utilities | Heat-trace circuit 8 (power to the trace junction box) | HTP-3 | HTP-3: heat-trace panel (tanks) | HTP-3 | HTP-3: heat-trace panel (tanks) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0047 | E | Water / utilities | Heat-trace circuit 9 (power to the trace junction box) | HTP-3 | HTP-3: heat-trace panel (tanks) | HTP-3 | HTP-3: heat-trace panel (tanks) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0048 | E | Water / utilities | Heat-trace circuit 10 (power to the trace junction box) | HTP-3 | HTP-3: heat-trace panel (tanks) | HTP-3 | HTP-3: heat-trace panel (tanks) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0049 | E | Water / utilities | Heat-trace circuit 11 (power to the trace junction box) | HTP-3 | HTP-3: heat-trace panel (tanks) | HTP-3 | HTP-3: heat-trace panel (tanks) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0050 | E | Water / utilities | Heat-trace circuit 12 (power to the trace junction box) | HTP-3 | HTP-3: heat-trace panel (tanks) | HTP-3 | HTP-3: heat-trace panel (tanks) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0051 | E | Water / utilities | Heat-trace circuit 13 (power to the trace junction box) | HTP-3 | HTP-3: heat-trace panel (tanks) | HTP-3 | HTP-3: heat-trace panel (tanks) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0052 | E | Water / utilities | Heat-trace circuit 14 (power to the trace junction box) | HTP-3 | HTP-3: heat-trace panel (tanks) | HTP-3 | HTP-3: heat-trace panel (tanks) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0053 | E | Water / utilities | Heat-trace circuit 15 (power to the trace junction box) | HTP-3 | HTP-3: heat-trace panel (tanks) | HTP-3 | HTP-3: heat-trace panel (tanks) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0054 | E | Water / utilities | Heat-trace circuit 16 (power to the trace junction box) | HTP-3 | HTP-3: heat-trace panel (tanks) | HTP-3 | HTP-3: heat-trace panel (tanks) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0055 | E | Water / utilities | Heat-trace circuit 17 (power to the trace junction box) | HTP-3 | HTP-3: heat-trace panel (tanks) | HTP-3 | HTP-3: heat-trace panel (tanks) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0056 | E | Water / utilities | Heat-trace circuit 18 (power to the trace junction box) | HTP-3 | HTP-3: heat-trace panel (tanks) | HTP-3 | HTP-3: heat-trace panel (tanks) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0057 | E | Water / utilities | Heat-trace circuit 19 (power to the trace junction box) | HTP-3 | HTP-3: heat-trace panel (tanks) | HTP-3 | HTP-3: heat-trace panel (tanks) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0058 | E | Water / utilities | Heat-trace circuit 20 (power to the trace junction box) | HTP-3 | HTP-3: heat-trace panel (tanks) | HTP-3 | HTP-3: heat-trace panel (tanks) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0059 | E | Water / utilities | Heat-trace circuit 21 (power to the trace junction box) | HTP-3 | HTP-3: heat-trace panel (tanks) | HTP-3 | HTP-3: heat-trace panel (tanks) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0060 | E | Water / utilities | Heat-trace circuit 22 (power to the trace junction box) | HTP-3 | HTP-3: heat-trace panel (tanks) | HTP-3 | HTP-3: heat-trace panel (tanks) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0061 | E | Water / utilities | Heat-trace circuit 23 (power to the trace junction box) | HTP-3 | HTP-3: heat-trace panel (tanks) | HTP-3 | HTP-3: heat-trace panel (tanks) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0062 | E | Water / utilities | Heat-trace circuit 24 (power to the trace junction box) | HTP-3 | HTP-3: heat-trace panel (tanks) | HTP-3 | HTP-3: heat-trace panel (tanks) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 4 | 6 | Tray | 180 | 20 |  |  |  |  | heat-trace cable itself by others
E-P-0063 | E | Water / utilities | Motor 1 of 2, 7 kW | MCC-C2 | R1 MCC-C2 |  | Oil-water separator | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 2002 | 347 |  |  |  |  | VD 2.8 %
E-P-0064 | E | Water / utilities | Motor 2 of 2, 7 kW | MCC-C2 | R1 MCC-C2 |  | Oil-water separator | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 2002 | 347 |  |  |  |  | VD 2.8 %
E-P-0065 | E | Water / utilities | LV power feeder | MCC-C2 | R1 MCC-C2 |  | Raw water tank | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 10 | 14.2 | Duct bank | 1754 | 145 |  |  |  |  | VD 2.1 %
E-P-0066 | E | Water / utilities | Motor 1 of 8, 15 kW | MCC-C2 | R1 MCC-C2 |  | Wastewater treatment | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1859 | 212 |  |  |  |  | VD 2.7 %
E-P-0067 | E | Water / utilities | Motor 2 of 8, 15 kW | MCC-C2 | R1 MCC-C2 |  | Wastewater treatment | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1859 | 212 |  |  |  |  | VD 2.7 %
E-P-0068 | E | Water / utilities | Motor 3 of 8, 15 kW | MCC-C2 | R1 MCC-C2 |  | Wastewater treatment | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1859 | 212 |  |  |  |  | VD 2.7 %
E-P-0069 | E | Water / utilities | Motor 4 of 8, 15 kW | MCC-C2 | R1 MCC-C2 |  | Wastewater treatment | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1859 | 212 |  |  |  |  | VD 2.7 %
E-P-0070 | E | Water / utilities | Motor 5 of 8, 15 kW | MCC-C2 | R1 MCC-C2 |  | Wastewater treatment | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1859 | 212 |  |  |  |  | VD 2.7 %
E-P-0071 | E | Water / utilities | Motor 6 of 8, 15 kW | MCC-C2 | R1 MCC-C2 |  | Wastewater treatment | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1859 | 212 |  |  |  |  | VD 2.7 %
E-P-0072 | E | Water / utilities | Motor 7 of 8, 15 kW | MCC-C2 | R1 MCC-C2 |  | Wastewater treatment | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1859 | 212 |  |  |  |  | VD 2.7 %
E-P-0073 | E | Water / utilities | Motor 8 of 8, 15 kW | MCC-C2 | R1 MCC-C2 |  | Wastewater treatment | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1859 | 212 |  |  |  |  | VD 2.7 %
E-P-0074 | E | Water / utilities | Motor 1 of 20, 15 kW | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1629 | 145 |  |  |  |  | VD 2.9 %
E-P-0075 | E | Water / utilities | Motor 2 of 20, 15 kW | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1629 | 145 |  |  |  |  | VD 2.9 %
E-P-0076 | E | Water / utilities | Motor 3 of 20, 15 kW | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1629 | 145 |  |  |  |  | VD 2.9 %
E-P-0077 | E | Water / utilities | Motor 4 of 20, 15 kW | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1629 | 145 |  |  |  |  | VD 2.9 %
E-P-0078 | E | Water / utilities | Motor 5 of 20, 15 kW | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1629 | 145 |  |  |  |  | VD 2.9 %
E-P-0079 | E | Water / utilities | Motor 6 of 20, 15 kW | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1629 | 145 |  |  |  |  | VD 2.9 %
E-P-0080 | E | Water / utilities | Motor 7 of 20, 15 kW | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1629 | 145 |  |  |  |  | VD 2.9 %
E-P-0081 | E | Water / utilities | Motor 8 of 20, 15 kW | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1629 | 145 |  |  |  |  | VD 2.9 %
E-P-0082 | E | Water / utilities | Motor 9 of 20, 15 kW | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1629 | 145 |  |  |  |  | VD 2.9 %
E-P-0083 | E | Water / utilities | Motor 10 of 20, 15 kW | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1629 | 145 |  |  |  |  | VD 2.9 %
E-P-0084 | E | Water / utilities | Motor 11 of 20, 15 kW | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1629 | 145 |  |  |  |  | VD 2.9 %
E-P-0085 | E | Water / utilities | Motor 12 of 20, 15 kW | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1629 | 145 |  |  |  |  | VD 2.9 %
E-P-0086 | E | Water / utilities | Motor 13 of 20, 15 kW | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1629 | 145 |  |  |  |  | VD 2.9 %
E-P-0087 | E | Water / utilities | Motor 14 of 20, 15 kW | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1629 | 145 |  |  |  |  | VD 2.9 %
E-P-0088 | E | Water / utilities | Motor 15 of 20, 15 kW | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1629 | 145 |  |  |  |  | VD 2.9 %
E-P-0089 | E | Water / utilities | Motor 16 of 20, 15 kW | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1629 | 145 |  |  |  |  | VD 2.9 %
E-P-0090 | E | Water / utilities | Motor 17 of 20, 15 kW | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1629 | 145 |  |  |  |  | VD 2.9 %
E-P-0091 | E | Water / utilities | Motor 18 of 20, 15 kW | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1629 | 145 |  |  |  |  | VD 2.9 %
E-P-0092 | E | Water / utilities | Motor 19 of 20, 15 kW | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1629 | 145 |  |  |  |  | VD 2.9 %
E-P-0093 | E | Water / utilities | Motor 20 of 20, 15 kW | MCC-C2 | R1 MCC-C2 | R-WT | Water treatment building (incl. R-WT electrical room) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1629 | 145 |  |  |  |  | VD 2.9 %
F-L-0001 | F | Controls / service | Lighting, receptacles and small power branch circuits (allowance) | CR | Control / admin building (main control room) | CR | Control / admin building (main control room) | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | THHN¦1/C¦12 | 1/C | 12 | 1 | 1 | 277 |  |  | Conduit | 19339 | 0 |  |  |  |  | allowance: 1.6 ft of conductor per ft2 of floor
F-L-0002 | F | Controls / service | Lighting, receptacles and small power branch circuits (allowance) |  | Gatehouse |  | Gatehouse | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | THHN¦1/C¦12 | 1/C | 12 | 1 | 1 | 277 |  |  | Conduit | 736 | 0 |  |  |  |  | allowance: 1.6 ft of conductor per ft2 of floor
F-L-0003 | F | Controls / service | Lighting, receptacles and small power branch circuits (allowance) |  | Maintenance building / workshop |  | Maintenance building / workshop | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | THHN¦1/C¦12 | 1/C | 12 | 1 | 1 | 277 |  |  | Conduit | 8003 | 0 |  |  |  |  | allowance: 1.6 ft of conductor per ft2 of floor
F-L-0004 | F | Controls / service | Lighting, receptacles and small power branch circuits (allowance) |  | Warehouse |  | Warehouse | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | THHN¦1/C¦12 | 1/C | 12 | 1 | 1 | 277 |  |  | Conduit | 27227 | 0 |  |  |  |  | allowance: 1.6 ft of conductor per ft2 of floor
F-C-0001 | F | Controls / service | Control | CR | Control / admin building (main control room) | CR | Control / admin building (main control room) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 32
F-C-0002 | F | Controls / service | Control | CR | Control / admin building (main control room) | EDG-1 | EDG-1: 3 MW emergency diesel generator (480 V) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 626 | 62
F-C-0003 | F | Controls / service | Control | CR | Control / admin building (main control room) | EDG-2 | EDG-2: 3 MW emergency diesel generator (480 V) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 661 | 65
F-C-0004 | F | Controls / service | Control | CR | Control / admin building (main control room) |  | Gatehouse | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 33 | 32
F-C-0005 | F | Controls / service | Motor 1 of 2: control / local station | MCC-C2 | R1 MCC-C2 | LS-1 | LS-1: sanitary lift station (packaged duplex) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 744 | 173
F-C-0006 | F | Controls / service | Motor 2 of 2: control / local station | MCC-C2 | R1 MCC-C2 | LS-1 | LS-1: sanitary lift station (packaged duplex) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 744 | 173
F-C-0007 | F | Controls / service | Control | RH | RH: switchyard relay / control house (52 x 70 ft) |  | Main gate: sliding gate, barrier arms, card readers, entrance sign | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 875 | 248
F-C-0008 | F | Controls / service | Control | CR | Control / admin building (main control room) |  | Maintenance building / workshop | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 356 | 32
F-C-0009 | F | Controls / service | Control | CR | Control / admin building (main control room) |  | Perimeter fence barbed-wire arms and CCTV cameras | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 2486 | 264
F-C-0010 | F | Controls / service | Motor 1 of 2: control / local station | MCC-C2 | R1 MCC-C2 |  | Stormwater pump station (2 x 100% submersible pumps) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1832 | 145
F-C-0011 | F | Controls / service | Motor 2 of 2: control / local station | MCC-C2 | R1 MCC-C2 |  | Stormwater pump station (2 x 100% submersible pumps) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1832 | 145
F-C-0012 | F | Controls / service | Control | CR | Control / admin building (main control room) |  | Warehouse | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 37 | 109
F-F-0001 | F | Controls / service | Plant network / DCS fibre | CR | Control / admin building (main control room) | CR | Control / admin building (main control room) | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Tray | 0 | 32
F-F-0002 | F | Controls / service | Plant network / DCS fibre | CR | Control / admin building (main control room) |  | Gatehouse | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Tray | 33 | 32
F-F-0003 | F | Controls / service | Plant network / DCS fibre | CR | Control / admin building (main control room) |  | Maintenance building / workshop | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Duct bank | 356 | 32
F-F-0004 | F | Controls / service | Plant network / DCS fibre | CR | Control / admin building (main control room) |  | Warehouse | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Tray | 37 | 109
F-FA-0001 | F | Controls / service | Fire alarm / F&G loop (to the local FACP / F&G node) | CR | Control / admin building (main control room) | CR | Control / admin building (main control room) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 32
F-FA-0002 | F | Controls / service | Fire alarm / F&G loop (to the local FACP / F&G node) | CR | Control / admin building (main control room) | EDG-1 | EDG-1: 3 MW emergency diesel generator (480 V) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 626 | 62
F-FA-0003 | F | Controls / service | Fire alarm / F&G loop (to the local FACP / F&G node) | CR | Control / admin building (main control room) | EDG-2 | EDG-2: 3 MW emergency diesel generator (480 V) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 661 | 65
F-FA-0004 | F | Controls / service | Fire alarm / F&G loop (to the local FACP / F&G node) | CR | Control / admin building (main control room) |  | Gatehouse | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 33 | 32
F-FA-0005 | F | Controls / service | Fire alarm / F&G loop (to the local FACP / F&G node) | CR | Control / admin building (main control room) |  | Maintenance building / workshop | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 356 | 32
F-FA-0006 | F | Controls / service | Fire alarm / F&G loop (to the local FACP / F&G node) | CR | Control / admin building (main control room) |  | Warehouse | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 37 | 109
F-I-0001 | F | Controls / service | Instrumentation | CR | Control / admin building (main control room) | EDG-1 | EDG-1: 3 MW emergency diesel generator (480 V) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Duct bank | 626 | 62
F-I-0002 | F | Controls / service | Thermocouples | CR | Control / admin building (main control room) | EDG-1 | EDG-1: 3 MW emergency diesel generator (480 V) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦12 pr¦16 | 12 pr | 16 | 1 | 1 |  |  |  | Duct bank | 626 | 62
F-I-0003 | F | Controls / service | Thermocouples | CR | Control / admin building (main control room) | EDG-1 | EDG-1: 3 MW emergency diesel generator (480 V) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦12 pr¦16 | 12 pr | 16 | 1 | 1 |  |  |  | Duct bank | 626 | 62
F-I-0004 | F | Controls / service | Instrumentation | CR | Control / admin building (main control room) | EDG-2 | EDG-2: 3 MW emergency diesel generator (480 V) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Duct bank | 661 | 65
F-I-0005 | F | Controls / service | Thermocouples | CR | Control / admin building (main control room) | EDG-2 | EDG-2: 3 MW emergency diesel generator (480 V) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦12 pr¦16 | 12 pr | 16 | 1 | 1 |  |  |  | Duct bank | 661 | 65
F-I-0006 | F | Controls / service | Thermocouples | CR | Control / admin building (main control room) | EDG-2 | EDG-2: 3 MW emergency diesel generator (480 V) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦12 pr¦16 | 12 pr | 16 | 1 | 1 |  |  |  | Duct bank | 661 | 65
F-I-0007 | F | Controls / service | Analog instrument to JB JB-LS-1-AI01: 2 x 1 pr (field cables) | LS-1 | LS-1: sanitary lift station (packaged duplex) | JB-LS-1-AI01 | LS-1: sanitary lift station (packaged duplex) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 2 | 1 |  |  |  | Tray / conduit | 40 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
F-I-0008 | F | Controls / service | Home run JB-LS-1-AI01 to the control / marshalling room | CR | Control / admin building (main control room) | JB-LS-1-AI01 | LS-1: sanitary lift station (packaged duplex) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 366 | 60
F-I-0009 | F | Controls / service | Discrete device to JB JB-LS-1-DI01: 4 x 1 pr (field cables) | LS-1 | LS-1: sanitary lift station (packaged duplex) | JB-LS-1-DI01 | LS-1: sanitary lift station (packaged duplex) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 40 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
F-I-0010 | F | Controls / service | Home run JB-LS-1-DI01 to the control / marshalling room | CR | Control / admin building (main control room) | JB-LS-1-DI01 | LS-1: sanitary lift station (packaged duplex) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 366 | 60
F-I-0011 | F | Controls / service | Analog instrument to JB JB-Stormwater pump st-AI01: 4 x 1 pr (field cables) |  | Stormwater pump station (2 x 100% submersible pumps) | JB-Stormwater pump st-AI01 | Stormwater pump station (2 x 100% submersible pumps) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
F-I-0012 | F | Controls / service | Home run JB-Stormwater pump st-AI01 to the control / marshalling room | CR | Control / admin building (main control room) | JB-Stormwater pump st-AI01 | Stormwater pump station (2 x 100% submersible pumps) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1454 | 32
F-I-0013 | F | Controls / service | Discrete device to JB JB-Stormwater pump st-DI01: 6 x 1 pr (field cables) |  | Stormwater pump station (2 x 100% submersible pumps) | JB-Stormwater pump st-DI01 | Stormwater pump station (2 x 100% submersible pumps) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
F-I-0014 | F | Controls / service | Home run JB-Stormwater pump st-DI01 to the control / marshalling room | CR | Control / admin building (main control room) | JB-Stormwater pump st-DI01 | Stormwater pump station (2 x 100% submersible pumps) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1454 | 32
F-P-0001 | F | Controls / service | LV power feeder | MCC-C2 | R1 MCC-C2 | COMMS | Comms tower (lattice) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 10 | 14.2 | Tray | 1024 | 194 |  |  |  |  | VD 2.1 %
F-P-0002 | F | Controls / service | LV panel / distribution feeder | MCC-C2 | R1 MCC-C2 | CR | Control / admin building (main control room) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦500 | 3/C+G | 500 kcmil | 1 | 1 | 480 | 145 | 205.2 | Tray | 1020 | 145 |  |  |  |  | VD 2.4 %
F-P-0003 | F | Controls / service | LV power feeder | MCC-C2 | R1 MCC-C2 | EDG-1 | EDG-1: 3 MW emergency diesel generator (480 V) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 15 | 21.2 | Tray | 875 | 219 |  |  |  |  | VD 2.8 %
F-P-0004 | F | Controls / service | LV power feeder | MCC-C2 | R1 MCC-C2 | EDG-2 | EDG-2: 3 MW emergency diesel generator (480 V) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 15 | 21.2 | Tray | 981 | 193 |  |  |  |  | VD 1.9 %
F-P-0005 | F | Controls / service | LV panel / distribution feeder | MCC-C2 | R1 MCC-C2 |  | Gatehouse | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 30 | 42.5 | Tray | 1049 | 145 |  |  |  |  | VD 2.5 %
F-P-0006 | F | Controls / service | Motor 1 of 2, 7 kW | MCC-C2 | R1 MCC-C2 | LS-1 | LS-1: sanitary lift station (packaged duplex) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 7 | 9.9 | Tray | 744 | 173 |  |  |  |  | VD 2.8 %
F-P-0007 | F | Controls / service | Motor 2 of 2, 7 kW | MCC-C2 | R1 MCC-C2 | LS-1 | LS-1: sanitary lift station (packaged duplex) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 7 | 9.9 | Tray | 744 | 173 |  |  |  |  | VD 2.8 %
F-P-0008 | F | Controls / service | LV panel / distribution feeder | MCC-C2 | R1 MCC-C2 |  | Maintenance building / workshop | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2/0 | 3/C+G | 2/0 | 1 | 1 | 480 | 60 | 84.9 | Tray | 734 | 145 |  |  |  |  | VD 2.9 %
F-P-0009 | F | Controls / service | Site / road lighting: 120 poles, buried circuits pole to pole |  | Site lighting: pole handholes and photocells |  | Site lighting: pole handholes and photocells | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 120 | 1 | 480 |  |  | Buried | 120 | 30 |  |  |  |  | ~120 ft between poles + riser
F-P-0010 | F | Controls / service | Motor 1 of 2, 75 kW | MCC-C2 | R1 MCC-C2 |  | Stormwater pump station (2 x 100% submersible pumps) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦500 | 3/C+G | 500 kcmil | 1 | 1 | 480 | 75 | 106.1 | Duct bank | 1832 | 145 |  |  |  |  | VD 2.1 %
F-P-0011 | F | Controls / service | Motor 2 of 2, 75 kW | MCC-C2 | R1 MCC-C2 |  | Stormwater pump station (2 x 100% submersible pumps) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦500 | 3/C+G | 500 kcmil | 1 | 1 | 480 | 75 | 106.1 | Duct bank | 1832 | 145 |  |  |  |  | VD 2.1 %
F-P-0012 | F | Controls / service | LV panel / distribution feeder | MCC-C2 | R1 MCC-C2 |  | Warehouse | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦500 | 3/C+G | 500 kcmil | 1 | 1 | 480 | 204 | 288.7 | Tray | 734 | 204 |  |  |  |  | VD 2.8 %
G-L-0001 | G | Carbon capture | Lighting, receptacles and small power branch circuits (allowance) |  | CCS F&G / control |  | CCS F&G / control | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | THHN¦1/C¦12 | 1/C | 12 | 1 | 1 | 277 |  |  | Conduit | 5400 | 0 |  |  |  |  | allowance: 1.6 ft of conductor per ft2 of floor
G-L-0002 | G | Carbon capture | Lighting, receptacles and small power branch circuits (allowance) |  | CCS MV switchgear building (VFDs) |  | CCS MV switchgear building (VFDs) | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | THHN¦1/C¦12 | 1/C | 12 | 1 | 1 | 277 |  |  | Conduit | 14560 | 0 |  |  |  |  | allowance: 1.6 ft of conductor per ft2 of floor
G-L-0003 | G | Carbon capture | Lighting, receptacles and small power branch circuits (allowance) |  | CT MCC / VFD e-house |  | CT MCC / VFD e-house | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | THHN¦1/C¦12 | 1/C | 12 | 1 | 1 | 277 |  |  | Conduit | 7920 | 0 |  |  |  |  | allowance: 1.6 ft of conductor per ft2 of floor
G-C-0001 | G | Carbon capture | MOV 1: control |  | CCS MV switchgear building (VFDs) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 570 | 80
G-C-0002 | G | Carbon capture | MOV 2: control |  | CCS MV switchgear building (VFDs) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 570 | 80
G-C-0003 | G | Carbon capture | MOV 3: control |  | CCS MV switchgear building (VFDs) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 570 | 80
G-C-0004 | G | Carbon capture | MOV 4: control |  | CCS MV switchgear building (VFDs) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 570 | 80
G-C-0005 | G | Carbon capture | MOV 5: control |  | CCS MV switchgear building (VFDs) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 570 | 80
G-C-0006 | G | Carbon capture | MOV 6: control |  | CCS MV switchgear building (VFDs) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 570 | 80
G-C-0007 | G | Carbon capture | MOV 7: control |  | CCS MV switchgear building (VFDs) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 570 | 80
G-C-0008 | G | Carbon capture | MOV 8: control |  | CCS MV switchgear building (VFDs) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 570 | 80
G-C-0009 | G | Carbon capture | MOV 9: control |  | CCS MV switchgear building (VFDs) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 570 | 80
G-C-0010 | G | Carbon capture | MOV 10: control |  | CCS MV switchgear building (VFDs) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 570 | 80
G-C-0011 | G | Carbon capture | Motor 1 of 2: control / local station |  | CCS MV switchgear building (VFDs) |  | Absorber A intercooler (pumps + plate exchanger) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 552 | 81
G-C-0012 | G | Carbon capture | Motor 2 of 2: control / local station |  | CCS MV switchgear building (VFDs) |  | Absorber A intercooler (pumps + plate exchanger) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 552 | 81
G-C-0013 | G | Carbon capture | MOV 1: control |  | CCS MV switchgear building (VFDs) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 410 | 80
G-C-0014 | G | Carbon capture | MOV 2: control |  | CCS MV switchgear building (VFDs) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 410 | 80
G-C-0015 | G | Carbon capture | MOV 3: control |  | CCS MV switchgear building (VFDs) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 410 | 80
G-C-0016 | G | Carbon capture | MOV 4: control |  | CCS MV switchgear building (VFDs) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 410 | 80
G-C-0017 | G | Carbon capture | MOV 5: control |  | CCS MV switchgear building (VFDs) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 410 | 80
G-C-0018 | G | Carbon capture | MOV 6: control |  | CCS MV switchgear building (VFDs) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 410 | 80
G-C-0019 | G | Carbon capture | MOV 7: control |  | CCS MV switchgear building (VFDs) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 410 | 80
G-C-0020 | G | Carbon capture | MOV 8: control |  | CCS MV switchgear building (VFDs) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 410 | 80
G-C-0021 | G | Carbon capture | MOV 9: control |  | CCS MV switchgear building (VFDs) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 410 | 80
G-C-0022 | G | Carbon capture | MOV 10: control |  | CCS MV switchgear building (VFDs) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 410 | 80
G-C-0023 | G | Carbon capture | Motor 1 of 2: control / local station |  | CCS MV switchgear building (VFDs) |  | Absorber B intercooler (pumps + plate exchanger) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 392 | 81
G-C-0024 | G | Carbon capture | Motor 2 of 2: control / local station |  | CCS MV switchgear building (VFDs) |  | Absorber B intercooler (pumps + plate exchanger) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 392 | 81
G-C-0025 | G | Carbon capture | MOV 1: control |  | CCS MV switchgear building (VFDs) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 250 | 80
G-C-0026 | G | Carbon capture | MOV 2: control |  | CCS MV switchgear building (VFDs) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 250 | 80
G-C-0027 | G | Carbon capture | MOV 3: control |  | CCS MV switchgear building (VFDs) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 250 | 80
G-C-0028 | G | Carbon capture | MOV 4: control |  | CCS MV switchgear building (VFDs) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 250 | 80
G-C-0029 | G | Carbon capture | MOV 5: control |  | CCS MV switchgear building (VFDs) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 250 | 80
G-C-0030 | G | Carbon capture | MOV 6: control |  | CCS MV switchgear building (VFDs) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 250 | 80
G-C-0031 | G | Carbon capture | MOV 7: control |  | CCS MV switchgear building (VFDs) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 250 | 80
G-C-0032 | G | Carbon capture | MOV 8: control |  | CCS MV switchgear building (VFDs) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 250 | 80
G-C-0033 | G | Carbon capture | MOV 9: control |  | CCS MV switchgear building (VFDs) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 250 | 80
G-C-0034 | G | Carbon capture | MOV 10: control |  | CCS MV switchgear building (VFDs) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 250 | 80
G-C-0035 | G | Carbon capture | Motor 1 of 2: control / local station |  | CCS MV switchgear building (VFDs) |  | Absorber C intercooler (pumps + plate exchanger) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 232 | 81
G-C-0036 | G | Carbon capture | Motor 2 of 2: control / local station |  | CCS MV switchgear building (VFDs) |  | Absorber C intercooler (pumps + plate exchanger) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 232 | 81
G-C-0037 | G | Carbon capture | Motor 1 of 4: control / local station |  | CCS MV switchgear building (VFDs) | BF-A | BF-A: booster fan (~16 MW) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 460 | 32
G-C-0038 | G | Carbon capture | Motor 2 of 4: control / local station |  | CCS MV switchgear building (VFDs) | BF-A | BF-A: booster fan (~16 MW) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 460 | 32
G-C-0039 | G | Carbon capture | Motor 3 of 4: control / local station |  | CCS MV switchgear building (VFDs) | BF-A | BF-A: booster fan (~16 MW) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 460 | 32
G-C-0040 | G | Carbon capture | Motor 4 of 4: control / local station |  | CCS MV switchgear building (VFDs) | BF-A | BF-A: booster fan (~16 MW) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 460 | 32
G-C-0041 | G | Carbon capture | Motor 1 of 4: control / local station |  | CCS MV switchgear building (VFDs) | BF-B | BF-B: booster fan (~16 MW) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 300 | 32
G-C-0042 | G | Carbon capture | Motor 2 of 4: control / local station |  | CCS MV switchgear building (VFDs) | BF-B | BF-B: booster fan (~16 MW) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 300 | 32
G-C-0043 | G | Carbon capture | Motor 3 of 4: control / local station |  | CCS MV switchgear building (VFDs) | BF-B | BF-B: booster fan (~16 MW) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 300 | 32
G-C-0044 | G | Carbon capture | Motor 4 of 4: control / local station |  | CCS MV switchgear building (VFDs) | BF-B | BF-B: booster fan (~16 MW) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 300 | 32
G-C-0045 | G | Carbon capture | Motor 1 of 4: control / local station |  | CCS MV switchgear building (VFDs) | BF-C | BF-C: booster fan (~16 MW) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 16 | 150
G-C-0046 | G | Carbon capture | Motor 2 of 4: control / local station |  | CCS MV switchgear building (VFDs) | BF-C | BF-C: booster fan (~16 MW) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 16 | 150
G-C-0047 | G | Carbon capture | Motor 3 of 4: control / local station |  | CCS MV switchgear building (VFDs) | BF-C | BF-C: booster fan (~16 MW) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 16 | 150
G-C-0048 | G | Carbon capture | Motor 4 of 4: control / local station |  | CCS MV switchgear building (VFDs) | BF-C | BF-C: booster fan (~16 MW) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 16 | 150
G-C-0049 | G | Carbon capture | Control |  | CCS F&G / control |  | CCS F&G / control | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 170
G-C-0050 | G | Carbon capture | Control |  | CCS F&G / control |  | CCS MV switchgear building (VFDs) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 206 | 101
G-C-0051 | G | Carbon capture | Motor 1 of 6: control / local station |  | CCS MV switchgear building (VFDs) | CCS T-1 | CCS T-1: 230/13.8 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 361 | 32
G-C-0052 | G | Carbon capture | Motor 2 of 6: control / local station |  | CCS MV switchgear building (VFDs) | CCS T-1 | CCS T-1: 230/13.8 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 361 | 32
G-C-0053 | G | Carbon capture | Motor 3 of 6: control / local station |  | CCS MV switchgear building (VFDs) | CCS T-1 | CCS T-1: 230/13.8 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 361 | 32
G-C-0054 | G | Carbon capture | Motor 4 of 6: control / local station |  | CCS MV switchgear building (VFDs) | CCS T-1 | CCS T-1: 230/13.8 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 361 | 32
G-C-0055 | G | Carbon capture | Motor 5 of 6: control / local station |  | CCS MV switchgear building (VFDs) | CCS T-1 | CCS T-1: 230/13.8 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 361 | 32
G-C-0056 | G | Carbon capture | Motor 6 of 6: control / local station |  | CCS MV switchgear building (VFDs) | CCS T-1 | CCS T-1: 230/13.8 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 361 | 32
G-C-0057 | G | Carbon capture | Motor 1 of 6: control / local station |  | CCS MV switchgear building (VFDs) | CCS T-2 | CCS T-2: 230/13.8 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 409 | 32
G-C-0058 | G | Carbon capture | Motor 2 of 6: control / local station |  | CCS MV switchgear building (VFDs) | CCS T-2 | CCS T-2: 230/13.8 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 409 | 32
G-C-0059 | G | Carbon capture | Motor 3 of 6: control / local station |  | CCS MV switchgear building (VFDs) | CCS T-2 | CCS T-2: 230/13.8 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 409 | 32
G-C-0060 | G | Carbon capture | Motor 4 of 6: control / local station |  | CCS MV switchgear building (VFDs) | CCS T-2 | CCS T-2: 230/13.8 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 409 | 32
G-C-0061 | G | Carbon capture | Motor 5 of 6: control / local station |  | CCS MV switchgear building (VFDs) | CCS T-2 | CCS T-2: 230/13.8 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 409 | 32
G-C-0062 | G | Carbon capture | Motor 6 of 6: control / local station |  | CCS MV switchgear building (VFDs) | CCS T-2 | CCS T-2: 230/13.8 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 409 | 32
G-C-0063 | G | Carbon capture | Motor 1 of 30: control / local station |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 42
G-C-0064 | G | Carbon capture | Motor 2 of 30: control / local station |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 42
G-C-0065 | G | Carbon capture | Motor 3 of 30: control / local station |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 42
G-C-0066 | G | Carbon capture | Motor 4 of 30: control / local station |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 42
G-C-0067 | G | Carbon capture | Motor 5 of 30: control / local station |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 42
G-C-0068 | G | Carbon capture | Motor 6 of 30: control / local station |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 42
G-C-0069 | G | Carbon capture | Motor 7 of 30: control / local station |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 42
G-C-0070 | G | Carbon capture | Motor 8 of 30: control / local station |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 42
G-C-0071 | G | Carbon capture | Motor 9 of 30: control / local station |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 42
G-C-0072 | G | Carbon capture | Motor 10 of 30: control / local station |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 42
G-C-0073 | G | Carbon capture | Motor 11 of 30: control / local station |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 42
G-C-0074 | G | Carbon capture | Motor 12 of 30: control / local station |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 42
G-C-0075 | G | Carbon capture | Motor 13 of 30: control / local station |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 42
G-C-0076 | G | Carbon capture | Motor 14 of 30: control / local station |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 42
G-C-0077 | G | Carbon capture | Motor 15 of 30: control / local station |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 42
G-C-0078 | G | Carbon capture | Motor 16 of 30: control / local station |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 42
G-C-0079 | G | Carbon capture | Motor 17 of 30: control / local station |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 42
G-C-0080 | G | Carbon capture | Motor 18 of 30: control / local station |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 42
G-C-0081 | G | Carbon capture | Motor 19 of 30: control / local station |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 42
G-C-0082 | G | Carbon capture | Motor 20 of 30: control / local station |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 42
G-C-0083 | G | Carbon capture | Motor 21 of 30: control / local station |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 42
G-C-0084 | G | Carbon capture | Motor 22 of 30: control / local station |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 42
G-C-0085 | G | Carbon capture | Motor 23 of 30: control / local station |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 42
G-C-0086 | G | Carbon capture | Motor 24 of 30: control / local station |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 42
G-C-0087 | G | Carbon capture | Motor 25 of 30: control / local station |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 42
G-C-0088 | G | Carbon capture | Motor 26 of 30: control / local station |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 42
G-C-0089 | G | Carbon capture | Motor 27 of 30: control / local station |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 42
G-C-0090 | G | Carbon capture | Motor 28 of 30: control / local station |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 42
G-C-0091 | G | Carbon capture | Motor 29 of 30: control / local station |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 42
G-C-0092 | G | Carbon capture | Motor 30 of 30: control / local station |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 42
G-C-0093 | G | Carbon capture | Motor 1 of 2: control / local station |  | CCS MV switchgear building (VFDs) |  | CCS instrument air | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 206 | 51
G-C-0094 | G | Carbon capture | Motor 2 of 2: control / local station |  | CCS MV switchgear building (VFDs) |  | CCS instrument air | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 206 | 51
G-C-0095 | G | Carbon capture | Motor 1 of 6: control / local station |  | CT MCC / VFD e-house |  | CCS wastewater (DCC + tower blowdown) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 5 | 87
G-C-0096 | G | Carbon capture | Motor 2 of 6: control / local station |  | CT MCC / VFD e-house |  | CCS wastewater (DCC + tower blowdown) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 5 | 87
G-C-0097 | G | Carbon capture | Motor 3 of 6: control / local station |  | CT MCC / VFD e-house |  | CCS wastewater (DCC + tower blowdown) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 5 | 87
G-C-0098 | G | Carbon capture | Motor 4 of 6: control / local station |  | CT MCC / VFD e-house |  | CCS wastewater (DCC + tower blowdown) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 5 | 87
G-C-0099 | G | Carbon capture | Motor 5 of 6: control / local station |  | CT MCC / VFD e-house |  | CCS wastewater (DCC + tower blowdown) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 5 | 87
G-C-0100 | G | Carbon capture | Motor 6 of 6: control / local station |  | CT MCC / VFD e-house |  | CCS wastewater (DCC + tower blowdown) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 5 | 87
G-C-0101 | G | Carbon capture | Motor 1 of 10: control / local station |  | CCS MV switchgear building (VFDs) |  | CO2 compression 3 x ~19 MW + dehydration | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 291 | 36
G-C-0102 | G | Carbon capture | Motor 2 of 10: control / local station |  | CCS MV switchgear building (VFDs) |  | CO2 compression 3 x ~19 MW + dehydration | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 291 | 36
G-C-0103 | G | Carbon capture | Motor 3 of 10: control / local station |  | CCS MV switchgear building (VFDs) |  | CO2 compression 3 x ~19 MW + dehydration | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 291 | 36
G-C-0104 | G | Carbon capture | Motor 4 of 10: control / local station |  | CCS MV switchgear building (VFDs) |  | CO2 compression 3 x ~19 MW + dehydration | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 291 | 36
G-C-0105 | G | Carbon capture | Motor 5 of 10: control / local station |  | CCS MV switchgear building (VFDs) |  | CO2 compression 3 x ~19 MW + dehydration | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 291 | 36
G-C-0106 | G | Carbon capture | Motor 6 of 10: control / local station |  | CCS MV switchgear building (VFDs) |  | CO2 compression 3 x ~19 MW + dehydration | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 291 | 36
G-C-0107 | G | Carbon capture | Motor 7 of 10: control / local station |  | CCS MV switchgear building (VFDs) |  | CO2 compression 3 x ~19 MW + dehydration | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 291 | 36
G-C-0108 | G | Carbon capture | Motor 8 of 10: control / local station |  | CCS MV switchgear building (VFDs) |  | CO2 compression 3 x ~19 MW + dehydration | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 291 | 36
G-C-0109 | G | Carbon capture | Motor 9 of 10: control / local station |  | CCS MV switchgear building (VFDs) |  | CO2 compression 3 x ~19 MW + dehydration | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 291 | 36
G-C-0110 | G | Carbon capture | Motor 10 of 10: control / local station |  | CCS MV switchgear building (VFDs) |  | CO2 compression 3 x ~19 MW + dehydration | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 291 | 36
G-C-0111 | G | Carbon capture | Motor 1 of 2: control / local station |  | CCS MV switchgear building (VFDs) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 305 | 160
G-C-0112 | G | Carbon capture | Motor 2 of 2: control / local station |  | CCS MV switchgear building (VFDs) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 305 | 160
G-C-0113 | G | Carbon capture | Motor 1 of 1: control / local station |  | CCS MV switchgear building (VFDs) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 305 | 160
G-C-0114 | G | Carbon capture | MOV 1: control |  | CCS MV switchgear building (VFDs) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 305 | 160
G-C-0115 | G | Carbon capture | MOV 2: control |  | CCS MV switchgear building (VFDs) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 305 | 160
G-C-0116 | G | Carbon capture | MOV 3: control |  | CCS MV switchgear building (VFDs) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 305 | 160
G-C-0117 | G | Carbon capture | MOV 4: control |  | CCS MV switchgear building (VFDs) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 305 | 160
G-C-0118 | G | Carbon capture | MOV 5: control |  | CCS MV switchgear building (VFDs) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 305 | 160
G-C-0119 | G | Carbon capture | MOV 6: control |  | CCS MV switchgear building (VFDs) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 305 | 160
G-C-0120 | G | Carbon capture | MOV 7: control |  | CCS MV switchgear building (VFDs) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 305 | 160
G-C-0121 | G | Carbon capture | MOV 8: control |  | CCS MV switchgear building (VFDs) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 305 | 160
G-C-0122 | G | Carbon capture | MOV 9: control |  | CCS MV switchgear building (VFDs) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 305 | 160
G-C-0123 | G | Carbon capture | MOV 10: control |  | CCS MV switchgear building (VFDs) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 305 | 160
G-C-0124 | G | Carbon capture | MOV 11: control |  | CCS MV switchgear building (VFDs) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 305 | 160
G-C-0125 | G | Carbon capture | MOV 12: control |  | CCS MV switchgear building (VFDs) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 305 | 160
G-C-0126 | G | Carbon capture | Motor 1 of 4: control / local station |  | CCS MV switchgear building (VFDs) |  | CONDITIONAL: HP export compressor + metering | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 303 | 34
G-C-0127 | G | Carbon capture | Motor 2 of 4: control / local station |  | CCS MV switchgear building (VFDs) |  | CONDITIONAL: HP export compressor + metering | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 303 | 34
G-C-0128 | G | Carbon capture | Motor 3 of 4: control / local station |  | CCS MV switchgear building (VFDs) |  | CONDITIONAL: HP export compressor + metering | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 303 | 34
G-C-0129 | G | Carbon capture | Motor 4 of 4: control / local station |  | CCS MV switchgear building (VFDs) |  | CONDITIONAL: HP export compressor + metering | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 303 | 34
G-C-0130 | G | Carbon capture | Motor 1 of 2: control / local station |  | CCS MV switchgear building (VFDs) |  | DCC-A pumps + water filter | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 515 | 164
G-C-0131 | G | Carbon capture | Motor 2 of 2: control / local station |  | CCS MV switchgear building (VFDs) |  | DCC-A pumps + water filter | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 515 | 164
G-C-0132 | G | Carbon capture | Motor 1 of 2: control / local station |  | CCS MV switchgear building (VFDs) |  | DCC-B pumps + water filter | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 415 | 122
G-C-0133 | G | Carbon capture | Motor 2 of 2: control / local station |  | CCS MV switchgear building (VFDs) |  | DCC-B pumps + water filter | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 415 | 122
G-C-0134 | G | Carbon capture | Motor 1 of 2: control / local station |  | CCS MV switchgear building (VFDs) |  | DCC-C pumps + water filter | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 195 | 164
G-C-0135 | G | Carbon capture | Motor 2 of 2: control / local station |  | CCS MV switchgear building (VFDs) |  | DCC-C pumps + water filter | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 195 | 164
G-C-0136 | G | Carbon capture | Motor 1 of 2: control / local station |  | CCS MV switchgear building (VFDs) | DMP-A | DMP-A: diverter / bypass damper | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1436 | 124
G-C-0137 | G | Carbon capture | Motor 2 of 2: control / local station |  | CCS MV switchgear building (VFDs) | DMP-A | DMP-A: diverter / bypass damper | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1436 | 124
G-C-0138 | G | Carbon capture | Motor 1 of 2: control / local station |  | CCS MV switchgear building (VFDs) | DMP-B | DMP-B: diverter / bypass damper | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1280 | 120
G-C-0139 | G | Carbon capture | Motor 2 of 2: control / local station |  | CCS MV switchgear building (VFDs) | DMP-B | DMP-B: diverter / bypass damper | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1280 | 120
G-C-0140 | G | Carbon capture | Motor 1 of 2: control / local station |  | CCS MV switchgear building (VFDs) | DMP-C | DMP-C: diverter / bypass damper | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1116 | 124
G-C-0141 | G | Carbon capture | Motor 2 of 2: control / local station |  | CCS MV switchgear building (VFDs) | DMP-C | DMP-C: diverter / bypass damper | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1116 | 124
G-C-0142 | G | Carbon capture | MOV 1: control |  | CCS MV switchgear building (VFDs) |  | RB-A: reboiler (LP steam from ST extraction) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 50 | 37
G-C-0143 | G | Carbon capture | MOV 2: control |  | CCS MV switchgear building (VFDs) |  | RB-A: reboiler (LP steam from ST extraction) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 50 | 37
G-C-0144 | G | Carbon capture | MOV 3: control |  | CCS MV switchgear building (VFDs) |  | RB-A: reboiler (LP steam from ST extraction) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 50 | 37
G-C-0145 | G | Carbon capture | MOV 4: control |  | CCS MV switchgear building (VFDs) |  | RB-A: reboiler (LP steam from ST extraction) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 50 | 37
G-C-0146 | G | Carbon capture | MOV 1: control |  | CCS MV switchgear building (VFDs) |  | RB-B: reboiler (LP steam from ST extraction) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 83 | 42
G-C-0147 | G | Carbon capture | MOV 2: control |  | CCS MV switchgear building (VFDs) |  | RB-B: reboiler (LP steam from ST extraction) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 83 | 42
G-C-0148 | G | Carbon capture | MOV 3: control |  | CCS MV switchgear building (VFDs) |  | RB-B: reboiler (LP steam from ST extraction) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 83 | 42
G-C-0149 | G | Carbon capture | MOV 4: control |  | CCS MV switchgear building (VFDs) |  | RB-B: reboiler (LP steam from ST extraction) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 83 | 42
G-C-0150 | G | Carbon capture | MOV 1: control |  | CCS MV switchgear building (VFDs) |  | RB-C: reboiler (LP steam from ST extraction) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 45 | 47
G-C-0151 | G | Carbon capture | MOV 2: control |  | CCS MV switchgear building (VFDs) |  | RB-C: reboiler (LP steam from ST extraction) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 45 | 47
G-C-0152 | G | Carbon capture | MOV 3: control |  | CCS MV switchgear building (VFDs) |  | RB-C: reboiler (LP steam from ST extraction) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 45 | 47
G-C-0153 | G | Carbon capture | MOV 4: control |  | CCS MV switchgear building (VFDs) |  | RB-C: reboiler (LP steam from ST extraction) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 45 | 47
G-C-0154 | G | Carbon capture | Motor 1 of 2: control / local station |  | CCS MV switchgear building (VFDs) |  | Reclaimer (thermal, intermittent) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 45 | 57
G-C-0155 | G | Carbon capture | Motor 2 of 2: control / local station |  | CCS MV switchgear building (VFDs) |  | Reclaimer (thermal, intermittent) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 45 | 57
G-C-0156 | G | Carbon capture | MOV 1: control |  | CCS MV switchgear building (VFDs) | STR-A | STR-A: stripper / regenerator (45 ft dia x 207 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 146 | 36
G-C-0157 | G | Carbon capture | MOV 2: control |  | CCS MV switchgear building (VFDs) | STR-A | STR-A: stripper / regenerator (45 ft dia x 207 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 146 | 36
G-C-0158 | G | Carbon capture | MOV 3: control |  | CCS MV switchgear building (VFDs) | STR-A | STR-A: stripper / regenerator (45 ft dia x 207 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 146 | 36
G-C-0159 | G | Carbon capture | MOV 4: control |  | CCS MV switchgear building (VFDs) | STR-A | STR-A: stripper / regenerator (45 ft dia x 207 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 146 | 36
G-C-0160 | G | Carbon capture | MOV 5: control |  | CCS MV switchgear building (VFDs) | STR-A | STR-A: stripper / regenerator (45 ft dia x 207 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 146 | 36
G-C-0161 | G | Carbon capture | MOV 6: control |  | CCS MV switchgear building (VFDs) | STR-A | STR-A: stripper / regenerator (45 ft dia x 207 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 146 | 36
G-C-0162 | G | Carbon capture | MOV 1: control |  | CCS MV switchgear building (VFDs) | STR-B | STR-B: stripper / regenerator (45 ft dia x 207 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 146 | 36
G-C-0163 | G | Carbon capture | MOV 2: control |  | CCS MV switchgear building (VFDs) | STR-B | STR-B: stripper / regenerator (45 ft dia x 207 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 146 | 36
G-C-0164 | G | Carbon capture | MOV 3: control |  | CCS MV switchgear building (VFDs) | STR-B | STR-B: stripper / regenerator (45 ft dia x 207 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 146 | 36
G-C-0165 | G | Carbon capture | MOV 4: control |  | CCS MV switchgear building (VFDs) | STR-B | STR-B: stripper / regenerator (45 ft dia x 207 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 146 | 36
G-C-0166 | G | Carbon capture | MOV 5: control |  | CCS MV switchgear building (VFDs) | STR-B | STR-B: stripper / regenerator (45 ft dia x 207 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 146 | 36
G-C-0167 | G | Carbon capture | MOV 6: control |  | CCS MV switchgear building (VFDs) | STR-B | STR-B: stripper / regenerator (45 ft dia x 207 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 146 | 36
G-C-0168 | G | Carbon capture | MOV 1: control |  | CCS MV switchgear building (VFDs) | STR-C | STR-C: stripper / regenerator (45 ft dia x 207 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 196 | 36
G-C-0169 | G | Carbon capture | MOV 2: control |  | CCS MV switchgear building (VFDs) | STR-C | STR-C: stripper / regenerator (45 ft dia x 207 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 196 | 36
G-C-0170 | G | Carbon capture | MOV 3: control |  | CCS MV switchgear building (VFDs) | STR-C | STR-C: stripper / regenerator (45 ft dia x 207 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 196 | 36
G-C-0171 | G | Carbon capture | MOV 4: control |  | CCS MV switchgear building (VFDs) | STR-C | STR-C: stripper / regenerator (45 ft dia x 207 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 196 | 36
G-C-0172 | G | Carbon capture | MOV 5: control |  | CCS MV switchgear building (VFDs) | STR-C | STR-C: stripper / regenerator (45 ft dia x 207 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 196 | 36
G-C-0173 | G | Carbon capture | MOV 6: control |  | CCS MV switchgear building (VFDs) | STR-C | STR-C: stripper / regenerator (45 ft dia x 207 ft) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 196 | 36
G-C-0174 | G | Carbon capture | Motor 1 of 4: control / local station |  | CCS MV switchgear building (VFDs) |  | Solvent + NaOH storage | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 250 | 37
G-C-0175 | G | Carbon capture | Motor 2 of 4: control / local station |  | CCS MV switchgear building (VFDs) |  | Solvent + NaOH storage | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 250 | 37
G-C-0176 | G | Carbon capture | Motor 3 of 4: control / local station |  | CCS MV switchgear building (VFDs) |  | Solvent + NaOH storage | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 250 | 37
G-C-0177 | G | Carbon capture | Motor 4 of 4: control / local station |  | CCS MV switchgear building (VFDs) |  | Solvent + NaOH storage | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 250 | 37
G-C-0178 | G | Carbon capture | Motor 1 of 2: control / local station |  | CCS MV switchgear building (VFDs) |  | Water-wash pumps A | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 465 | 96
G-C-0179 | G | Carbon capture | Motor 2 of 2: control / local station |  | CCS MV switchgear building (VFDs) |  | Water-wash pumps A | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 465 | 96
G-C-0180 | G | Carbon capture | Motor 1 of 2: control / local station |  | CCS MV switchgear building (VFDs) |  | Water-wash pumps B | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 305 | 96
G-C-0181 | G | Carbon capture | Motor 2 of 2: control / local station |  | CCS MV switchgear building (VFDs) |  | Water-wash pumps B | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 305 | 96
G-C-0182 | G | Carbon capture | Motor 1 of 2: control / local station |  | CCS MV switchgear building (VFDs) |  | Water-wash pumps C | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 145 | 96
G-C-0183 | G | Carbon capture | Motor 2 of 2: control / local station |  | CCS MV switchgear building (VFDs) |  | Water-wash pumps C | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 145 | 96
G-F-0001 | G | Carbon capture | Plant network / DCS fibre | CR | Control / admin building (main control room) |  | CCS F&G / control | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Tray | 2379 | 333
G-F-0002 | G | Carbon capture | Plant network / DCS fibre | CR | Control / admin building (main control room) |  | CCS MV switchgear building (VFDs) | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Duct bank | 2585 | 264
G-F-0003 | G | Carbon capture | Plant network / DCS fibre | CR | Control / admin building (main control room) |  | CT MCC / VFD e-house | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Duct bank | 3200 | 264
G-FA-0001 | G | Carbon capture | Fire alarm / F&G loop (to the local FACP / F&G node) |  | CCS F&G / control |  | CCS F&G / control | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 170
G-FA-0002 | G | Carbon capture | Fire alarm / F&G loop (to the local FACP / F&G node) |  | CCS F&G / control |  | CCS MV switchgear building (VFDs) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 206 | 101
G-FA-0003 | G | Carbon capture | Fire alarm / F&G loop (to the local FACP / F&G node) |  | CCS F&G / control |  | CT MCC / VFD e-house | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 821 | 101
G-I-0001 | G | Carbon capture | Analog instrument to JB JB-ABS-A-AI01: 20 x 1 pr (field cables) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | JB-ABS-A-AI01 | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 212 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0002 | G | Carbon capture | Home run JB-ABS-A-AI01 to the control / marshalling room |  | CCS F&G / control | JB-ABS-A-AI01 | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 939 | 149
G-I-0003 | G | Carbon capture | Analog instrument to JB JB-ABS-A-AI02: 20 x 1 pr (field cables) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | JB-ABS-A-AI02 | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 212 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0004 | G | Carbon capture | Home run JB-ABS-A-AI02 to the control / marshalling room |  | CCS F&G / control | JB-ABS-A-AI02 | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 939 | 149
G-I-0005 | G | Carbon capture | Analog instrument to JB JB-ABS-A-AI03: 20 x 1 pr (field cables) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | JB-ABS-A-AI03 | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 212 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0006 | G | Carbon capture | Home run JB-ABS-A-AI03 to the control / marshalling room |  | CCS F&G / control | JB-ABS-A-AI03 | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 939 | 149
G-I-0007 | G | Carbon capture | Discrete device to JB JB-ABS-A-DI01: 20 x 1 pr (field cables) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | JB-ABS-A-DI01 | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 212 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0008 | G | Carbon capture | Home run JB-ABS-A-DI01 to the control / marshalling room |  | CCS F&G / control | JB-ABS-A-DI01 | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 939 | 149
G-I-0009 | G | Carbon capture | Discrete device to JB JB-ABS-A-DI02: 20 x 1 pr (field cables) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | JB-ABS-A-DI02 | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 212 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0010 | G | Carbon capture | Home run JB-ABS-A-DI02 to the control / marshalling room |  | CCS F&G / control | JB-ABS-A-DI02 | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 939 | 149
G-I-0011 | G | Carbon capture | Analog instrument to JB JB-Absorber A interco-AI01: 15 x 1 pr (field cables) |  | Absorber A intercooler (pumps + plate exchanger) | JB-Absorber A interco-AI01 | Absorber A intercooler (pumps + plate exchanger) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 15 | 1 |  |  |  | Tray / conduit | 55 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0012 | G | Carbon capture | Home run JB-Absorber A interco-AI01 to the control / marshalling room |  | CCS F&G / control | JB-Absorber A interco-AI01 | Absorber A intercooler (pumps + plate exchanger) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 921 | 150
G-I-0013 | G | Carbon capture | Discrete device to JB JB-Absorber A interco-DI01: 15 x 1 pr (field cables) |  | Absorber A intercooler (pumps + plate exchanger) | JB-Absorber A interco-DI01 | Absorber A intercooler (pumps + plate exchanger) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 15 | 1 |  |  |  | Tray / conduit | 55 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0014 | G | Carbon capture | Home run JB-Absorber A interco-DI01 to the control / marshalling room |  | CCS F&G / control | JB-Absorber A interco-DI01 | Absorber A intercooler (pumps + plate exchanger) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 921 | 150
G-I-0015 | G | Carbon capture | Analog instrument to JB JB-ABS-B-AI01: 20 x 1 pr (field cables) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | JB-ABS-B-AI01 | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 212 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0016 | G | Carbon capture | Home run JB-ABS-B-AI01 to the control / marshalling room |  | CCS F&G / control | JB-ABS-B-AI01 | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 779 | 149
G-I-0017 | G | Carbon capture | Analog instrument to JB JB-ABS-B-AI02: 20 x 1 pr (field cables) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | JB-ABS-B-AI02 | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 212 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0018 | G | Carbon capture | Home run JB-ABS-B-AI02 to the control / marshalling room |  | CCS F&G / control | JB-ABS-B-AI02 | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 779 | 149
G-I-0019 | G | Carbon capture | Analog instrument to JB JB-ABS-B-AI03: 20 x 1 pr (field cables) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | JB-ABS-B-AI03 | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 212 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0020 | G | Carbon capture | Home run JB-ABS-B-AI03 to the control / marshalling room |  | CCS F&G / control | JB-ABS-B-AI03 | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 779 | 149
G-I-0021 | G | Carbon capture | Discrete device to JB JB-ABS-B-DI01: 20 x 1 pr (field cables) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | JB-ABS-B-DI01 | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 212 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0022 | G | Carbon capture | Home run JB-ABS-B-DI01 to the control / marshalling room |  | CCS F&G / control | JB-ABS-B-DI01 | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 779 | 149
G-I-0023 | G | Carbon capture | Discrete device to JB JB-ABS-B-DI02: 20 x 1 pr (field cables) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | JB-ABS-B-DI02 | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 212 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0024 | G | Carbon capture | Home run JB-ABS-B-DI02 to the control / marshalling room |  | CCS F&G / control | JB-ABS-B-DI02 | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 779 | 149
G-I-0025 | G | Carbon capture | Analog instrument to JB JB-Absorber B interco-AI01: 15 x 1 pr (field cables) |  | Absorber B intercooler (pumps + plate exchanger) | JB-Absorber B interco-AI01 | Absorber B intercooler (pumps + plate exchanger) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 15 | 1 |  |  |  | Tray / conduit | 55 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0026 | G | Carbon capture | Home run JB-Absorber B interco-AI01 to the control / marshalling room |  | CCS F&G / control | JB-Absorber B interco-AI01 | Absorber B intercooler (pumps + plate exchanger) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 761 | 150
G-I-0027 | G | Carbon capture | Discrete device to JB JB-Absorber B interco-DI01: 15 x 1 pr (field cables) |  | Absorber B intercooler (pumps + plate exchanger) | JB-Absorber B interco-DI01 | Absorber B intercooler (pumps + plate exchanger) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 15 | 1 |  |  |  | Tray / conduit | 55 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0028 | G | Carbon capture | Home run JB-Absorber B interco-DI01 to the control / marshalling room |  | CCS F&G / control | JB-Absorber B interco-DI01 | Absorber B intercooler (pumps + plate exchanger) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 761 | 150
G-I-0029 | G | Carbon capture | Analog instrument to JB JB-ABS-C-AI01: 20 x 1 pr (field cables) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | JB-ABS-C-AI01 | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 212 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0030 | G | Carbon capture | Home run JB-ABS-C-AI01 to the control / marshalling room |  | CCS F&G / control | JB-ABS-C-AI01 | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 619 | 149
G-I-0031 | G | Carbon capture | Analog instrument to JB JB-ABS-C-AI02: 20 x 1 pr (field cables) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | JB-ABS-C-AI02 | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 212 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0032 | G | Carbon capture | Home run JB-ABS-C-AI02 to the control / marshalling room |  | CCS F&G / control | JB-ABS-C-AI02 | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 619 | 149
G-I-0033 | G | Carbon capture | Analog instrument to JB JB-ABS-C-AI03: 20 x 1 pr (field cables) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | JB-ABS-C-AI03 | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 212 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0034 | G | Carbon capture | Home run JB-ABS-C-AI03 to the control / marshalling room |  | CCS F&G / control | JB-ABS-C-AI03 | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 619 | 149
G-I-0035 | G | Carbon capture | Discrete device to JB JB-ABS-C-DI01: 20 x 1 pr (field cables) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | JB-ABS-C-DI01 | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 212 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0036 | G | Carbon capture | Home run JB-ABS-C-DI01 to the control / marshalling room |  | CCS F&G / control | JB-ABS-C-DI01 | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 619 | 149
G-I-0037 | G | Carbon capture | Discrete device to JB JB-ABS-C-DI02: 20 x 1 pr (field cables) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | JB-ABS-C-DI02 | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 212 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0038 | G | Carbon capture | Home run JB-ABS-C-DI02 to the control / marshalling room |  | CCS F&G / control | JB-ABS-C-DI02 | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 619 | 149
G-I-0039 | G | Carbon capture | Analog instrument to JB JB-Absorber C interco-AI01: 15 x 1 pr (field cables) |  | Absorber C intercooler (pumps + plate exchanger) | JB-Absorber C interco-AI01 | Absorber C intercooler (pumps + plate exchanger) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 15 | 1 |  |  |  | Tray / conduit | 55 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0040 | G | Carbon capture | Home run JB-Absorber C interco-AI01 to the control / marshalling room |  | CCS F&G / control | JB-Absorber C interco-AI01 | Absorber C intercooler (pumps + plate exchanger) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 601 | 150
G-I-0041 | G | Carbon capture | Discrete device to JB JB-Absorber C interco-DI01: 15 x 1 pr (field cables) |  | Absorber C intercooler (pumps + plate exchanger) | JB-Absorber C interco-DI01 | Absorber C intercooler (pumps + plate exchanger) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 15 | 1 |  |  |  | Tray / conduit | 55 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0042 | G | Carbon capture | Home run JB-Absorber C interco-DI01 to the control / marshalling room |  | CCS F&G / control | JB-Absorber C interco-DI01 | Absorber C intercooler (pumps + plate exchanger) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 601 | 150
G-I-0043 | G | Carbon capture | Analog instrument to JB JB-Activated-carbon f-AI01: 6 x 1 pr (field cables) |  | Activated-carbon filter | JB-Activated-carbon f-AI01 | Activated-carbon filter | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 91 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0044 | G | Carbon capture | Home run JB-Activated-carbon f-AI01 to the control / marshalling room |  | CCS F&G / control | JB-Activated-carbon f-AI01 | Activated-carbon filter | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 185 | 112
G-I-0045 | G | Carbon capture | Discrete device to JB JB-Activated-carbon f-DI01: 6 x 1 pr (field cables) |  | Activated-carbon filter | JB-Activated-carbon f-DI01 | Activated-carbon filter | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 91 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0046 | G | Carbon capture | Home run JB-Activated-carbon f-DI01 to the control / marshalling room |  | CCS F&G / control | JB-Activated-carbon f-DI01 | Activated-carbon filter | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 185 | 112
G-I-0047 | G | Carbon capture | Analog instrument to JB JB-BF-A-AI01: 20 x 1 pr (field cables) | BF-A | BF-A: booster fan (~16 MW) | JB-BF-A-AI01 | BF-A: booster fan (~16 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 82 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0048 | G | Carbon capture | Home run JB-BF-A-AI01 to the control / marshalling room |  | CCS F&G / control | JB-BF-A-AI01 | BF-A: booster fan (~16 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 861 | 101
G-I-0049 | G | Carbon capture | Analog instrument to JB JB-BF-A-AI02: 10 x 1 pr (field cables) | BF-A | BF-A: booster fan (~16 MW) | JB-BF-A-AI02 | BF-A: booster fan (~16 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 82 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0050 | G | Carbon capture | Home run JB-BF-A-AI02 to the control / marshalling room |  | CCS F&G / control | JB-BF-A-AI02 | BF-A: booster fan (~16 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 861 | 101
G-I-0051 | G | Carbon capture | Discrete device to JB JB-BF-A-DI01: 20 x 1 pr (field cables) | BF-A | BF-A: booster fan (~16 MW) | JB-BF-A-DI01 | BF-A: booster fan (~16 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 82 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0052 | G | Carbon capture | Home run JB-BF-A-DI01 to the control / marshalling room |  | CCS F&G / control | JB-BF-A-DI01 | BF-A: booster fan (~16 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 861 | 101
G-I-0053 | G | Carbon capture | RTD to JB JB-BF-A-RTD01: 10 x 1 tri (field cables) | BF-A | BF-A: booster fan (~16 MW) | JB-BF-A-RTD01 | BF-A: booster fan (~16 MW) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 82 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0054 | G | Carbon capture | Home run JB-BF-A-RTD01 to the control / marshalling room |  | CCS F&G / control | JB-BF-A-RTD01 | BF-A: booster fan (~16 MW) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 861 | 101
G-I-0055 | G | Carbon capture | RTD to JB JB-BF-A-RTD02: 8 x 1 tri (field cables) | BF-A | BF-A: booster fan (~16 MW) | JB-BF-A-RTD02 | BF-A: booster fan (~16 MW) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 8 | 1 |  |  |  | Tray / conduit | 82 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0056 | G | Carbon capture | Home run JB-BF-A-RTD02 to the control / marshalling room |  | CCS F&G / control | JB-BF-A-RTD02 | BF-A: booster fan (~16 MW) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 861 | 101
G-I-0057 | G | Carbon capture | Analog instrument to JB JB-BF-B-AI01: 20 x 1 pr (field cables) | BF-B | BF-B: booster fan (~16 MW) | JB-BF-B-AI01 | BF-B: booster fan (~16 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 82 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0058 | G | Carbon capture | Home run JB-BF-B-AI01 to the control / marshalling room |  | CCS F&G / control | JB-BF-B-AI01 | BF-B: booster fan (~16 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 701 | 101
G-I-0059 | G | Carbon capture | Analog instrument to JB JB-BF-B-AI02: 10 x 1 pr (field cables) | BF-B | BF-B: booster fan (~16 MW) | JB-BF-B-AI02 | BF-B: booster fan (~16 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 82 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0060 | G | Carbon capture | Home run JB-BF-B-AI02 to the control / marshalling room |  | CCS F&G / control | JB-BF-B-AI02 | BF-B: booster fan (~16 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 701 | 101
G-I-0061 | G | Carbon capture | Discrete device to JB JB-BF-B-DI01: 20 x 1 pr (field cables) | BF-B | BF-B: booster fan (~16 MW) | JB-BF-B-DI01 | BF-B: booster fan (~16 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 82 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0062 | G | Carbon capture | Home run JB-BF-B-DI01 to the control / marshalling room |  | CCS F&G / control | JB-BF-B-DI01 | BF-B: booster fan (~16 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 701 | 101
G-I-0063 | G | Carbon capture | RTD to JB JB-BF-B-RTD01: 10 x 1 tri (field cables) | BF-B | BF-B: booster fan (~16 MW) | JB-BF-B-RTD01 | BF-B: booster fan (~16 MW) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 82 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0064 | G | Carbon capture | Home run JB-BF-B-RTD01 to the control / marshalling room |  | CCS F&G / control | JB-BF-B-RTD01 | BF-B: booster fan (~16 MW) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 701 | 101
G-I-0065 | G | Carbon capture | RTD to JB JB-BF-B-RTD02: 8 x 1 tri (field cables) | BF-B | BF-B: booster fan (~16 MW) | JB-BF-B-RTD02 | BF-B: booster fan (~16 MW) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 8 | 1 |  |  |  | Tray / conduit | 82 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0066 | G | Carbon capture | Home run JB-BF-B-RTD02 to the control / marshalling room |  | CCS F&G / control | JB-BF-B-RTD02 | BF-B: booster fan (~16 MW) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 701 | 101
G-I-0067 | G | Carbon capture | Analog instrument to JB JB-BF-C-AI01: 20 x 1 pr (field cables) | BF-C | BF-C: booster fan (~16 MW) | JB-BF-C-AI01 | BF-C: booster fan (~16 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 82 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0068 | G | Carbon capture | Home run JB-BF-C-AI01 to the control / marshalling room |  | CCS F&G / control | JB-BF-C-AI01 | BF-C: booster fan (~16 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 385 | 219
G-I-0069 | G | Carbon capture | Analog instrument to JB JB-BF-C-AI02: 10 x 1 pr (field cables) | BF-C | BF-C: booster fan (~16 MW) | JB-BF-C-AI02 | BF-C: booster fan (~16 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 82 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0070 | G | Carbon capture | Home run JB-BF-C-AI02 to the control / marshalling room |  | CCS F&G / control | JB-BF-C-AI02 | BF-C: booster fan (~16 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 385 | 219
G-I-0071 | G | Carbon capture | Discrete device to JB JB-BF-C-DI01: 20 x 1 pr (field cables) | BF-C | BF-C: booster fan (~16 MW) | JB-BF-C-DI01 | BF-C: booster fan (~16 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 82 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0072 | G | Carbon capture | Home run JB-BF-C-DI01 to the control / marshalling room |  | CCS F&G / control | JB-BF-C-DI01 | BF-C: booster fan (~16 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 385 | 219
G-I-0073 | G | Carbon capture | RTD to JB JB-BF-C-RTD01: 10 x 1 tri (field cables) | BF-C | BF-C: booster fan (~16 MW) | JB-BF-C-RTD01 | BF-C: booster fan (~16 MW) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 82 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0074 | G | Carbon capture | Home run JB-BF-C-RTD01 to the control / marshalling room |  | CCS F&G / control | JB-BF-C-RTD01 | BF-C: booster fan (~16 MW) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 385 | 219
G-I-0075 | G | Carbon capture | RTD to JB JB-BF-C-RTD02: 8 x 1 tri (field cables) | BF-C | BF-C: booster fan (~16 MW) | JB-BF-C-RTD02 | BF-C: booster fan (~16 MW) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 8 | 1 |  |  |  | Tray / conduit | 82 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0076 | G | Carbon capture | Home run JB-BF-C-RTD02 to the control / marshalling room |  | CCS F&G / control | JB-BF-C-RTD02 | BF-C: booster fan (~16 MW) | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 385 | 219
G-I-0077 | G | Carbon capture | Analog instrument to JB JB-CCS T-1-AI01: 8 x 1 pr (field cables) | CCS T-1 | CCS T-1: 230/13.8 kV | JB-CCS T-1-AI01 | CCS T-1: 230/13.8 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 82 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0078 | G | Carbon capture | Home run JB-CCS T-1-AI01 to the control / marshalling room |  | CCS F&G / control | JB-CCS T-1-AI01 | CCS T-1: 230/13.8 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | HV duct bank | 77 | 103
G-I-0079 | G | Carbon capture | Discrete device to JB JB-CCS T-1-DI01: 16 x 1 pr (field cables) | CCS T-1 | CCS T-1: 230/13.8 kV | JB-CCS T-1-DI01 | CCS T-1: 230/13.8 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 82 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0080 | G | Carbon capture | Home run JB-CCS T-1-DI01 to the control / marshalling room |  | CCS F&G / control | JB-CCS T-1-DI01 | CCS T-1: 230/13.8 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | HV duct bank | 77 | 103
G-I-0081 | G | Carbon capture | Analog instrument to JB JB-CCS T-2-AI01: 8 x 1 pr (field cables) | CCS T-2 | CCS T-2: 230/13.8 kV | JB-CCS T-2-AI01 | CCS T-2: 230/13.8 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 82 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0082 | G | Carbon capture | Home run JB-CCS T-2-AI01 to the control / marshalling room |  | CCS F&G / control | JB-CCS T-2-AI01 | CCS T-2: 230/13.8 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 11 | 101
G-I-0083 | G | Carbon capture | Discrete device to JB JB-CCS T-2-DI01: 16 x 1 pr (field cables) | CCS T-2 | CCS T-2: 230/13.8 kV | JB-CCS T-2-DI01 | CCS T-2: 230/13.8 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 82 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0084 | G | Carbon capture | Home run JB-CCS T-2-DI01 to the control / marshalling room |  | CCS F&G / control | JB-CCS T-2-DI01 | CCS T-2: 230/13.8 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 11 | 101
G-I-0085 | G | Carbon capture | Analog instrument to JB JB-CCS circulating-wa-AI01: 20 x 1 pr (field cables) |  | CCS circulating-water pumps | JB-CCS circulating-wa-AI01 | CCS circulating-water pumps | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 100 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0086 | G | Carbon capture | Home run JB-CCS circulating-wa-AI01 to the control / marshalling room |  | CCS F&G / control | JB-CCS circulating-wa-AI01 | CCS circulating-water pumps | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 821 | 141
G-I-0087 | G | Carbon capture | Discrete device to JB JB-CCS circulating-wa-DI01: 20 x 1 pr (field cables) |  | CCS circulating-water pumps | JB-CCS circulating-wa-DI01 | CCS circulating-water pumps | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 100 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0088 | G | Carbon capture | Home run JB-CCS circulating-wa-DI01 to the control / marshalling room |  | CCS F&G / control | JB-CCS circulating-wa-DI01 | CCS circulating-water pumps | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 821 | 141
G-I-0089 | G | Carbon capture | Analog instrument to JB JB-CCS-CT-AI01: 20 x 1 pr (field cables) | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | JB-CCS-CT-AI01 | CCS cooling tower (~30 cells): CCS process cooling only | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 250 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0090 | G | Carbon capture | Home run JB-CCS-CT-AI01 to the control / marshalling room |  | CCS F&G / control | JB-CCS-CT-AI01 | CCS cooling tower (~30 cells): CCS process cooling only | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 911 | 111
G-I-0091 | G | Carbon capture | Analog instrument to JB JB-CCS-CT-AI02: 10 x 1 pr (field cables) | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | JB-CCS-CT-AI02 | CCS cooling tower (~30 cells): CCS process cooling only | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 250 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0092 | G | Carbon capture | Home run JB-CCS-CT-AI02 to the control / marshalling room |  | CCS F&G / control | JB-CCS-CT-AI02 | CCS cooling tower (~30 cells): CCS process cooling only | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 911 | 111
G-I-0093 | G | Carbon capture | Discrete device to JB JB-CCS-CT-DI01: 20 x 1 pr (field cables) | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | JB-CCS-CT-DI01 | CCS cooling tower (~30 cells): CCS process cooling only | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 250 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0094 | G | Carbon capture | Home run JB-CCS-CT-DI01 to the control / marshalling room |  | CCS F&G / control | JB-CCS-CT-DI01 | CCS cooling tower (~30 cells): CCS process cooling only | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 911 | 111
G-I-0095 | G | Carbon capture | Discrete device to JB JB-CCS-CT-DI02: 20 x 1 pr (field cables) | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | JB-CCS-CT-DI02 | CCS cooling tower (~30 cells): CCS process cooling only | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 250 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0096 | G | Carbon capture | Home run JB-CCS-CT-DI02 to the control / marshalling room |  | CCS F&G / control | JB-CCS-CT-DI02 | CCS cooling tower (~30 cells): CCS process cooling only | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 911 | 111
G-I-0097 | G | Carbon capture | Discrete device to JB JB-CCS-CT-DI03: 20 x 1 pr (field cables) | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | JB-CCS-CT-DI03 | CCS cooling tower (~30 cells): CCS process cooling only | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 250 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0098 | G | Carbon capture | Home run JB-CCS-CT-DI03 to the control / marshalling room |  | CCS F&G / control | JB-CCS-CT-DI03 | CCS cooling tower (~30 cells): CCS process cooling only | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 911 | 111
G-I-0099 | G | Carbon capture | Analog instrument to JB JB-CCS instrument air-AI01: 10 x 1 pr (field cables) |  | CCS instrument air | JB-CCS instrument air-AI01 | CCS instrument air | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0100 | G | Carbon capture | Home run JB-CCS instrument air-AI01 to the control / marshalling room |  | CCS F&G / control | JB-CCS instrument air-AI01 | CCS instrument air | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 120
G-I-0101 | G | Carbon capture | Discrete device to JB JB-CCS instrument air-DI01: 10 x 1 pr (field cables) |  | CCS instrument air | JB-CCS instrument air-DI01 | CCS instrument air | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0102 | G | Carbon capture | Home run JB-CCS instrument air-DI01 to the control / marshalling room |  | CCS F&G / control | JB-CCS instrument air-DI01 | CCS instrument air | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 120
G-I-0103 | G | Carbon capture | Analog instrument to JB JB-CCS wastewater (DC-AI01: 15 x 1 pr (field cables) |  | CCS wastewater (DCC + tower blowdown) | JB-CCS wastewater (DC-AI01 | CCS wastewater (DCC + tower blowdown) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 15 | 1 |  |  |  | Tray / conduit | 140 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0104 | G | Carbon capture | Home run JB-CCS wastewater (DC-AI01 to the control / marshalling room |  | CCS F&G / control | JB-CCS wastewater (DC-AI01 | CCS wastewater (DCC + tower blowdown) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 656 | 121
G-I-0105 | G | Carbon capture | Discrete device to JB JB-CCS wastewater (DC-DI01: 15 x 1 pr (field cables) |  | CCS wastewater (DCC + tower blowdown) | JB-CCS wastewater (DC-DI01 | CCS wastewater (DCC + tower blowdown) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 15 | 1 |  |  |  | Tray / conduit | 140 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0106 | G | Carbon capture | Home run JB-CCS wastewater (DC-DI01 to the control / marshalling room |  | CCS F&G / control | JB-CCS wastewater (DC-DI01 | CCS wastewater (DCC + tower blowdown) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 656 | 121
G-I-0107 | G | Carbon capture | Analog instrument to JB JB-CO2 compression 3 -AI01: 20 x 1 pr (field cables) |  | CO2 compression 3 x ~19 MW + dehydration | JB-CO2 compression 3 -AI01 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 159 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0108 | G | Carbon capture | Home run JB-CO2 compression 3 -AI01 to the control / marshalling room |  | CCS F&G / control | JB-CO2 compression 3 -AI01 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 183 | 105
G-I-0109 | G | Carbon capture | Analog instrument to JB JB-CO2 compression 3 -AI02: 20 x 1 pr (field cables) |  | CO2 compression 3 x ~19 MW + dehydration | JB-CO2 compression 3 -AI02 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 159 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0110 | G | Carbon capture | Home run JB-CO2 compression 3 -AI02 to the control / marshalling room |  | CCS F&G / control | JB-CO2 compression 3 -AI02 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 183 | 105
G-I-0111 | G | Carbon capture | Analog instrument to JB JB-CO2 compression 3 -AI03: 20 x 1 pr (field cables) |  | CO2 compression 3 x ~19 MW + dehydration | JB-CO2 compression 3 -AI03 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 159 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0112 | G | Carbon capture | Home run JB-CO2 compression 3 -AI03 to the control / marshalling room |  | CCS F&G / control | JB-CO2 compression 3 -AI03 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 183 | 105
G-I-0113 | G | Carbon capture | Analog instrument to JB JB-CO2 compression 3 -AI04: 20 x 1 pr (field cables) |  | CO2 compression 3 x ~19 MW + dehydration | JB-CO2 compression 3 -AI04 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 159 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0114 | G | Carbon capture | Home run JB-CO2 compression 3 -AI04 to the control / marshalling room |  | CCS F&G / control | JB-CO2 compression 3 -AI04 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 183 | 105
G-I-0115 | G | Carbon capture | Analog instrument to JB JB-CO2 compression 3 -AI05: 20 x 1 pr (field cables) |  | CO2 compression 3 x ~19 MW + dehydration | JB-CO2 compression 3 -AI05 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 159 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0116 | G | Carbon capture | Home run JB-CO2 compression 3 -AI05 to the control / marshalling room |  | CCS F&G / control | JB-CO2 compression 3 -AI05 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 183 | 105
G-I-0117 | G | Carbon capture | Analog instrument to JB JB-CO2 compression 3 -AI06: 20 x 1 pr (field cables) |  | CO2 compression 3 x ~19 MW + dehydration | JB-CO2 compression 3 -AI06 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 159 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0118 | G | Carbon capture | Home run JB-CO2 compression 3 -AI06 to the control / marshalling room |  | CCS F&G / control | JB-CO2 compression 3 -AI06 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 183 | 105
G-I-0119 | G | Carbon capture | Analog instrument to JB JB-CO2 compression 3 -AI07: 20 x 1 pr (field cables) |  | CO2 compression 3 x ~19 MW + dehydration | JB-CO2 compression 3 -AI07 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 159 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0120 | G | Carbon capture | Home run JB-CO2 compression 3 -AI07 to the control / marshalling room |  | CCS F&G / control | JB-CO2 compression 3 -AI07 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 183 | 105
G-I-0121 | G | Carbon capture | Analog instrument to JB JB-CO2 compression 3 -AI08: 10 x 1 pr (field cables) |  | CO2 compression 3 x ~19 MW + dehydration | JB-CO2 compression 3 -AI08 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 159 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0122 | G | Carbon capture | Home run JB-CO2 compression 3 -AI08 to the control / marshalling room |  | CCS F&G / control | JB-CO2 compression 3 -AI08 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 183 | 105
G-I-0123 | G | Carbon capture | Discrete device to JB JB-CO2 compression 3 -DI01: 20 x 1 pr (field cables) |  | CO2 compression 3 x ~19 MW + dehydration | JB-CO2 compression 3 -DI01 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 159 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0124 | G | Carbon capture | Home run JB-CO2 compression 3 -DI01 to the control / marshalling room |  | CCS F&G / control | JB-CO2 compression 3 -DI01 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 183 | 105
G-I-0125 | G | Carbon capture | Discrete device to JB JB-CO2 compression 3 -DI02: 20 x 1 pr (field cables) |  | CO2 compression 3 x ~19 MW + dehydration | JB-CO2 compression 3 -DI02 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 159 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0126 | G | Carbon capture | Home run JB-CO2 compression 3 -DI02 to the control / marshalling room |  | CCS F&G / control | JB-CO2 compression 3 -DI02 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 183 | 105
G-I-0127 | G | Carbon capture | Discrete device to JB JB-CO2 compression 3 -DI03: 20 x 1 pr (field cables) |  | CO2 compression 3 x ~19 MW + dehydration | JB-CO2 compression 3 -DI03 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 159 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0128 | G | Carbon capture | Home run JB-CO2 compression 3 -DI03 to the control / marshalling room |  | CCS F&G / control | JB-CO2 compression 3 -DI03 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 183 | 105
G-I-0129 | G | Carbon capture | Discrete device to JB JB-CO2 compression 3 -DI04: 20 x 1 pr (field cables) |  | CO2 compression 3 x ~19 MW + dehydration | JB-CO2 compression 3 -DI04 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 159 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0130 | G | Carbon capture | Home run JB-CO2 compression 3 -DI04 to the control / marshalling room |  | CCS F&G / control | JB-CO2 compression 3 -DI04 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 183 | 105
G-I-0131 | G | Carbon capture | Discrete device to JB JB-CO2 compression 3 -DI05: 20 x 1 pr (field cables) |  | CO2 compression 3 x ~19 MW + dehydration | JB-CO2 compression 3 -DI05 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 159 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0132 | G | Carbon capture | Home run JB-CO2 compression 3 -DI05 to the control / marshalling room |  | CCS F&G / control | JB-CO2 compression 3 -DI05 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 183 | 105
G-I-0133 | G | Carbon capture | RTD to JB JB-CO2 compression 3 -RTD01: 10 x 1 tri (field cables) |  | CO2 compression 3 x ~19 MW + dehydration | JB-CO2 compression 3 -RTD01 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 159 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0134 | G | Carbon capture | Home run JB-CO2 compression 3 -RTD01 to the control / marshalling room |  | CCS F&G / control | JB-CO2 compression 3 -RTD01 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 183 | 105
G-I-0135 | G | Carbon capture | RTD to JB JB-CO2 compression 3 -RTD02: 10 x 1 tri (field cables) |  | CO2 compression 3 x ~19 MW + dehydration | JB-CO2 compression 3 -RTD02 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 159 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0136 | G | Carbon capture | Home run JB-CO2 compression 3 -RTD02 to the control / marshalling room |  | CCS F&G / control | JB-CO2 compression 3 -RTD02 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 183 | 105
G-I-0137 | G | Carbon capture | RTD to JB JB-CO2 compression 3 -RTD03: 10 x 1 tri (field cables) |  | CO2 compression 3 x ~19 MW + dehydration | JB-CO2 compression 3 -RTD03 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 159 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0138 | G | Carbon capture | Home run JB-CO2 compression 3 -RTD03 to the control / marshalling room |  | CCS F&G / control | JB-CO2 compression 3 -RTD03 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 183 | 105
G-I-0139 | G | Carbon capture | RTD to JB JB-CO2 compression 3 -RTD04: 6 x 1 tri (field cables) |  | CO2 compression 3 x ~19 MW + dehydration | JB-CO2 compression 3 -RTD04 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 6 | 1 |  |  |  | Tray / conduit | 159 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0140 | G | Carbon capture | Home run JB-CO2 compression 3 -RTD04 to the control / marshalling room |  | CCS F&G / control | JB-CO2 compression 3 -RTD04 | CO2 compression 3 x ~19 MW + dehydration | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 183 | 105
G-I-0141 | G | Carbon capture | Analog instrument to JB JB-CO2 dehydration: m-AI01: 20 x 1 pr (field cables) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | JB-CO2 dehydration: m-AI01 | CO2 dehydration: molecular-sieve towers and regeneration heater | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 81 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0142 | G | Carbon capture | Home run JB-CO2 dehydration: m-AI01 to the control / marshalling room |  | CCS F&G / control | JB-CO2 dehydration: m-AI01 | CO2 dehydration: molecular-sieve towers and regeneration heater | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 197 | 229
G-I-0143 | G | Carbon capture | Analog instrument to JB JB-CO2 dehydration: m-AI02: 10 x 1 pr (field cables) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | JB-CO2 dehydration: m-AI02 | CO2 dehydration: molecular-sieve towers and regeneration heater | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 81 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0144 | G | Carbon capture | Home run JB-CO2 dehydration: m-AI02 to the control / marshalling room |  | CCS F&G / control | JB-CO2 dehydration: m-AI02 | CO2 dehydration: molecular-sieve towers and regeneration heater | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 197 | 229
G-I-0145 | G | Carbon capture | Discrete device to JB JB-CO2 dehydration: m-DI01: 20 x 1 pr (field cables) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | JB-CO2 dehydration: m-DI01 | CO2 dehydration: molecular-sieve towers and regeneration heater | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 81 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0146 | G | Carbon capture | Home run JB-CO2 dehydration: m-DI01 to the control / marshalling room |  | CCS F&G / control | JB-CO2 dehydration: m-DI01 | CO2 dehydration: molecular-sieve towers and regeneration heater | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 197 | 229
G-I-0147 | G | Carbon capture | Discrete device to JB JB-CO2 dehydration: m-DI02: 10 x 1 pr (field cables) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | JB-CO2 dehydration: m-DI02 | CO2 dehydration: molecular-sieve towers and regeneration heater | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 81 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0148 | G | Carbon capture | Home run JB-CO2 dehydration: m-DI02 to the control / marshalling room |  | CCS F&G / control | JB-CO2 dehydration: m-DI02 | CO2 dehydration: molecular-sieve towers and regeneration heater | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 197 | 229
G-I-0149 | G | Carbon capture | Analog instrument to JB JB-CONDITIONAL: HP ex-AI01: 20 x 1 pr (field cables) |  | CONDITIONAL: HP export compressor + metering | JB-CONDITIONAL: HP ex-AI01 | CONDITIONAL: HP export compressor + metering | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 100 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0150 | G | Carbon capture | Home run JB-CONDITIONAL: HP ex-AI01 to the control / marshalling room |  | CCS F&G / control | JB-CONDITIONAL: HP ex-AI01 | CONDITIONAL: HP export compressor + metering | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 144 | 154
G-I-0151 | G | Carbon capture | Analog instrument to JB JB-CONDITIONAL: HP ex-AI02: 20 x 1 pr (field cables) |  | CONDITIONAL: HP export compressor + metering | JB-CONDITIONAL: HP ex-AI02 | CONDITIONAL: HP export compressor + metering | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 100 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0152 | G | Carbon capture | Home run JB-CONDITIONAL: HP ex-AI02 to the control / marshalling room |  | CCS F&G / control | JB-CONDITIONAL: HP ex-AI02 | CONDITIONAL: HP export compressor + metering | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 144 | 154
G-I-0153 | G | Carbon capture | Analog instrument to JB JB-CONDITIONAL: HP ex-AI03: 20 x 1 pr (field cables) |  | CONDITIONAL: HP export compressor + metering | JB-CONDITIONAL: HP ex-AI03 | CONDITIONAL: HP export compressor + metering | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 100 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0154 | G | Carbon capture | Home run JB-CONDITIONAL: HP ex-AI03 to the control / marshalling room |  | CCS F&G / control | JB-CONDITIONAL: HP ex-AI03 | CONDITIONAL: HP export compressor + metering | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 144 | 154
G-I-0155 | G | Carbon capture | Discrete device to JB JB-CONDITIONAL: HP ex-DI01: 20 x 1 pr (field cables) |  | CONDITIONAL: HP export compressor + metering | JB-CONDITIONAL: HP ex-DI01 | CONDITIONAL: HP export compressor + metering | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 100 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0156 | G | Carbon capture | Home run JB-CONDITIONAL: HP ex-DI01 to the control / marshalling room |  | CCS F&G / control | JB-CONDITIONAL: HP ex-DI01 | CONDITIONAL: HP export compressor + metering | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 144 | 154
G-I-0157 | G | Carbon capture | Discrete device to JB JB-CONDITIONAL: HP ex-DI02: 20 x 1 pr (field cables) |  | CONDITIONAL: HP export compressor + metering | JB-CONDITIONAL: HP ex-DI02 | CONDITIONAL: HP export compressor + metering | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 100 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0158 | G | Carbon capture | Home run JB-CONDITIONAL: HP ex-DI02 to the control / marshalling room |  | CCS F&G / control | JB-CONDITIONAL: HP ex-DI02 | CONDITIONAL: HP export compressor + metering | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 144 | 154
G-I-0159 | G | Carbon capture | RTD to JB JB-CONDITIONAL: HP ex-RTD01: 10 x 1 tri (field cables) |  | CONDITIONAL: HP export compressor + metering | JB-CONDITIONAL: HP ex-RTD01 | CONDITIONAL: HP export compressor + metering | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 100 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0160 | G | Carbon capture | Home run JB-CONDITIONAL: HP ex-RTD01 to the control / marshalling room |  | CCS F&G / control | JB-CONDITIONAL: HP ex-RTD01 | CONDITIONAL: HP export compressor + metering | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 144 | 154
G-I-0161 | G | Carbon capture | RTD to JB JB-CONDITIONAL: HP ex-RTD02: 2 x 1 tri (field cables) |  | CONDITIONAL: HP export compressor + metering | JB-CONDITIONAL: HP ex-RTD02 | CONDITIONAL: HP export compressor + metering | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 2 | 1 |  |  |  | Tray / conduit | 100 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0162 | G | Carbon capture | Home run JB-CONDITIONAL: HP ex-RTD02 to the control / marshalling room |  | CCS F&G / control | JB-CONDITIONAL: HP ex-RTD02 | CONDITIONAL: HP export compressor + metering | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 144 | 154
G-I-0163 | G | Carbon capture | Analog instrument to JB JB-DCC-A pumps + wate-AI01: 10 x 1 pr (field cables) |  | DCC-A pumps + water filter | JB-DCC-A pumps + wate-AI01 | DCC-A pumps + water filter | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 60 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0164 | G | Carbon capture | Home run JB-DCC-A pumps + wate-AI01 to the control / marshalling room |  | CCS F&G / control | JB-DCC-A pumps + wate-AI01 | DCC-A pumps + water filter | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 884 | 233
G-I-0165 | G | Carbon capture | Discrete device to JB JB-DCC-A pumps + wate-DI01: 10 x 1 pr (field cables) |  | DCC-A pumps + water filter | JB-DCC-A pumps + wate-DI01 | DCC-A pumps + water filter | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 60 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0166 | G | Carbon capture | Home run JB-DCC-A pumps + wate-DI01 to the control / marshalling room |  | CCS F&G / control | JB-DCC-A pumps + wate-DI01 | DCC-A pumps + water filter | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 884 | 233
G-I-0167 | G | Carbon capture | Analog instrument to JB JB-DCC-A-AI01: 20 x 1 pr (field cables) | DCC-A | DCC-A: direct-contact cooler (quench) | JB-DCC-A-AI01 | DCC-A: direct-contact cooler (quench) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 121 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0168 | G | Carbon capture | Home run JB-DCC-A-AI01 to the control / marshalling room |  | CCS F&G / control | JB-DCC-A-AI01 | DCC-A: direct-contact cooler (quench) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 861 | 129
G-I-0169 | G | Carbon capture | Discrete device to JB JB-DCC-A-DI01: 10 x 1 pr (field cables) | DCC-A | DCC-A: direct-contact cooler (quench) | JB-DCC-A-DI01 | DCC-A: direct-contact cooler (quench) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 121 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0170 | G | Carbon capture | Home run JB-DCC-A-DI01 to the control / marshalling room |  | CCS F&G / control | JB-DCC-A-DI01 | DCC-A: direct-contact cooler (quench) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 861 | 129
G-I-0171 | G | Carbon capture | Analog instrument to JB JB-DCC-B pumps + wate-AI01: 10 x 1 pr (field cables) |  | DCC-B pumps + water filter | JB-DCC-B pumps + wate-AI01 | DCC-B pumps + water filter | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 60 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0172 | G | Carbon capture | Home run JB-DCC-B pumps + wate-AI01 to the control / marshalling room |  | CCS F&G / control | JB-DCC-B pumps + wate-AI01 | DCC-B pumps + water filter | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 784 | 191
G-I-0173 | G | Carbon capture | Discrete device to JB JB-DCC-B pumps + wate-DI01: 10 x 1 pr (field cables) |  | DCC-B pumps + water filter | JB-DCC-B pumps + wate-DI01 | DCC-B pumps + water filter | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 60 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0174 | G | Carbon capture | Home run JB-DCC-B pumps + wate-DI01 to the control / marshalling room |  | CCS F&G / control | JB-DCC-B pumps + wate-DI01 | DCC-B pumps + water filter | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 784 | 191
G-I-0175 | G | Carbon capture | Analog instrument to JB JB-DCC-B-AI01: 20 x 1 pr (field cables) | DCC-B | DCC-B: direct-contact cooler (quench) | JB-DCC-B-AI01 | DCC-B: direct-contact cooler (quench) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 121 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0176 | G | Carbon capture | Home run JB-DCC-B-AI01 to the control / marshalling room |  | CCS F&G / control | JB-DCC-B-AI01 | DCC-B: direct-contact cooler (quench) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 701 | 129
G-I-0177 | G | Carbon capture | Discrete device to JB JB-DCC-B-DI01: 10 x 1 pr (field cables) | DCC-B | DCC-B: direct-contact cooler (quench) | JB-DCC-B-DI01 | DCC-B: direct-contact cooler (quench) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 121 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0178 | G | Carbon capture | Home run JB-DCC-B-DI01 to the control / marshalling room |  | CCS F&G / control | JB-DCC-B-DI01 | DCC-B: direct-contact cooler (quench) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 701 | 129
G-I-0179 | G | Carbon capture | Analog instrument to JB JB-DCC-C pumps + wate-AI01: 10 x 1 pr (field cables) |  | DCC-C pumps + water filter | JB-DCC-C pumps + wate-AI01 | DCC-C pumps + water filter | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 60 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0180 | G | Carbon capture | Home run JB-DCC-C pumps + wate-AI01 to the control / marshalling room |  | CCS F&G / control | JB-DCC-C pumps + wate-AI01 | DCC-C pumps + water filter | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 564 | 233
G-I-0181 | G | Carbon capture | Discrete device to JB JB-DCC-C pumps + wate-DI01: 10 x 1 pr (field cables) |  | DCC-C pumps + water filter | JB-DCC-C pumps + wate-DI01 | DCC-C pumps + water filter | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 60 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0182 | G | Carbon capture | Home run JB-DCC-C pumps + wate-DI01 to the control / marshalling room |  | CCS F&G / control | JB-DCC-C pumps + wate-DI01 | DCC-C pumps + water filter | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 564 | 233
G-I-0183 | G | Carbon capture | Analog instrument to JB JB-DCC-C-AI01: 20 x 1 pr (field cables) | DCC-C | DCC-C: direct-contact cooler (quench) | JB-DCC-C-AI01 | DCC-C: direct-contact cooler (quench) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 121 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0184 | G | Carbon capture | Home run JB-DCC-C-AI01 to the control / marshalling room |  | CCS F&G / control | JB-DCC-C-AI01 | DCC-C: direct-contact cooler (quench) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 541 | 129
G-I-0185 | G | Carbon capture | Discrete device to JB JB-DCC-C-DI01: 10 x 1 pr (field cables) | DCC-C | DCC-C: direct-contact cooler (quench) | JB-DCC-C-DI01 | DCC-C: direct-contact cooler (quench) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 121 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0186 | G | Carbon capture | Home run JB-DCC-C-DI01 to the control / marshalling room |  | CCS F&G / control | JB-DCC-C-DI01 | DCC-C: direct-contact cooler (quench) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 541 | 129
G-I-0187 | G | Carbon capture | Analog instrument to JB JB-DMP-A-AI01: 8 x 1 pr (field cables) | DMP-A | DMP-A: diverter / bypass damper | JB-DMP-A-AI01 | DMP-A: diverter / bypass damper | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 74 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0188 | G | Carbon capture | Home run JB-DMP-A-AI01 to the control / marshalling room |  | CCS F&G / control | JB-DMP-A-AI01 | DMP-A: diverter / bypass damper | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1230 | 193
G-I-0189 | G | Carbon capture | Discrete device to JB JB-DMP-A-DI01: 16 x 1 pr (field cables) | DMP-A | DMP-A: diverter / bypass damper | JB-DMP-A-DI01 | DMP-A: diverter / bypass damper | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 74 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0190 | G | Carbon capture | Home run JB-DMP-A-DI01 to the control / marshalling room |  | CCS F&G / control | JB-DMP-A-DI01 | DMP-A: diverter / bypass damper | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1230 | 193
G-I-0191 | G | Carbon capture | Analog instrument to JB JB-DMP-B-AI01: 8 x 1 pr (field cables) | DMP-B | DMP-B: diverter / bypass damper | JB-DMP-B-AI01 | DMP-B: diverter / bypass damper | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 74 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0192 | G | Carbon capture | Home run JB-DMP-B-AI01 to the control / marshalling room |  | CCS F&G / control | JB-DMP-B-AI01 | DMP-B: diverter / bypass damper | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1074 | 189
G-I-0193 | G | Carbon capture | Discrete device to JB JB-DMP-B-DI01: 16 x 1 pr (field cables) | DMP-B | DMP-B: diverter / bypass damper | JB-DMP-B-DI01 | DMP-B: diverter / bypass damper | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 74 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0194 | G | Carbon capture | Home run JB-DMP-B-DI01 to the control / marshalling room |  | CCS F&G / control | JB-DMP-B-DI01 | DMP-B: diverter / bypass damper | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1074 | 189
G-I-0195 | G | Carbon capture | Analog instrument to JB JB-DMP-C-AI01: 8 x 1 pr (field cables) | DMP-C | DMP-C: diverter / bypass damper | JB-DMP-C-AI01 | DMP-C: diverter / bypass damper | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 74 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0196 | G | Carbon capture | Home run JB-DMP-C-AI01 to the control / marshalling room |  | CCS F&G / control | JB-DMP-C-AI01 | DMP-C: diverter / bypass damper | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 910 | 193
G-I-0197 | G | Carbon capture | Discrete device to JB JB-DMP-C-DI01: 16 x 1 pr (field cables) | DMP-C | DMP-C: diverter / bypass damper | JB-DMP-C-DI01 | DMP-C: diverter / bypass damper | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 74 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0198 | G | Carbon capture | Home run JB-DMP-C-DI01 to the control / marshalling room |  | CCS F&G / control | JB-DMP-C-DI01 | DMP-C: diverter / bypass damper | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 910 | 193
G-I-0199 | G | Carbon capture | Analog instrument to JB JB-RB-A: reboiler (LP-AI01: 15 x 1 pr (field cables) |  | RB-A: reboiler (LP steam from ST extraction) | JB-RB-A: reboiler (LP-AI01 | RB-A: reboiler (LP steam from ST extraction) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 15 | 1 |  |  |  | Tray / conduit | 80 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0200 | G | Carbon capture | Home run JB-RB-A: reboiler (LP-AI01 to the control / marshalling room |  | CCS F&G / control | JB-RB-A: reboiler (LP-AI01 | RB-A: reboiler (LP steam from ST extraction) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 266 | 111
G-I-0201 | G | Carbon capture | Discrete device to JB JB-RB-A: reboiler (LP-DI01: 10 x 1 pr (field cables) |  | RB-A: reboiler (LP steam from ST extraction) | JB-RB-A: reboiler (LP-DI01 | RB-A: reboiler (LP steam from ST extraction) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 80 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0202 | G | Carbon capture | Home run JB-RB-A: reboiler (LP-DI01 to the control / marshalling room |  | CCS F&G / control | JB-RB-A: reboiler (LP-DI01 | RB-A: reboiler (LP steam from ST extraction) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 266 | 111
G-I-0203 | G | Carbon capture | Analog instrument to JB JB-RB-B: reboiler (LP-AI01: 15 x 1 pr (field cables) |  | RB-B: reboiler (LP steam from ST extraction) | JB-RB-B: reboiler (LP-AI01 | RB-B: reboiler (LP steam from ST extraction) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 15 | 1 |  |  |  | Tray / conduit | 80 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0204 | G | Carbon capture | Home run JB-RB-B: reboiler (LP-AI01 to the control / marshalling room |  | CCS F&G / control | JB-RB-B: reboiler (LP-AI01 | RB-B: reboiler (LP steam from ST extraction) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 216 | 111
G-I-0205 | G | Carbon capture | Discrete device to JB JB-RB-B: reboiler (LP-DI01: 10 x 1 pr (field cables) |  | RB-B: reboiler (LP steam from ST extraction) | JB-RB-B: reboiler (LP-DI01 | RB-B: reboiler (LP steam from ST extraction) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 80 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0206 | G | Carbon capture | Home run JB-RB-B: reboiler (LP-DI01 to the control / marshalling room |  | CCS F&G / control | JB-RB-B: reboiler (LP-DI01 | RB-B: reboiler (LP steam from ST extraction) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 216 | 111
G-I-0207 | G | Carbon capture | Analog instrument to JB JB-RB-C: reboiler (LP-AI01: 15 x 1 pr (field cables) |  | RB-C: reboiler (LP steam from ST extraction) | JB-RB-C: reboiler (LP-AI01 | RB-C: reboiler (LP steam from ST extraction) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 15 | 1 |  |  |  | Tray / conduit | 80 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0208 | G | Carbon capture | Home run JB-RB-C: reboiler (LP-AI01 to the control / marshalling room |  | CCS F&G / control | JB-RB-C: reboiler (LP-AI01 | RB-C: reboiler (LP steam from ST extraction) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 161 | 116
G-I-0209 | G | Carbon capture | Discrete device to JB JB-RB-C: reboiler (LP-DI01: 10 x 1 pr (field cables) |  | RB-C: reboiler (LP steam from ST extraction) | JB-RB-C: reboiler (LP-DI01 | RB-C: reboiler (LP steam from ST extraction) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 80 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0210 | G | Carbon capture | Home run JB-RB-C: reboiler (LP-DI01 to the control / marshalling room |  | CCS F&G / control | JB-RB-C: reboiler (LP-DI01 | RB-C: reboiler (LP steam from ST extraction) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 161 | 116
G-I-0211 | G | Carbon capture | Analog instrument to JB JB-Reclaimer (thermal-AI01: 15 x 1 pr (field cables) |  | Reclaimer (thermal, intermittent) | JB-Reclaimer (thermal-AI01 | Reclaimer (thermal, intermittent) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 15 | 1 |  |  |  | Tray / conduit | 82 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0212 | G | Carbon capture | Home run JB-Reclaimer (thermal-AI01 to the control / marshalling room |  | CCS F&G / control | JB-Reclaimer (thermal-AI01 | Reclaimer (thermal, intermittent) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 130 | 102
G-I-0213 | G | Carbon capture | Discrete device to JB JB-Reclaimer (thermal-DI01: 10 x 1 pr (field cables) |  | Reclaimer (thermal, intermittent) | JB-Reclaimer (thermal-DI01 | Reclaimer (thermal, intermittent) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 82 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0214 | G | Carbon capture | Home run JB-Reclaimer (thermal-DI01 to the control / marshalling room |  | CCS F&G / control | JB-Reclaimer (thermal-DI01 | Reclaimer (thermal, intermittent) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 130 | 102
G-I-0215 | G | Carbon capture | Analog instrument to JB JB-Rich/lean pumps, c-AI01: 20 x 1 pr (field cables) |  | Rich/lean pumps, cross exchanger, lean cooler A | JB-Rich/lean pumps, c-AI01 | Rich/lean pumps, cross exchanger, lean cooler A | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 84 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0216 | G | Carbon capture | Home run JB-Rich/lean pumps, c-AI01 to the control / marshalling room |  | CCS F&G / control | JB-Rich/lean pumps, c-AI01 | Rich/lean pumps, cross exchanger, lean cooler A | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 834 | 181
G-I-0217 | G | Carbon capture | Discrete device to JB JB-Rich/lean pumps, c-DI01: 20 x 1 pr (field cables) |  | Rich/lean pumps, cross exchanger, lean cooler A | JB-Rich/lean pumps, c-DI01 | Rich/lean pumps, cross exchanger, lean cooler A | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 84 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0218 | G | Carbon capture | Home run JB-Rich/lean pumps, c-DI01 to the control / marshalling room |  | CCS F&G / control | JB-Rich/lean pumps, c-DI01 | Rich/lean pumps, cross exchanger, lean cooler A | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 834 | 181
G-I-0219 | G | Carbon capture | RTD to JB JB-Rich/lean pumps, c-RTD01: 10 x 1 tri (field cables) |  | Rich/lean pumps, cross exchanger, lean cooler A | JB-Rich/lean pumps, c-RTD01 | Rich/lean pumps, cross exchanger, lean cooler A | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 84 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0220 | G | Carbon capture | Home run JB-Rich/lean pumps, c-RTD01 to the control / marshalling room |  | CCS F&G / control | JB-Rich/lean pumps, c-RTD01 | Rich/lean pumps, cross exchanger, lean cooler A | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Tray | 834 | 181
G-I-0221 | G | Carbon capture | RTD to JB JB-Rich/lean pumps, c-RTD02: 2 x 1 tri (field cables) |  | Rich/lean pumps, cross exchanger, lean cooler A | JB-Rich/lean pumps, c-RTD02 | Rich/lean pumps, cross exchanger, lean cooler A | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 2 | 1 |  |  |  | Tray / conduit | 84 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0222 | G | Carbon capture | Home run JB-Rich/lean pumps, c-RTD02 to the control / marshalling room |  | CCS F&G / control | JB-Rich/lean pumps, c-RTD02 | Rich/lean pumps, cross exchanger, lean cooler A | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Tray | 834 | 181
G-I-0223 | G | Carbon capture | Analog instrument to JB JB-Rich/lean pumps, c-AI01: 20 x 1 pr (field cables) |  | Rich/lean pumps, cross exchanger, lean cooler B | JB-Rich/lean pumps, c-AI01 | Rich/lean pumps, cross exchanger, lean cooler B | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 84 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0224 | G | Carbon capture | Home run JB-Rich/lean pumps, c-AI01 to the control / marshalling room |  | CCS F&G / control | JB-Rich/lean pumps, c-AI01 | Rich/lean pumps, cross exchanger, lean cooler B | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 674 | 181
G-I-0225 | G | Carbon capture | Discrete device to JB JB-Rich/lean pumps, c-DI01: 20 x 1 pr (field cables) |  | Rich/lean pumps, cross exchanger, lean cooler B | JB-Rich/lean pumps, c-DI01 | Rich/lean pumps, cross exchanger, lean cooler B | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 84 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0226 | G | Carbon capture | Home run JB-Rich/lean pumps, c-DI01 to the control / marshalling room |  | CCS F&G / control | JB-Rich/lean pumps, c-DI01 | Rich/lean pumps, cross exchanger, lean cooler B | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 674 | 181
G-I-0227 | G | Carbon capture | RTD to JB JB-Rich/lean pumps, c-RTD01: 10 x 1 tri (field cables) |  | Rich/lean pumps, cross exchanger, lean cooler B | JB-Rich/lean pumps, c-RTD01 | Rich/lean pumps, cross exchanger, lean cooler B | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 84 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0228 | G | Carbon capture | Home run JB-Rich/lean pumps, c-RTD01 to the control / marshalling room |  | CCS F&G / control | JB-Rich/lean pumps, c-RTD01 | Rich/lean pumps, cross exchanger, lean cooler B | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 674 | 181
G-I-0229 | G | Carbon capture | RTD to JB JB-Rich/lean pumps, c-RTD02: 2 x 1 tri (field cables) |  | Rich/lean pumps, cross exchanger, lean cooler B | JB-Rich/lean pumps, c-RTD02 | Rich/lean pumps, cross exchanger, lean cooler B | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 2 | 1 |  |  |  | Tray / conduit | 84 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0230 | G | Carbon capture | Home run JB-Rich/lean pumps, c-RTD02 to the control / marshalling room |  | CCS F&G / control | JB-Rich/lean pumps, c-RTD02 | Rich/lean pumps, cross exchanger, lean cooler B | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 674 | 181
G-I-0231 | G | Carbon capture | Analog instrument to JB JB-Rich/lean pumps, c-AI01: 20 x 1 pr (field cables) |  | Rich/lean pumps, cross exchanger, lean cooler C | JB-Rich/lean pumps, c-AI01 | Rich/lean pumps, cross exchanger, lean cooler C | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 84 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0232 | G | Carbon capture | Home run JB-Rich/lean pumps, c-AI01 to the control / marshalling room |  | CCS F&G / control | JB-Rich/lean pumps, c-AI01 | Rich/lean pumps, cross exchanger, lean cooler C | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 299 | 138
G-I-0233 | G | Carbon capture | Discrete device to JB JB-Rich/lean pumps, c-DI01: 20 x 1 pr (field cables) |  | Rich/lean pumps, cross exchanger, lean cooler C | JB-Rich/lean pumps, c-DI01 | Rich/lean pumps, cross exchanger, lean cooler C | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 84 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0234 | G | Carbon capture | Home run JB-Rich/lean pumps, c-DI01 to the control / marshalling room |  | CCS F&G / control | JB-Rich/lean pumps, c-DI01 | Rich/lean pumps, cross exchanger, lean cooler C | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 299 | 138
G-I-0235 | G | Carbon capture | RTD to JB JB-Rich/lean pumps, c-RTD01: 10 x 1 tri (field cables) |  | Rich/lean pumps, cross exchanger, lean cooler C | JB-Rich/lean pumps, c-RTD01 | Rich/lean pumps, cross exchanger, lean cooler C | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 84 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0236 | G | Carbon capture | Home run JB-Rich/lean pumps, c-RTD01 to the control / marshalling room |  | CCS F&G / control | JB-Rich/lean pumps, c-RTD01 | Rich/lean pumps, cross exchanger, lean cooler C | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 299 | 138
G-I-0237 | G | Carbon capture | RTD to JB JB-Rich/lean pumps, c-RTD02: 2 x 1 tri (field cables) |  | Rich/lean pumps, cross exchanger, lean cooler C | JB-Rich/lean pumps, c-RTD02 | Rich/lean pumps, cross exchanger, lean cooler C | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 2 | 1 |  |  |  | Tray / conduit | 84 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0238 | G | Carbon capture | Home run JB-Rich/lean pumps, c-RTD02 to the control / marshalling room |  | CCS F&G / control | JB-Rich/lean pumps, c-RTD02 | Rich/lean pumps, cross exchanger, lean cooler C | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 299 | 138
G-I-0239 | G | Carbon capture | Analog instrument to JB JB-STR-A-AI01: 20 x 1 pr (field cables) | STR-A | STR-A: stripper / regenerator (45 ft dia x 207 ft) | JB-STR-A-AI01 | STR-A: stripper / regenerator (45 ft dia x 207 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 153 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0240 | G | Carbon capture | Home run JB-STR-A-AI01 to the control / marshalling room |  | CCS F&G / control | JB-STR-A-AI01 | STR-A: stripper / regenerator (45 ft dia x 207 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 329 | 106
G-I-0241 | G | Carbon capture | Analog instrument to JB JB-STR-A-AI02: 20 x 1 pr (field cables) | STR-A | STR-A: stripper / regenerator (45 ft dia x 207 ft) | JB-STR-A-AI02 | STR-A: stripper / regenerator (45 ft dia x 207 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 153 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0242 | G | Carbon capture | Home run JB-STR-A-AI02 to the control / marshalling room |  | CCS F&G / control | JB-STR-A-AI02 | STR-A: stripper / regenerator (45 ft dia x 207 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 329 | 106
G-I-0243 | G | Carbon capture | Analog instrument to JB JB-STR-A-AI03: 10 x 1 pr (field cables) | STR-A | STR-A: stripper / regenerator (45 ft dia x 207 ft) | JB-STR-A-AI03 | STR-A: stripper / regenerator (45 ft dia x 207 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 153 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0244 | G | Carbon capture | Home run JB-STR-A-AI03 to the control / marshalling room |  | CCS F&G / control | JB-STR-A-AI03 | STR-A: stripper / regenerator (45 ft dia x 207 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 329 | 106
G-I-0245 | G | Carbon capture | Discrete device to JB JB-STR-A-DI01: 20 x 1 pr (field cables) | STR-A | STR-A: stripper / regenerator (45 ft dia x 207 ft) | JB-STR-A-DI01 | STR-A: stripper / regenerator (45 ft dia x 207 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 153 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0246 | G | Carbon capture | Home run JB-STR-A-DI01 to the control / marshalling room |  | CCS F&G / control | JB-STR-A-DI01 | STR-A: stripper / regenerator (45 ft dia x 207 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 329 | 106
G-I-0247 | G | Carbon capture | Discrete device to JB JB-STR-A-DI02: 10 x 1 pr (field cables) | STR-A | STR-A: stripper / regenerator (45 ft dia x 207 ft) | JB-STR-A-DI02 | STR-A: stripper / regenerator (45 ft dia x 207 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 153 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0248 | G | Carbon capture | Home run JB-STR-A-DI02 to the control / marshalling room |  | CCS F&G / control | JB-STR-A-DI02 | STR-A: stripper / regenerator (45 ft dia x 207 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 329 | 106
G-I-0249 | G | Carbon capture | Analog instrument to JB JB-STR-B-AI01: 20 x 1 pr (field cables) | STR-B | STR-B: stripper / regenerator (45 ft dia x 207 ft) | JB-STR-B-AI01 | STR-B: stripper / regenerator (45 ft dia x 207 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 153 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0250 | G | Carbon capture | Home run JB-STR-B-AI01 to the control / marshalling room |  | CCS F&G / control | JB-STR-B-AI01 | STR-B: stripper / regenerator (45 ft dia x 207 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 279 | 106
G-I-0251 | G | Carbon capture | Analog instrument to JB JB-STR-B-AI02: 20 x 1 pr (field cables) | STR-B | STR-B: stripper / regenerator (45 ft dia x 207 ft) | JB-STR-B-AI02 | STR-B: stripper / regenerator (45 ft dia x 207 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 153 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0252 | G | Carbon capture | Home run JB-STR-B-AI02 to the control / marshalling room |  | CCS F&G / control | JB-STR-B-AI02 | STR-B: stripper / regenerator (45 ft dia x 207 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 279 | 106
G-I-0253 | G | Carbon capture | Analog instrument to JB JB-STR-B-AI03: 10 x 1 pr (field cables) | STR-B | STR-B: stripper / regenerator (45 ft dia x 207 ft) | JB-STR-B-AI03 | STR-B: stripper / regenerator (45 ft dia x 207 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 153 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0254 | G | Carbon capture | Home run JB-STR-B-AI03 to the control / marshalling room |  | CCS F&G / control | JB-STR-B-AI03 | STR-B: stripper / regenerator (45 ft dia x 207 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 279 | 106
G-I-0255 | G | Carbon capture | Discrete device to JB JB-STR-B-DI01: 20 x 1 pr (field cables) | STR-B | STR-B: stripper / regenerator (45 ft dia x 207 ft) | JB-STR-B-DI01 | STR-B: stripper / regenerator (45 ft dia x 207 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 153 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0256 | G | Carbon capture | Home run JB-STR-B-DI01 to the control / marshalling room |  | CCS F&G / control | JB-STR-B-DI01 | STR-B: stripper / regenerator (45 ft dia x 207 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 279 | 106
G-I-0257 | G | Carbon capture | Discrete device to JB JB-STR-B-DI02: 10 x 1 pr (field cables) | STR-B | STR-B: stripper / regenerator (45 ft dia x 207 ft) | JB-STR-B-DI02 | STR-B: stripper / regenerator (45 ft dia x 207 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 153 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0258 | G | Carbon capture | Home run JB-STR-B-DI02 to the control / marshalling room |  | CCS F&G / control | JB-STR-B-DI02 | STR-B: stripper / regenerator (45 ft dia x 207 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 279 | 106
G-I-0259 | G | Carbon capture | Analog instrument to JB JB-STR-C-AI01: 20 x 1 pr (field cables) | STR-C | STR-C: stripper / regenerator (45 ft dia x 207 ft) | JB-STR-C-AI01 | STR-C: stripper / regenerator (45 ft dia x 207 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 153 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0260 | G | Carbon capture | Home run JB-STR-C-AI01 to the control / marshalling room |  | CCS F&G / control | JB-STR-C-AI01 | STR-C: stripper / regenerator (45 ft dia x 207 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 195 | 162
G-I-0261 | G | Carbon capture | Analog instrument to JB JB-STR-C-AI02: 20 x 1 pr (field cables) | STR-C | STR-C: stripper / regenerator (45 ft dia x 207 ft) | JB-STR-C-AI02 | STR-C: stripper / regenerator (45 ft dia x 207 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 153 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0262 | G | Carbon capture | Home run JB-STR-C-AI02 to the control / marshalling room |  | CCS F&G / control | JB-STR-C-AI02 | STR-C: stripper / regenerator (45 ft dia x 207 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 195 | 162
G-I-0263 | G | Carbon capture | Analog instrument to JB JB-STR-C-AI03: 10 x 1 pr (field cables) | STR-C | STR-C: stripper / regenerator (45 ft dia x 207 ft) | JB-STR-C-AI03 | STR-C: stripper / regenerator (45 ft dia x 207 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 153 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0264 | G | Carbon capture | Home run JB-STR-C-AI03 to the control / marshalling room |  | CCS F&G / control | JB-STR-C-AI03 | STR-C: stripper / regenerator (45 ft dia x 207 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 195 | 162
G-I-0265 | G | Carbon capture | Discrete device to JB JB-STR-C-DI01: 20 x 1 pr (field cables) | STR-C | STR-C: stripper / regenerator (45 ft dia x 207 ft) | JB-STR-C-DI01 | STR-C: stripper / regenerator (45 ft dia x 207 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 153 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0266 | G | Carbon capture | Home run JB-STR-C-DI01 to the control / marshalling room |  | CCS F&G / control | JB-STR-C-DI01 | STR-C: stripper / regenerator (45 ft dia x 207 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 195 | 162
G-I-0267 | G | Carbon capture | Discrete device to JB JB-STR-C-DI02: 10 x 1 pr (field cables) | STR-C | STR-C: stripper / regenerator (45 ft dia x 207 ft) | JB-STR-C-DI02 | STR-C: stripper / regenerator (45 ft dia x 207 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 153 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0268 | G | Carbon capture | Home run JB-STR-C-DI02 to the control / marshalling room |  | CCS F&G / control | JB-STR-C-DI02 | STR-C: stripper / regenerator (45 ft dia x 207 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 195 | 162
G-I-0269 | G | Carbon capture | Analog instrument to JB JB-Solvent + NaOH sto-AI01: 10 x 1 pr (field cables) |  | Solvent + NaOH storage | JB-Solvent + NaOH sto-AI01 | Solvent + NaOH storage | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 113 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0270 | G | Carbon capture | Home run JB-Solvent + NaOH sto-AI01 to the control / marshalling room |  | CCS F&G / control | JB-Solvent + NaOH sto-AI01 | Solvent + NaOH storage | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 146 | 106
G-I-0271 | G | Carbon capture | Discrete device to JB JB-Solvent + NaOH sto-DI01: 10 x 1 pr (field cables) |  | Solvent + NaOH storage | JB-Solvent + NaOH sto-DI01 | Solvent + NaOH storage | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 113 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0272 | G | Carbon capture | Home run JB-Solvent + NaOH sto-DI01 to the control / marshalling room |  | CCS F&G / control | JB-Solvent + NaOH sto-DI01 | Solvent + NaOH storage | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 146 | 106
G-I-0273 | G | Carbon capture | Analog instrument to JB JB-Water-wash pumps A-AI01: 8 x 1 pr (field cables) |  | Water-wash pumps A | JB-Water-wash pumps A-AI01 | Water-wash pumps A | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 66 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0274 | G | Carbon capture | Home run JB-Water-wash pumps A-AI01 to the control / marshalling room |  | CCS F&G / control | JB-Water-wash pumps A-AI01 | Water-wash pumps A | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 834 | 165
G-I-0275 | G | Carbon capture | Discrete device to JB JB-Water-wash pumps A-DI01: 8 x 1 pr (field cables) |  | Water-wash pumps A | JB-Water-wash pumps A-DI01 | Water-wash pumps A | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 66 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0276 | G | Carbon capture | Home run JB-Water-wash pumps A-DI01 to the control / marshalling room |  | CCS F&G / control | JB-Water-wash pumps A-DI01 | Water-wash pumps A | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 834 | 165
G-I-0277 | G | Carbon capture | Analog instrument to JB JB-Water-wash pumps B-AI01: 8 x 1 pr (field cables) |  | Water-wash pumps B | JB-Water-wash pumps B-AI01 | Water-wash pumps B | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 66 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0278 | G | Carbon capture | Home run JB-Water-wash pumps B-AI01 to the control / marshalling room |  | CCS F&G / control | JB-Water-wash pumps B-AI01 | Water-wash pumps B | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 674 | 165
G-I-0279 | G | Carbon capture | Discrete device to JB JB-Water-wash pumps B-DI01: 8 x 1 pr (field cables) |  | Water-wash pumps B | JB-Water-wash pumps B-DI01 | Water-wash pumps B | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 66 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0280 | G | Carbon capture | Home run JB-Water-wash pumps B-DI01 to the control / marshalling room |  | CCS F&G / control | JB-Water-wash pumps B-DI01 | Water-wash pumps B | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 674 | 165
G-I-0281 | G | Carbon capture | Analog instrument to JB JB-Water-wash pumps C-AI01: 8 x 1 pr (field cables) |  | Water-wash pumps C | JB-Water-wash pumps C-AI01 | Water-wash pumps C | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 66 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0282 | G | Carbon capture | Home run JB-Water-wash pumps C-AI01 to the control / marshalling room |  | CCS F&G / control | JB-Water-wash pumps C-AI01 | Water-wash pumps C | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 514 | 165
G-I-0283 | G | Carbon capture | Discrete device to JB JB-Water-wash pumps C-DI01: 8 x 1 pr (field cables) |  | Water-wash pumps C | JB-Water-wash pumps C-DI01 | Water-wash pumps C | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 66 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
G-I-0284 | G | Carbon capture | Home run JB-Water-wash pumps C-DI01 to the control / marshalling room |  | CCS F&G / control | JB-Water-wash pumps C-DI01 | Water-wash pumps C | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 514 | 165
G-P-0001 | G | Carbon capture | MOV 1: power |  | CCS MV switchgear building (VFDs) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 570 | 80 |  |  |  |  | VD 1.1 %
G-P-0002 | G | Carbon capture | MOV 2: power |  | CCS MV switchgear building (VFDs) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 570 | 80 |  |  |  |  | VD 1.1 %
G-P-0003 | G | Carbon capture | MOV 3: power |  | CCS MV switchgear building (VFDs) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 570 | 80 |  |  |  |  | VD 1.1 %
G-P-0004 | G | Carbon capture | MOV 4: power |  | CCS MV switchgear building (VFDs) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 570 | 80 |  |  |  |  | VD 1.1 %
G-P-0005 | G | Carbon capture | MOV 5: power |  | CCS MV switchgear building (VFDs) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 570 | 80 |  |  |  |  | VD 1.1 %
G-P-0006 | G | Carbon capture | MOV 6: power |  | CCS MV switchgear building (VFDs) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 570 | 80 |  |  |  |  | VD 1.1 %
G-P-0007 | G | Carbon capture | MOV 7: power |  | CCS MV switchgear building (VFDs) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 570 | 80 |  |  |  |  | VD 1.1 %
G-P-0008 | G | Carbon capture | MOV 8: power |  | CCS MV switchgear building (VFDs) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 570 | 80 |  |  |  |  | VD 1.1 %
G-P-0009 | G | Carbon capture | MOV 9: power |  | CCS MV switchgear building (VFDs) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 570 | 80 |  |  |  |  | VD 1.1 %
G-P-0010 | G | Carbon capture | MOV 10: power |  | CCS MV switchgear building (VFDs) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 570 | 80 |  |  |  |  | VD 1.1 %
G-P-0011 | G | Carbon capture | LV power feeder |  | CCS MV switchgear building (VFDs) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 40 | 56.6 | Tray | 570 | 80 |  |  |  |  | VD 2.8 %
G-P-0012 | G | Carbon capture | Area / platform lighting circuit 1 (12 fixtures) |  | CCS MV switchgear building (VFDs) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 870 | 80 |  |  |  |  | fixture-to-fixture run included
G-P-0013 | G | Carbon capture | Area / platform lighting circuit 2 (12 fixtures) |  | CCS MV switchgear building (VFDs) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 870 | 80 |  |  |  |  | fixture-to-fixture run included
G-P-0014 | G | Carbon capture | Area / platform lighting circuit 3 (6 fixtures) |  | CCS MV switchgear building (VFDs) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 870 | 80 |  |  |  |  | fixture-to-fixture run included
G-P-0015 | G | Carbon capture | 480 V welding receptacle 1 |  | CCS MV switchgear building (VFDs) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 60 | 76 | Tray | 570 | 80 |  |  |  |  | VD 2.4 %
G-P-0016 | G | Carbon capture | 480 V welding receptacle 2 |  | CCS MV switchgear building (VFDs) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 60 | 76 | Tray | 570 | 80 |  |  |  |  | VD 2.4 %
G-P-0017 | G | Carbon capture | 480 V welding receptacle 3 |  | CCS MV switchgear building (VFDs) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 60 | 76 | Tray | 570 | 80 |  |  |  |  | VD 2.4 %
G-P-0018 | G | Carbon capture | 480 V welding receptacle 4 |  | CCS MV switchgear building (VFDs) | ABS-A | Absorber A (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 60 | 76 | Tray | 570 | 80 |  |  |  |  | VD 2.4 %
G-P-0019 | G | Carbon capture | Motor 1 of 2, 150 kW |  | CCS MV switchgear building (VFDs) |  | Absorber A intercooler (pumps + plate exchanger) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 150 | 212.3 | Tray | 552 | 81 |  |  |  |  | VD 2.0 %
G-P-0020 | G | Carbon capture | Motor 2 of 2, 150 kW |  | CCS MV switchgear building (VFDs) |  | Absorber A intercooler (pumps + plate exchanger) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 150 | 212.3 | Tray | 552 | 81 |  |  |  |  | VD 2.0 %
G-P-0021 | G | Carbon capture | MOV 1: power |  | CCS MV switchgear building (VFDs) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 410 | 80 |  |  |  |  | VD 0.8 %
G-P-0022 | G | Carbon capture | MOV 2: power |  | CCS MV switchgear building (VFDs) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 410 | 80 |  |  |  |  | VD 0.8 %
G-P-0023 | G | Carbon capture | MOV 3: power |  | CCS MV switchgear building (VFDs) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 410 | 80 |  |  |  |  | VD 0.8 %
G-P-0024 | G | Carbon capture | MOV 4: power |  | CCS MV switchgear building (VFDs) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 410 | 80 |  |  |  |  | VD 0.8 %
G-P-0025 | G | Carbon capture | MOV 5: power |  | CCS MV switchgear building (VFDs) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 410 | 80 |  |  |  |  | VD 0.8 %
G-P-0026 | G | Carbon capture | MOV 6: power |  | CCS MV switchgear building (VFDs) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 410 | 80 |  |  |  |  | VD 0.8 %
G-P-0027 | G | Carbon capture | MOV 7: power |  | CCS MV switchgear building (VFDs) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 410 | 80 |  |  |  |  | VD 0.8 %
G-P-0028 | G | Carbon capture | MOV 8: power |  | CCS MV switchgear building (VFDs) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 410 | 80 |  |  |  |  | VD 0.8 %
G-P-0029 | G | Carbon capture | MOV 9: power |  | CCS MV switchgear building (VFDs) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 410 | 80 |  |  |  |  | VD 0.8 %
G-P-0030 | G | Carbon capture | MOV 10: power |  | CCS MV switchgear building (VFDs) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 410 | 80 |  |  |  |  | VD 0.8 %
G-P-0031 | G | Carbon capture | LV power feeder |  | CCS MV switchgear building (VFDs) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 40 | 56.6 | Tray | 410 | 80 |  |  |  |  | VD 2.1 %
G-P-0032 | G | Carbon capture | Area / platform lighting circuit 1 (12 fixtures) |  | CCS MV switchgear building (VFDs) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 710 | 80 |  |  |  |  | fixture-to-fixture run included
G-P-0033 | G | Carbon capture | Area / platform lighting circuit 2 (12 fixtures) |  | CCS MV switchgear building (VFDs) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 710 | 80 |  |  |  |  | fixture-to-fixture run included
G-P-0034 | G | Carbon capture | Area / platform lighting circuit 3 (6 fixtures) |  | CCS MV switchgear building (VFDs) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 710 | 80 |  |  |  |  | fixture-to-fixture run included
G-P-0035 | G | Carbon capture | 480 V welding receptacle 1 |  | CCS MV switchgear building (VFDs) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 410 | 80 |  |  |  |  | VD 2.9 %
G-P-0036 | G | Carbon capture | 480 V welding receptacle 2 |  | CCS MV switchgear building (VFDs) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 410 | 80 |  |  |  |  | VD 2.9 %
G-P-0037 | G | Carbon capture | 480 V welding receptacle 3 |  | CCS MV switchgear building (VFDs) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 410 | 80 |  |  |  |  | VD 2.9 %
G-P-0038 | G | Carbon capture | 480 V welding receptacle 4 |  | CCS MV switchgear building (VFDs) | ABS-B | Absorber B (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 410 | 80 |  |  |  |  | VD 2.9 %
G-P-0039 | G | Carbon capture | Motor 1 of 2, 150 kW |  | CCS MV switchgear building (VFDs) |  | Absorber B intercooler (pumps + plate exchanger) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 150 | 212.3 | Tray | 392 | 81 |  |  |  |  | VD 1.5 %
G-P-0040 | G | Carbon capture | Motor 2 of 2, 150 kW |  | CCS MV switchgear building (VFDs) |  | Absorber B intercooler (pumps + plate exchanger) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 150 | 212.3 | Tray | 392 | 81 |  |  |  |  | VD 1.5 %
G-P-0041 | G | Carbon capture | MOV 1: power |  | CCS MV switchgear building (VFDs) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 250 | 80 |  |  |  |  | VD 0.6 %
G-P-0042 | G | Carbon capture | MOV 2: power |  | CCS MV switchgear building (VFDs) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 250 | 80 |  |  |  |  | VD 0.6 %
G-P-0043 | G | Carbon capture | MOV 3: power |  | CCS MV switchgear building (VFDs) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 250 | 80 |  |  |  |  | VD 0.6 %
G-P-0044 | G | Carbon capture | MOV 4: power |  | CCS MV switchgear building (VFDs) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 250 | 80 |  |  |  |  | VD 0.6 %
G-P-0045 | G | Carbon capture | MOV 5: power |  | CCS MV switchgear building (VFDs) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 250 | 80 |  |  |  |  | VD 0.6 %
G-P-0046 | G | Carbon capture | MOV 6: power |  | CCS MV switchgear building (VFDs) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 250 | 80 |  |  |  |  | VD 0.6 %
G-P-0047 | G | Carbon capture | MOV 7: power |  | CCS MV switchgear building (VFDs) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 250 | 80 |  |  |  |  | VD 0.6 %
G-P-0048 | G | Carbon capture | MOV 8: power |  | CCS MV switchgear building (VFDs) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 250 | 80 |  |  |  |  | VD 0.6 %
G-P-0049 | G | Carbon capture | MOV 9: power |  | CCS MV switchgear building (VFDs) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 250 | 80 |  |  |  |  | VD 0.6 %
G-P-0050 | G | Carbon capture | MOV 10: power |  | CCS MV switchgear building (VFDs) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Tray | 250 | 80 |  |  |  |  | VD 0.6 %
G-P-0051 | G | Carbon capture | LV power feeder |  | CCS MV switchgear building (VFDs) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 40 | 56.6 | Tray | 250 | 80 |  |  |  |  | VD 2.3 %
G-P-0052 | G | Carbon capture | Area / platform lighting circuit 1 (12 fixtures) |  | CCS MV switchgear building (VFDs) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 550 | 80 |  |  |  |  | fixture-to-fixture run included
G-P-0053 | G | Carbon capture | Area / platform lighting circuit 2 (12 fixtures) |  | CCS MV switchgear building (VFDs) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 550 | 80 |  |  |  |  | fixture-to-fixture run included
G-P-0054 | G | Carbon capture | Area / platform lighting circuit 3 (6 fixtures) |  | CCS MV switchgear building (VFDs) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 550 | 80 |  |  |  |  | fixture-to-fixture run included
G-P-0055 | G | Carbon capture | 480 V welding receptacle 1 |  | CCS MV switchgear building (VFDs) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 250 | 80 |  |  |  |  | VD 1.9 %
G-P-0056 | G | Carbon capture | 480 V welding receptacle 2 |  | CCS MV switchgear building (VFDs) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 250 | 80 |  |  |  |  | VD 1.9 %
G-P-0057 | G | Carbon capture | 480 V welding receptacle 3 |  | CCS MV switchgear building (VFDs) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 250 | 80 |  |  |  |  | VD 1.9 %
G-P-0058 | G | Carbon capture | 480 V welding receptacle 4 |  | CCS MV switchgear building (VFDs) | ABS-C | Absorber C (62 ft dia x 262 ft, stack to 313 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 250 | 80 |  |  |  |  | VD 1.9 %
G-P-0059 | G | Carbon capture | Motor 1 of 2, 150 kW |  | CCS MV switchgear building (VFDs) |  | Absorber C intercooler (pumps + plate exchanger) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 150 | 212.3 | Tray | 232 | 81 |  |  |  |  | VD 1.0 %
G-P-0060 | G | Carbon capture | Motor 2 of 2, 150 kW |  | CCS MV switchgear building (VFDs) |  | Absorber C intercooler (pumps + plate exchanger) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 150 | 212.3 | Tray | 232 | 81 |  |  |  |  | VD 1.0 %
G-P-0061 | G | Carbon capture | LV power feeder |  | CCS MV switchgear building (VFDs) |  | Activated-carbon filter | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 289 | 43 |  |  |  |  | VD 2.1 %
G-P-0062 | G | Carbon capture | Motor 1 of 4, 15 kW |  | CCS MV switchgear building (VFDs) | BF-A | BF-A: booster fan (~16 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 460 | 32 |  |  |  |  | VD 2.0 %
G-P-0063 | G | Carbon capture | Motor 2 of 4, 15 kW |  | CCS MV switchgear building (VFDs) | BF-A | BF-A: booster fan (~16 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 460 | 32 |  |  |  |  | VD 2.0 %
G-P-0064 | G | Carbon capture | Motor 3 of 4, 15 kW |  | CCS MV switchgear building (VFDs) | BF-A | BF-A: booster fan (~16 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 460 | 32 |  |  |  |  | VD 2.0 %
G-P-0065 | G | Carbon capture | Motor 4 of 4, 15 kW |  | CCS MV switchgear building (VFDs) | BF-A | BF-A: booster fan (~16 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 460 | 32 |  |  |  |  | VD 2.0 %
G-P-0066 | G | Carbon capture | 480 V welding receptacle 1 |  | CCS MV switchgear building (VFDs) | BF-A | BF-A: booster fan (~16 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Duct bank | 460 | 32 |  |  |  |  | VD 2.9 %
G-P-0067 | G | Carbon capture | 480 V welding receptacle 2 |  | CCS MV switchgear building (VFDs) | BF-A | BF-A: booster fan (~16 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Duct bank | 460 | 32 |  |  |  |  | VD 2.9 %
G-P-0068 | G | Carbon capture | 480 V welding receptacle 3 |  | CCS MV switchgear building (VFDs) | BF-A | BF-A: booster fan (~16 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Duct bank | 460 | 32 |  |  |  |  | VD 2.9 %
G-P-0069 | G | Carbon capture | 480 V welding receptacle 4 |  | CCS MV switchgear building (VFDs) | BF-A | BF-A: booster fan (~16 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Duct bank | 460 | 32 |  |  |  |  | VD 2.9 %
G-P-0070 | G | Carbon capture | Motor 1 of 4, 15 kW |  | CCS MV switchgear building (VFDs) | BF-B | BF-B: booster fan (~16 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 300 | 32 |  |  |  |  | VD 2.1 %
G-P-0071 | G | Carbon capture | Motor 2 of 4, 15 kW |  | CCS MV switchgear building (VFDs) | BF-B | BF-B: booster fan (~16 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 300 | 32 |  |  |  |  | VD 2.1 %
G-P-0072 | G | Carbon capture | Motor 3 of 4, 15 kW |  | CCS MV switchgear building (VFDs) | BF-B | BF-B: booster fan (~16 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 300 | 32 |  |  |  |  | VD 2.1 %
G-P-0073 | G | Carbon capture | Motor 4 of 4, 15 kW |  | CCS MV switchgear building (VFDs) | BF-B | BF-B: booster fan (~16 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 300 | 32 |  |  |  |  | VD 2.1 %
G-P-0074 | G | Carbon capture | 480 V welding receptacle 1 |  | CCS MV switchgear building (VFDs) | BF-B | BF-B: booster fan (~16 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Duct bank | 300 | 32 |  |  |  |  | VD 1.9 %
G-P-0075 | G | Carbon capture | 480 V welding receptacle 2 |  | CCS MV switchgear building (VFDs) | BF-B | BF-B: booster fan (~16 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Duct bank | 300 | 32 |  |  |  |  | VD 1.9 %
G-P-0076 | G | Carbon capture | 480 V welding receptacle 3 |  | CCS MV switchgear building (VFDs) | BF-B | BF-B: booster fan (~16 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Duct bank | 300 | 32 |  |  |  |  | VD 1.9 %
G-P-0077 | G | Carbon capture | 480 V welding receptacle 4 |  | CCS MV switchgear building (VFDs) | BF-B | BF-B: booster fan (~16 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Duct bank | 300 | 32 |  |  |  |  | VD 1.9 %
G-P-0078 | G | Carbon capture | Motor 1 of 4, 15 kW |  | CCS MV switchgear building (VFDs) | BF-C | BF-C: booster fan (~16 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Tray | 16 | 150 |  |  |  |  | VD 1.7 %
G-P-0079 | G | Carbon capture | Motor 2 of 4, 15 kW |  | CCS MV switchgear building (VFDs) | BF-C | BF-C: booster fan (~16 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Tray | 16 | 150 |  |  |  |  | VD 1.7 %
G-P-0080 | G | Carbon capture | Motor 3 of 4, 15 kW |  | CCS MV switchgear building (VFDs) | BF-C | BF-C: booster fan (~16 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Tray | 16 | 150 |  |  |  |  | VD 1.7 %
G-P-0081 | G | Carbon capture | Motor 4 of 4, 15 kW |  | CCS MV switchgear building (VFDs) | BF-C | BF-C: booster fan (~16 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Tray | 16 | 150 |  |  |  |  | VD 1.7 %
G-P-0082 | G | Carbon capture | 480 V welding receptacle 1 |  | CCS MV switchgear building (VFDs) | BF-C | BF-C: booster fan (~16 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 16 | 150 |  |  |  |  | VD 1.0 %
G-P-0083 | G | Carbon capture | 480 V welding receptacle 2 |  | CCS MV switchgear building (VFDs) | BF-C | BF-C: booster fan (~16 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 16 | 150 |  |  |  |  | VD 1.0 %
G-P-0084 | G | Carbon capture | 480 V welding receptacle 3 |  | CCS MV switchgear building (VFDs) | BF-C | BF-C: booster fan (~16 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 16 | 150 |  |  |  |  | VD 1.0 %
G-P-0085 | G | Carbon capture | 480 V welding receptacle 4 |  | CCS MV switchgear building (VFDs) | BF-C | BF-C: booster fan (~16 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 16 | 150 |  |  |  |  | VD 1.0 %
G-P-0086 | G | Carbon capture | LV panel / distribution feeder |  | CCS MV switchgear building (VFDs) |  | CCS F&G / control | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 40 | 56.6 | Duct bank | 206 | 101 |  |  |  |  | VD 2.1 %
G-P-0087 | G | Carbon capture | LV panel / distribution feeder |  | CCS MV switchgear building (VFDs) |  | CCS MV switchgear building (VFDs) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦3/0 | 3/C+G | 3/0 | 1 | 1 | 480 | 109 | 154.2 | Tray | 0 | 32 |  |  |  |  | VD 0.2 %
G-P-0088 | G | Carbon capture | Motor 1 of 6, 2 kW |  | CCS MV switchgear building (VFDs) | CCS T-1 | CCS T-1: 230/13.8 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 361 | 32 |  |  |  |  | VD 0.5 %
G-P-0089 | G | Carbon capture | Motor 2 of 6, 2 kW |  | CCS MV switchgear building (VFDs) | CCS T-1 | CCS T-1: 230/13.8 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 361 | 32 |  |  |  |  | VD 0.5 %
G-P-0090 | G | Carbon capture | Motor 3 of 6, 2 kW |  | CCS MV switchgear building (VFDs) | CCS T-1 | CCS T-1: 230/13.8 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 361 | 32 |  |  |  |  | VD 0.5 %
G-P-0091 | G | Carbon capture | Motor 4 of 6, 2 kW |  | CCS MV switchgear building (VFDs) | CCS T-1 | CCS T-1: 230/13.8 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 361 | 32 |  |  |  |  | VD 0.5 %
G-P-0092 | G | Carbon capture | Motor 5 of 6, 2 kW |  | CCS MV switchgear building (VFDs) | CCS T-1 | CCS T-1: 230/13.8 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 361 | 32 |  |  |  |  | VD 0.5 %
G-P-0093 | G | Carbon capture | Motor 6 of 6, 2 kW |  | CCS MV switchgear building (VFDs) | CCS T-1 | CCS T-1: 230/13.8 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 361 | 32 |  |  |  |  | VD 0.5 %
G-P-0094 | G | Carbon capture | Motor 1 of 6, 2 kW |  | CCS MV switchgear building (VFDs) | CCS T-2 | CCS T-2: 230/13.8 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 409 | 32 |  |  |  |  | VD 0.6 %
G-P-0095 | G | Carbon capture | Motor 2 of 6, 2 kW |  | CCS MV switchgear building (VFDs) | CCS T-2 | CCS T-2: 230/13.8 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 409 | 32 |  |  |  |  | VD 0.6 %
G-P-0096 | G | Carbon capture | Motor 3 of 6, 2 kW |  | CCS MV switchgear building (VFDs) | CCS T-2 | CCS T-2: 230/13.8 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 409 | 32 |  |  |  |  | VD 0.6 %
G-P-0097 | G | Carbon capture | Motor 4 of 6, 2 kW |  | CCS MV switchgear building (VFDs) | CCS T-2 | CCS T-2: 230/13.8 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 409 | 32 |  |  |  |  | VD 0.6 %
G-P-0098 | G | Carbon capture | Motor 5 of 6, 2 kW |  | CCS MV switchgear building (VFDs) | CCS T-2 | CCS T-2: 230/13.8 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 409 | 32 |  |  |  |  | VD 0.6 %
G-P-0099 | G | Carbon capture | Motor 6 of 6, 2 kW |  | CCS MV switchgear building (VFDs) | CCS T-2 | CCS T-2: 230/13.8 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 409 | 32 |  |  |  |  | VD 0.6 %
G-P-0100 | G | Carbon capture | Motor 1 of 30, 110 kW (VFD output) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦3/0 | 3/C+3G | 3/0 | 1 | 1 | 480 | 110 | 156 | Tray | 250 | 42 |  |  |  |  | VD 1.4 %
G-P-0101 | G | Carbon capture | Motor 2 of 30, 110 kW (VFD output) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦3/0 | 3/C+3G | 3/0 | 1 | 1 | 480 | 110 | 156 | Tray | 250 | 42 |  |  |  |  | VD 1.4 %
G-P-0102 | G | Carbon capture | Motor 3 of 30, 110 kW (VFD output) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦3/0 | 3/C+3G | 3/0 | 1 | 1 | 480 | 110 | 156 | Tray | 250 | 42 |  |  |  |  | VD 1.4 %
G-P-0103 | G | Carbon capture | Motor 4 of 30, 110 kW (VFD output) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦3/0 | 3/C+3G | 3/0 | 1 | 1 | 480 | 110 | 156 | Tray | 250 | 42 |  |  |  |  | VD 1.4 %
G-P-0104 | G | Carbon capture | Motor 5 of 30, 110 kW (VFD output) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦3/0 | 3/C+3G | 3/0 | 1 | 1 | 480 | 110 | 156 | Tray | 250 | 42 |  |  |  |  | VD 1.4 %
G-P-0105 | G | Carbon capture | Motor 6 of 30, 110 kW (VFD output) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦3/0 | 3/C+3G | 3/0 | 1 | 1 | 480 | 110 | 156 | Tray | 250 | 42 |  |  |  |  | VD 1.4 %
G-P-0106 | G | Carbon capture | Motor 7 of 30, 110 kW (VFD output) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦3/0 | 3/C+3G | 3/0 | 1 | 1 | 480 | 110 | 156 | Tray | 250 | 42 |  |  |  |  | VD 1.4 %
G-P-0107 | G | Carbon capture | Motor 8 of 30, 110 kW (VFD output) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦3/0 | 3/C+3G | 3/0 | 1 | 1 | 480 | 110 | 156 | Tray | 250 | 42 |  |  |  |  | VD 1.4 %
G-P-0108 | G | Carbon capture | Motor 9 of 30, 110 kW (VFD output) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦3/0 | 3/C+3G | 3/0 | 1 | 1 | 480 | 110 | 156 | Tray | 250 | 42 |  |  |  |  | VD 1.4 %
G-P-0109 | G | Carbon capture | Motor 10 of 30, 110 kW (VFD output) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦3/0 | 3/C+3G | 3/0 | 1 | 1 | 480 | 110 | 156 | Tray | 250 | 42 |  |  |  |  | VD 1.4 %
G-P-0110 | G | Carbon capture | Motor 11 of 30, 110 kW (VFD output) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦3/0 | 3/C+3G | 3/0 | 1 | 1 | 480 | 110 | 156 | Tray | 250 | 42 |  |  |  |  | VD 1.4 %
G-P-0111 | G | Carbon capture | Motor 12 of 30, 110 kW (VFD output) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦3/0 | 3/C+3G | 3/0 | 1 | 1 | 480 | 110 | 156 | Tray | 250 | 42 |  |  |  |  | VD 1.4 %
G-P-0112 | G | Carbon capture | Motor 13 of 30, 110 kW (VFD output) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦3/0 | 3/C+3G | 3/0 | 1 | 1 | 480 | 110 | 156 | Tray | 250 | 42 |  |  |  |  | VD 1.4 %
G-P-0113 | G | Carbon capture | Motor 14 of 30, 110 kW (VFD output) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦3/0 | 3/C+3G | 3/0 | 1 | 1 | 480 | 110 | 156 | Tray | 250 | 42 |  |  |  |  | VD 1.4 %
G-P-0114 | G | Carbon capture | Motor 15 of 30, 110 kW (VFD output) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦3/0 | 3/C+3G | 3/0 | 1 | 1 | 480 | 110 | 156 | Tray | 250 | 42 |  |  |  |  | VD 1.4 %
G-P-0115 | G | Carbon capture | Motor 16 of 30, 110 kW (VFD output) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦3/0 | 3/C+3G | 3/0 | 1 | 1 | 480 | 110 | 156 | Tray | 250 | 42 |  |  |  |  | VD 1.4 %
G-P-0116 | G | Carbon capture | Motor 17 of 30, 110 kW (VFD output) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦3/0 | 3/C+3G | 3/0 | 1 | 1 | 480 | 110 | 156 | Tray | 250 | 42 |  |  |  |  | VD 1.4 %
G-P-0117 | G | Carbon capture | Motor 18 of 30, 110 kW (VFD output) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦3/0 | 3/C+3G | 3/0 | 1 | 1 | 480 | 110 | 156 | Tray | 250 | 42 |  |  |  |  | VD 1.4 %
G-P-0118 | G | Carbon capture | Motor 19 of 30, 110 kW (VFD output) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦3/0 | 3/C+3G | 3/0 | 1 | 1 | 480 | 110 | 156 | Tray | 250 | 42 |  |  |  |  | VD 1.4 %
G-P-0119 | G | Carbon capture | Motor 20 of 30, 110 kW (VFD output) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦3/0 | 3/C+3G | 3/0 | 1 | 1 | 480 | 110 | 156 | Tray | 250 | 42 |  |  |  |  | VD 1.4 %
G-P-0120 | G | Carbon capture | Motor 21 of 30, 110 kW (VFD output) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦3/0 | 3/C+3G | 3/0 | 1 | 1 | 480 | 110 | 156 | Tray | 250 | 42 |  |  |  |  | VD 1.4 %
G-P-0121 | G | Carbon capture | Motor 22 of 30, 110 kW (VFD output) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦3/0 | 3/C+3G | 3/0 | 1 | 1 | 480 | 110 | 156 | Tray | 250 | 42 |  |  |  |  | VD 1.4 %
G-P-0122 | G | Carbon capture | Motor 23 of 30, 110 kW (VFD output) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦3/0 | 3/C+3G | 3/0 | 1 | 1 | 480 | 110 | 156 | Tray | 250 | 42 |  |  |  |  | VD 1.4 %
G-P-0123 | G | Carbon capture | Motor 24 of 30, 110 kW (VFD output) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦3/0 | 3/C+3G | 3/0 | 1 | 1 | 480 | 110 | 156 | Tray | 250 | 42 |  |  |  |  | VD 1.4 %
G-P-0124 | G | Carbon capture | Motor 25 of 30, 110 kW (VFD output) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦3/0 | 3/C+3G | 3/0 | 1 | 1 | 480 | 110 | 156 | Tray | 250 | 42 |  |  |  |  | VD 1.4 %
G-P-0125 | G | Carbon capture | Motor 26 of 30, 110 kW (VFD output) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦3/0 | 3/C+3G | 3/0 | 1 | 1 | 480 | 110 | 156 | Tray | 250 | 42 |  |  |  |  | VD 1.4 %
G-P-0126 | G | Carbon capture | Motor 27 of 30, 110 kW (VFD output) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦3/0 | 3/C+3G | 3/0 | 1 | 1 | 480 | 110 | 156 | Tray | 250 | 42 |  |  |  |  | VD 1.4 %
G-P-0127 | G | Carbon capture | Motor 28 of 30, 110 kW (VFD output) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦3/0 | 3/C+3G | 3/0 | 1 | 1 | 480 | 110 | 156 | Tray | 250 | 42 |  |  |  |  | VD 1.4 %
G-P-0128 | G | Carbon capture | Motor 29 of 30, 110 kW (VFD output) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦3/0 | 3/C+3G | 3/0 | 1 | 1 | 480 | 110 | 156 | Tray | 250 | 42 |  |  |  |  | VD 1.4 %
G-P-0129 | G | Carbon capture | Motor 30 of 30, 110 kW (VFD output) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦3/0 | 3/C+3G | 3/0 | 1 | 1 | 480 | 110 | 156 | Tray | 250 | 42 |  |  |  |  | VD 1.4 %
G-P-0130 | G | Carbon capture | Area / platform lighting circuit 1 (12 fixtures) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 300 | 42 |  |  |  |  | fixture-to-fixture run included
G-P-0131 | G | Carbon capture | Area / platform lighting circuit 2 (12 fixtures) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 300 | 42 |  |  |  |  | fixture-to-fixture run included
G-P-0132 | G | Carbon capture | Area / platform lighting circuit 3 (6 fixtures) |  | CT MCC / VFD e-house | CCS-CT | CCS cooling tower (~30 cells): CCS process cooling only | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Tray | 300 | 42 |  |  |  |  | fixture-to-fixture run included
G-P-0133 | G | Carbon capture | Motor 1 of 2, 250 kW |  | CCS MV switchgear building (VFDs) |  | CCS instrument air | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4/0 | 3/C+G | 4/0 | 2 | 1 | 480 | 250 | 353.8 | Duct bank | 206 | 51 |  |  |  |  | VD 1.1 %
G-P-0134 | G | Carbon capture | Motor 2 of 2, 250 kW |  | CCS MV switchgear building (VFDs) |  | CCS instrument air | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4/0 | 3/C+G | 4/0 | 2 | 1 | 480 | 250 | 353.8 | Duct bank | 206 | 51 |  |  |  |  | VD 1.1 %
G-P-0135 | G | Carbon capture | Motor 1 of 6, 15 kW |  | CT MCC / VFD e-house |  | CCS wastewater (DCC + tower blowdown) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 5 | 87 |  |  |  |  | VD 0.9 %
G-P-0136 | G | Carbon capture | Motor 2 of 6, 15 kW |  | CT MCC / VFD e-house |  | CCS wastewater (DCC + tower blowdown) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 5 | 87 |  |  |  |  | VD 0.9 %
G-P-0137 | G | Carbon capture | Motor 3 of 6, 15 kW |  | CT MCC / VFD e-house |  | CCS wastewater (DCC + tower blowdown) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 5 | 87 |  |  |  |  | VD 0.9 %
G-P-0138 | G | Carbon capture | Motor 4 of 6, 15 kW |  | CT MCC / VFD e-house |  | CCS wastewater (DCC + tower blowdown) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 5 | 87 |  |  |  |  | VD 0.9 %
G-P-0139 | G | Carbon capture | Motor 5 of 6, 15 kW |  | CT MCC / VFD e-house |  | CCS wastewater (DCC + tower blowdown) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 5 | 87 |  |  |  |  | VD 0.9 %
G-P-0140 | G | Carbon capture | Motor 6 of 6, 15 kW |  | CT MCC / VFD e-house |  | CCS wastewater (DCC + tower blowdown) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 5 | 87 |  |  |  |  | VD 0.9 %
G-P-0141 | G | Carbon capture | Motor 1 of 10, 30 kW |  | CCS MV switchgear building (VFDs) |  | CO2 compression 3 x ~19 MW + dehydration | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 291 | 36 |  |  |  |  | VD 2.7 %
G-P-0142 | G | Carbon capture | Motor 2 of 10, 30 kW |  | CCS MV switchgear building (VFDs) |  | CO2 compression 3 x ~19 MW + dehydration | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 291 | 36 |  |  |  |  | VD 2.7 %
G-P-0143 | G | Carbon capture | Motor 3 of 10, 30 kW |  | CCS MV switchgear building (VFDs) |  | CO2 compression 3 x ~19 MW + dehydration | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 291 | 36 |  |  |  |  | VD 2.7 %
G-P-0144 | G | Carbon capture | Motor 4 of 10, 30 kW |  | CCS MV switchgear building (VFDs) |  | CO2 compression 3 x ~19 MW + dehydration | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 291 | 36 |  |  |  |  | VD 2.7 %
G-P-0145 | G | Carbon capture | Motor 5 of 10, 30 kW |  | CCS MV switchgear building (VFDs) |  | CO2 compression 3 x ~19 MW + dehydration | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 291 | 36 |  |  |  |  | VD 2.7 %
G-P-0146 | G | Carbon capture | Motor 6 of 10, 30 kW |  | CCS MV switchgear building (VFDs) |  | CO2 compression 3 x ~19 MW + dehydration | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 291 | 36 |  |  |  |  | VD 2.7 %
G-P-0147 | G | Carbon capture | Motor 7 of 10, 30 kW |  | CCS MV switchgear building (VFDs) |  | CO2 compression 3 x ~19 MW + dehydration | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 291 | 36 |  |  |  |  | VD 2.7 %
G-P-0148 | G | Carbon capture | Motor 8 of 10, 30 kW |  | CCS MV switchgear building (VFDs) |  | CO2 compression 3 x ~19 MW + dehydration | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 291 | 36 |  |  |  |  | VD 2.7 %
G-P-0149 | G | Carbon capture | Motor 9 of 10, 30 kW |  | CCS MV switchgear building (VFDs) |  | CO2 compression 3 x ~19 MW + dehydration | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 291 | 36 |  |  |  |  | VD 2.7 %
G-P-0150 | G | Carbon capture | Motor 10 of 10, 30 kW |  | CCS MV switchgear building (VFDs) |  | CO2 compression 3 x ~19 MW + dehydration | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 291 | 36 |  |  |  |  | VD 2.7 %
G-P-0151 | G | Carbon capture | 480 V welding receptacle 1 |  | CCS MV switchgear building (VFDs) |  | CO2 compression 3 x ~19 MW + dehydration | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Duct bank | 291 | 36 |  |  |  |  | VD 1.9 %
G-P-0152 | G | Carbon capture | 480 V welding receptacle 2 |  | CCS MV switchgear building (VFDs) |  | CO2 compression 3 x ~19 MW + dehydration | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Duct bank | 291 | 36 |  |  |  |  | VD 1.9 %
G-P-0153 | G | Carbon capture | 480 V welding receptacle 3 |  | CCS MV switchgear building (VFDs) |  | CO2 compression 3 x ~19 MW + dehydration | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Duct bank | 291 | 36 |  |  |  |  | VD 1.9 %
G-P-0154 | G | Carbon capture | 480 V welding receptacle 4 |  | CCS MV switchgear building (VFDs) |  | CO2 compression 3 x ~19 MW + dehydration | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Duct bank | 291 | 36 |  |  |  |  | VD 1.9 %
G-P-0155 | G | Carbon capture | Motor 1 of 2, 20 kW |  | CCS MV switchgear building (VFDs) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 20 | 28.3 | Duct bank | 305 | 160 |  |  |  |  | VD 2.6 %
G-P-0156 | G | Carbon capture | Motor 2 of 2, 20 kW |  | CCS MV switchgear building (VFDs) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 20 | 28.3 | Duct bank | 305 | 160 |  |  |  |  | VD 2.6 %
G-P-0157 | G | Carbon capture | Motor 1 of 1, 200 kW |  | CCS MV switchgear building (VFDs) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦500 | 3/C+G | 500 kcmil | 1 | 1 | 480 | 200 | 283 | Duct bank | 305 | 160 |  |  |  |  | VD 1.3 %
G-P-0158 | G | Carbon capture | MOV 1: power |  | CCS MV switchgear building (VFDs) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 305 | 160 |  |  |  |  | VD 0.8 %
G-P-0159 | G | Carbon capture | MOV 2: power |  | CCS MV switchgear building (VFDs) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 305 | 160 |  |  |  |  | VD 0.8 %
G-P-0160 | G | Carbon capture | MOV 3: power |  | CCS MV switchgear building (VFDs) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 305 | 160 |  |  |  |  | VD 0.8 %
G-P-0161 | G | Carbon capture | MOV 4: power |  | CCS MV switchgear building (VFDs) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 305 | 160 |  |  |  |  | VD 0.8 %
G-P-0162 | G | Carbon capture | MOV 5: power |  | CCS MV switchgear building (VFDs) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 305 | 160 |  |  |  |  | VD 0.8 %
G-P-0163 | G | Carbon capture | MOV 6: power |  | CCS MV switchgear building (VFDs) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 305 | 160 |  |  |  |  | VD 0.8 %
G-P-0164 | G | Carbon capture | MOV 7: power |  | CCS MV switchgear building (VFDs) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 305 | 160 |  |  |  |  | VD 0.8 %
G-P-0165 | G | Carbon capture | MOV 8: power |  | CCS MV switchgear building (VFDs) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 305 | 160 |  |  |  |  | VD 0.8 %
G-P-0166 | G | Carbon capture | MOV 9: power |  | CCS MV switchgear building (VFDs) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 305 | 160 |  |  |  |  | VD 0.8 %
G-P-0167 | G | Carbon capture | MOV 10: power |  | CCS MV switchgear building (VFDs) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 305 | 160 |  |  |  |  | VD 0.8 %
G-P-0168 | G | Carbon capture | MOV 11: power |  | CCS MV switchgear building (VFDs) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 305 | 160 |  |  |  |  | VD 0.8 %
G-P-0169 | G | Carbon capture | MOV 12: power |  | CCS MV switchgear building (VFDs) |  | CO2 dehydration: molecular-sieve towers and regeneration heater | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 305 | 160 |  |  |  |  | VD 0.8 %
G-P-0170 | G | Carbon capture | Motor 1 of 4, 30 kW |  | CCS MV switchgear building (VFDs) |  | CONDITIONAL: HP export compressor + metering | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 303 | 34 |  |  |  |  | VD 2.8 %
G-P-0171 | G | Carbon capture | Motor 2 of 4, 30 kW |  | CCS MV switchgear building (VFDs) |  | CONDITIONAL: HP export compressor + metering | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 303 | 34 |  |  |  |  | VD 2.8 %
G-P-0172 | G | Carbon capture | Motor 3 of 4, 30 kW |  | CCS MV switchgear building (VFDs) |  | CONDITIONAL: HP export compressor + metering | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 303 | 34 |  |  |  |  | VD 2.8 %
G-P-0173 | G | Carbon capture | Motor 4 of 4, 30 kW |  | CCS MV switchgear building (VFDs) |  | CONDITIONAL: HP export compressor + metering | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 303 | 34 |  |  |  |  | VD 2.8 %
G-P-0174 | G | Carbon capture | Motor 1 of 2, 200 kW |  | CCS MV switchgear building (VFDs) |  | DCC-A pumps + water filter | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦500 | 3/C+G | 500 kcmil | 1 | 1 | 480 | 200 | 283 | Tray | 515 | 164 |  |  |  |  | VD 2.0 %
G-P-0175 | G | Carbon capture | Motor 2 of 2, 200 kW |  | CCS MV switchgear building (VFDs) |  | DCC-A pumps + water filter | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦500 | 3/C+G | 500 kcmil | 1 | 1 | 480 | 200 | 283 | Tray | 515 | 164 |  |  |  |  | VD 2.0 %
G-P-0176 | G | Carbon capture | LV power feeder |  | CCS MV switchgear building (VFDs) | DCC-A | DCC-A: direct-contact cooler (quench) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 460 | 60 |  |  |  |  | VD 2.2 %
G-P-0177 | G | Carbon capture | Area / platform lighting circuit 1 (8 fixtures) |  | CCS MV switchgear building (VFDs) | DCC-A | DCC-A: direct-contact cooler (quench) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Duct bank | 760 | 60 |  |  |  |  | fixture-to-fixture run included
G-P-0178 | G | Carbon capture | Motor 1 of 2, 200 kW |  | CCS MV switchgear building (VFDs) |  | DCC-B pumps + water filter | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦500 | 3/C+G | 500 kcmil | 1 | 1 | 480 | 200 | 283 | Tray | 415 | 122 |  |  |  |  | VD 1.6 %
G-P-0179 | G | Carbon capture | Motor 2 of 2, 200 kW |  | CCS MV switchgear building (VFDs) |  | DCC-B pumps + water filter | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦500 | 3/C+G | 500 kcmil | 1 | 1 | 480 | 200 | 283 | Tray | 415 | 122 |  |  |  |  | VD 1.6 %
G-P-0180 | G | Carbon capture | LV power feeder |  | CCS MV switchgear building (VFDs) | DCC-B | DCC-B: direct-contact cooler (quench) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 300 | 60 |  |  |  |  | VD 2.3 %
G-P-0181 | G | Carbon capture | Area / platform lighting circuit 1 (8 fixtures) |  | CCS MV switchgear building (VFDs) | DCC-B | DCC-B: direct-contact cooler (quench) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Duct bank | 600 | 60 |  |  |  |  | fixture-to-fixture run included
G-P-0182 | G | Carbon capture | Motor 1 of 2, 200 kW |  | CCS MV switchgear building (VFDs) |  | DCC-C pumps + water filter | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦500 | 3/C+G | 500 kcmil | 1 | 1 | 480 | 200 | 283 | Tray | 195 | 164 |  |  |  |  | VD 1.0 %
G-P-0183 | G | Carbon capture | Motor 2 of 2, 200 kW |  | CCS MV switchgear building (VFDs) |  | DCC-C pumps + water filter | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦500 | 3/C+G | 500 kcmil | 1 | 1 | 480 | 200 | 283 | Tray | 195 | 164 |  |  |  |  | VD 1.0 %
G-P-0184 | G | Carbon capture | LV power feeder |  | CCS MV switchgear building (VFDs) | DCC-C | DCC-C: direct-contact cooler (quench) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 140 | 60 |  |  |  |  | VD 2.0 %
G-P-0185 | G | Carbon capture | Area / platform lighting circuit 1 (8 fixtures) |  | CCS MV switchgear building (VFDs) | DCC-C | DCC-C: direct-contact cooler (quench) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Duct bank | 440 | 60 |  |  |  |  | fixture-to-fixture run included
G-P-0186 | G | Carbon capture | Motor 1 of 2, 15 kW |  | CCS MV switchgear building (VFDs) | DMP-A | DMP-A: diverter / bypass damper | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1436 | 124 |  |  |  |  | VD 2.5 %
G-P-0187 | G | Carbon capture | Motor 2 of 2, 15 kW |  | CCS MV switchgear building (VFDs) | DMP-A | DMP-A: diverter / bypass damper | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1436 | 124 |  |  |  |  | VD 2.5 %
G-P-0188 | G | Carbon capture | Motor 1 of 2, 15 kW |  | CCS MV switchgear building (VFDs) | DMP-B | DMP-B: diverter / bypass damper | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1280 | 120 |  |  |  |  | VD 2.3 %
G-P-0189 | G | Carbon capture | Motor 2 of 2, 15 kW |  | CCS MV switchgear building (VFDs) | DMP-B | DMP-B: diverter / bypass damper | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1280 | 120 |  |  |  |  | VD 2.3 %
G-P-0190 | G | Carbon capture | Motor 1 of 2, 15 kW |  | CCS MV switchgear building (VFDs) | DMP-C | DMP-C: diverter / bypass damper | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1116 | 124 |  |  |  |  | VD 2.0 %
G-P-0191 | G | Carbon capture | Motor 2 of 2, 15 kW |  | CCS MV switchgear building (VFDs) | DMP-C | DMP-C: diverter / bypass damper | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 1116 | 124 |  |  |  |  | VD 2.0 %
G-P-0192 | G | Carbon capture | MOV 1: power |  | CCS MV switchgear building (VFDs) |  | RB-A: reboiler (LP steam from ST extraction) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 50 | 37 |  |  |  |  | VD 0.1 %
G-P-0193 | G | Carbon capture | MOV 2: power |  | CCS MV switchgear building (VFDs) |  | RB-A: reboiler (LP steam from ST extraction) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 50 | 37 |  |  |  |  | VD 0.1 %
G-P-0194 | G | Carbon capture | MOV 3: power |  | CCS MV switchgear building (VFDs) |  | RB-A: reboiler (LP steam from ST extraction) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 50 | 37 |  |  |  |  | VD 0.1 %
G-P-0195 | G | Carbon capture | MOV 4: power |  | CCS MV switchgear building (VFDs) |  | RB-A: reboiler (LP steam from ST extraction) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 50 | 37 |  |  |  |  | VD 0.1 %
G-P-0196 | G | Carbon capture | LV power feeder |  | CCS MV switchgear building (VFDs) |  | RB-A: reboiler (LP steam from ST extraction) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 10 | 14.2 | Duct bank | 50 | 37 |  |  |  |  | VD 0.6 %
G-P-0197 | G | Carbon capture | MOV 1: power |  | CCS MV switchgear building (VFDs) |  | RB-B: reboiler (LP steam from ST extraction) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 83 | 42 |  |  |  |  | VD 0.2 %
G-P-0198 | G | Carbon capture | MOV 2: power |  | CCS MV switchgear building (VFDs) |  | RB-B: reboiler (LP steam from ST extraction) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 83 | 42 |  |  |  |  | VD 0.2 %
G-P-0199 | G | Carbon capture | MOV 3: power |  | CCS MV switchgear building (VFDs) |  | RB-B: reboiler (LP steam from ST extraction) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 83 | 42 |  |  |  |  | VD 0.2 %
G-P-0200 | G | Carbon capture | MOV 4: power |  | CCS MV switchgear building (VFDs) |  | RB-B: reboiler (LP steam from ST extraction) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 83 | 42 |  |  |  |  | VD 0.2 %
G-P-0201 | G | Carbon capture | LV power feeder |  | CCS MV switchgear building (VFDs) |  | RB-B: reboiler (LP steam from ST extraction) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 10 | 14.2 | Duct bank | 83 | 42 |  |  |  |  | VD 0.8 %
G-P-0202 | G | Carbon capture | MOV 1: power |  | CCS MV switchgear building (VFDs) |  | RB-C: reboiler (LP steam from ST extraction) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 45 | 47 |  |  |  |  | VD 0.2 %
G-P-0203 | G | Carbon capture | MOV 2: power |  | CCS MV switchgear building (VFDs) |  | RB-C: reboiler (LP steam from ST extraction) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 45 | 47 |  |  |  |  | VD 0.2 %
G-P-0204 | G | Carbon capture | MOV 3: power |  | CCS MV switchgear building (VFDs) |  | RB-C: reboiler (LP steam from ST extraction) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 45 | 47 |  |  |  |  | VD 0.2 %
G-P-0205 | G | Carbon capture | MOV 4: power |  | CCS MV switchgear building (VFDs) |  | RB-C: reboiler (LP steam from ST extraction) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 45 | 47 |  |  |  |  | VD 0.2 %
G-P-0206 | G | Carbon capture | LV power feeder |  | CCS MV switchgear building (VFDs) |  | RB-C: reboiler (LP steam from ST extraction) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 10 | 14.2 | Duct bank | 45 | 47 |  |  |  |  | VD 0.6 %
G-P-0207 | G | Carbon capture | Motor 1 of 2, 15 kW |  | CCS MV switchgear building (VFDs) |  | Reclaimer (thermal, intermittent) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 45 | 57 |  |  |  |  | VD 1.0 %
G-P-0208 | G | Carbon capture | Motor 2 of 2, 15 kW |  | CCS MV switchgear building (VFDs) |  | Reclaimer (thermal, intermittent) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 45 | 57 |  |  |  |  | VD 1.0 %
G-P-0209 | G | Carbon capture | MOV 1: power |  | CCS MV switchgear building (VFDs) | STR-A | STR-A: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 146 | 36 |  |  |  |  | VD 0.3 %
G-P-0210 | G | Carbon capture | MOV 2: power |  | CCS MV switchgear building (VFDs) | STR-A | STR-A: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 146 | 36 |  |  |  |  | VD 0.3 %
G-P-0211 | G | Carbon capture | MOV 3: power |  | CCS MV switchgear building (VFDs) | STR-A | STR-A: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 146 | 36 |  |  |  |  | VD 0.3 %
G-P-0212 | G | Carbon capture | MOV 4: power |  | CCS MV switchgear building (VFDs) | STR-A | STR-A: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 146 | 36 |  |  |  |  | VD 0.3 %
G-P-0213 | G | Carbon capture | MOV 5: power |  | CCS MV switchgear building (VFDs) | STR-A | STR-A: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 146 | 36 |  |  |  |  | VD 0.3 %
G-P-0214 | G | Carbon capture | MOV 6: power |  | CCS MV switchgear building (VFDs) | STR-A | STR-A: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 146 | 36 |  |  |  |  | VD 0.3 %
G-P-0215 | G | Carbon capture | LV power feeder |  | CCS MV switchgear building (VFDs) | STR-A | STR-A: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 146 | 36 |  |  |  |  | VD 1.5 %
G-P-0216 | G | Carbon capture | Area / platform lighting circuit 1 (12 fixtures) |  | CCS MV switchgear building (VFDs) | STR-A | STR-A: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Duct bank | 446 | 36 |  |  |  |  | fixture-to-fixture run included
G-P-0217 | G | Carbon capture | Area / platform lighting circuit 2 (8 fixtures) |  | CCS MV switchgear building (VFDs) | STR-A | STR-A: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Duct bank | 446 | 36 |  |  |  |  | fixture-to-fixture run included
G-P-0218 | G | Carbon capture | 480 V welding receptacle 1 |  | CCS MV switchgear building (VFDs) | STR-A | STR-A: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Duct bank | 146 | 36 |  |  |  |  | VD 1.1 %
G-P-0219 | G | Carbon capture | 480 V welding receptacle 2 |  | CCS MV switchgear building (VFDs) | STR-A | STR-A: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Duct bank | 146 | 36 |  |  |  |  | VD 1.1 %
G-P-0220 | G | Carbon capture | 480 V welding receptacle 3 |  | CCS MV switchgear building (VFDs) | STR-A | STR-A: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Duct bank | 146 | 36 |  |  |  |  | VD 1.1 %
G-P-0221 | G | Carbon capture | 480 V welding receptacle 4 |  | CCS MV switchgear building (VFDs) | STR-A | STR-A: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Duct bank | 146 | 36 |  |  |  |  | VD 1.1 %
G-P-0222 | G | Carbon capture | MOV 1: power |  | CCS MV switchgear building (VFDs) | STR-B | STR-B: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 146 | 36 |  |  |  |  | VD 0.3 %
G-P-0223 | G | Carbon capture | MOV 2: power |  | CCS MV switchgear building (VFDs) | STR-B | STR-B: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 146 | 36 |  |  |  |  | VD 0.3 %
G-P-0224 | G | Carbon capture | MOV 3: power |  | CCS MV switchgear building (VFDs) | STR-B | STR-B: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 146 | 36 |  |  |  |  | VD 0.3 %
G-P-0225 | G | Carbon capture | MOV 4: power |  | CCS MV switchgear building (VFDs) | STR-B | STR-B: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 146 | 36 |  |  |  |  | VD 0.3 %
G-P-0226 | G | Carbon capture | MOV 5: power |  | CCS MV switchgear building (VFDs) | STR-B | STR-B: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 146 | 36 |  |  |  |  | VD 0.3 %
G-P-0227 | G | Carbon capture | MOV 6: power |  | CCS MV switchgear building (VFDs) | STR-B | STR-B: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 146 | 36 |  |  |  |  | VD 0.3 %
G-P-0228 | G | Carbon capture | LV power feeder |  | CCS MV switchgear building (VFDs) | STR-B | STR-B: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 146 | 36 |  |  |  |  | VD 1.5 %
G-P-0229 | G | Carbon capture | Area / platform lighting circuit 1 (12 fixtures) |  | CCS MV switchgear building (VFDs) | STR-B | STR-B: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Duct bank | 446 | 36 |  |  |  |  | fixture-to-fixture run included
G-P-0230 | G | Carbon capture | Area / platform lighting circuit 2 (8 fixtures) |  | CCS MV switchgear building (VFDs) | STR-B | STR-B: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Duct bank | 446 | 36 |  |  |  |  | fixture-to-fixture run included
G-P-0231 | G | Carbon capture | 480 V welding receptacle 1 |  | CCS MV switchgear building (VFDs) | STR-B | STR-B: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Duct bank | 146 | 36 |  |  |  |  | VD 1.1 %
G-P-0232 | G | Carbon capture | 480 V welding receptacle 2 |  | CCS MV switchgear building (VFDs) | STR-B | STR-B: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Duct bank | 146 | 36 |  |  |  |  | VD 1.1 %
G-P-0233 | G | Carbon capture | 480 V welding receptacle 3 |  | CCS MV switchgear building (VFDs) | STR-B | STR-B: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Duct bank | 146 | 36 |  |  |  |  | VD 1.1 %
G-P-0234 | G | Carbon capture | 480 V welding receptacle 4 |  | CCS MV switchgear building (VFDs) | STR-B | STR-B: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Duct bank | 146 | 36 |  |  |  |  | VD 1.1 %
G-P-0235 | G | Carbon capture | MOV 1: power |  | CCS MV switchgear building (VFDs) | STR-C | STR-C: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 196 | 36 |  |  |  |  | VD 0.4 %
G-P-0236 | G | Carbon capture | MOV 2: power |  | CCS MV switchgear building (VFDs) | STR-C | STR-C: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 196 | 36 |  |  |  |  | VD 0.4 %
G-P-0237 | G | Carbon capture | MOV 3: power |  | CCS MV switchgear building (VFDs) | STR-C | STR-C: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 196 | 36 |  |  |  |  | VD 0.4 %
G-P-0238 | G | Carbon capture | MOV 4: power |  | CCS MV switchgear building (VFDs) | STR-C | STR-C: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 196 | 36 |  |  |  |  | VD 0.4 %
G-P-0239 | G | Carbon capture | MOV 5: power |  | CCS MV switchgear building (VFDs) | STR-C | STR-C: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 196 | 36 |  |  |  |  | VD 0.4 %
G-P-0240 | G | Carbon capture | MOV 6: power |  | CCS MV switchgear building (VFDs) | STR-C | STR-C: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2.5 | 3.5 | Duct bank | 196 | 36 |  |  |  |  | VD 0.4 %
G-P-0241 | G | Carbon capture | LV power feeder |  | CCS MV switchgear building (VFDs) | STR-C | STR-C: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 196 | 36 |  |  |  |  | VD 1.9 %
G-P-0242 | G | Carbon capture | Area / platform lighting circuit 1 (12 fixtures) |  | CCS MV switchgear building (VFDs) | STR-C | STR-C: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Duct bank | 496 | 36 |  |  |  |  | fixture-to-fixture run included
G-P-0243 | G | Carbon capture | Area / platform lighting circuit 2 (8 fixtures) |  | CCS MV switchgear building (VFDs) | STR-C | STR-C: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Duct bank | 496 | 36 |  |  |  |  | fixture-to-fixture run included
G-P-0244 | G | Carbon capture | 480 V welding receptacle 1 |  | CCS MV switchgear building (VFDs) | STR-C | STR-C: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Duct bank | 196 | 36 |  |  |  |  | VD 1.4 %
G-P-0245 | G | Carbon capture | 480 V welding receptacle 2 |  | CCS MV switchgear building (VFDs) | STR-C | STR-C: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Duct bank | 196 | 36 |  |  |  |  | VD 1.4 %
G-P-0246 | G | Carbon capture | 480 V welding receptacle 3 |  | CCS MV switchgear building (VFDs) | STR-C | STR-C: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Duct bank | 196 | 36 |  |  |  |  | VD 1.4 %
G-P-0247 | G | Carbon capture | 480 V welding receptacle 4 |  | CCS MV switchgear building (VFDs) | STR-C | STR-C: stripper / regenerator (45 ft dia x 207 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Duct bank | 196 | 36 |  |  |  |  | VD 1.4 %
G-P-0248 | G | Carbon capture | Motor 1 of 4, 15 kW |  | CCS MV switchgear building (VFDs) |  | Solvent + NaOH storage | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 250 | 37 |  |  |  |  | VD 2.9 %
G-P-0249 | G | Carbon capture | Motor 2 of 4, 15 kW |  | CCS MV switchgear building (VFDs) |  | Solvent + NaOH storage | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 250 | 37 |  |  |  |  | VD 2.9 %
G-P-0250 | G | Carbon capture | Motor 3 of 4, 15 kW |  | CCS MV switchgear building (VFDs) |  | Solvent + NaOH storage | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 250 | 37 |  |  |  |  | VD 2.9 %
G-P-0251 | G | Carbon capture | Motor 4 of 4, 15 kW |  | CCS MV switchgear building (VFDs) |  | Solvent + NaOH storage | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 250 | 37 |  |  |  |  | VD 2.9 %
G-P-0252 | G | Carbon capture | Motor 1 of 2, 110 kW |  | CCS MV switchgear building (VFDs) |  | Water-wash pumps A | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦3/0 | 3/C+G | 3/0 | 1 | 1 | 480 | 110 | 155.7 | Tray | 465 | 96 |  |  |  |  | VD 2.7 %
G-P-0253 | G | Carbon capture | Motor 2 of 2, 110 kW |  | CCS MV switchgear building (VFDs) |  | Water-wash pumps A | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦3/0 | 3/C+G | 3/0 | 1 | 1 | 480 | 110 | 155.7 | Tray | 465 | 96 |  |  |  |  | VD 2.7 %
G-P-0254 | G | Carbon capture | Motor 1 of 2, 110 kW |  | CCS MV switchgear building (VFDs) |  | Water-wash pumps B | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦3/0 | 3/C+G | 3/0 | 1 | 1 | 480 | 110 | 155.7 | Tray | 305 | 96 |  |  |  |  | VD 1.9 %
G-P-0255 | G | Carbon capture | Motor 2 of 2, 110 kW |  | CCS MV switchgear building (VFDs) |  | Water-wash pumps B | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦3/0 | 3/C+G | 3/0 | 1 | 1 | 480 | 110 | 155.7 | Tray | 305 | 96 |  |  |  |  | VD 1.9 %
G-P-0256 | G | Carbon capture | Motor 1 of 2, 110 kW |  | CCS MV switchgear building (VFDs) |  | Water-wash pumps C | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦3/0 | 3/C+G | 3/0 | 1 | 1 | 480 | 110 | 155.7 | Tray | 145 | 96 |  |  |  |  | VD 1.1 %
G-P-0257 | G | Carbon capture | Motor 2 of 2, 110 kW |  | CCS MV switchgear building (VFDs) |  | Water-wash pumps C | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦3/0 | 3/C+G | 3/0 | 1 | 1 | 480 | 110 | 155.7 | Tray | 145 | 96 |  |  |  |  | VD 1.1 %
G-MV-0001 | G | Carbon capture | Booster fan BF-A (MV VFD output) |  | CCS MV switchgear building (VFDs) | BF-A | BF-A: booster fan (~16 MW) | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦750 | 1/C | 750 kcmil | 2 | 3 | 13800 | 16000 | 744 | Duct bank | 460 | 32 |  |  |  |  | ~16 MW per drawing
G-MV-0002 | G | Carbon capture | Booster fan BF-B (MV VFD output) |  | CCS MV switchgear building (VFDs) | BF-B | BF-B: booster fan (~16 MW) | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦750 | 1/C | 750 kcmil | 2 | 3 | 13800 | 16000 | 744 | Duct bank | 300 | 32 |  |  |  |  | ~16 MW per drawing
G-MV-0003 | G | Carbon capture | Booster fan BF-C (MV VFD output) |  | CCS MV switchgear building (VFDs) | BF-C | BF-C: booster fan (~16 MW) | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦750 | 1/C | 750 kcmil | 2 | 3 | 13800 | 16000 | 744 | Tray | 16 | 150 |  |  |  |  | ~16 MW per drawing
G-MV-0004 | G | Carbon capture | CCS T-1 secondary to CCS 13.8 kV switchgear | CCS T-1 | CCS T-1: 230/13.8 kV |  | CCS MV switchgear building (VFDs) | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦1000 | 1/C | 1000 kcmil | 5 | 3 | 13800 | 60000 | 2510 | Duct bank | 361 | 32 |  |  |  |  | 60 MVA (typ.)
G-MV-0005 | G | Carbon capture | CCS T-2 secondary to CCS 13.8 kV switchgear | CCS T-2 | CCS T-2: 230/13.8 kV |  | CCS MV switchgear building (VFDs) | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦1000 | 1/C | 1000 kcmil | 5 | 3 | 13800 | 60000 | 2510 | Duct bank | 409 | 32 |  |  |  |  | 60 MVA (typ.)
G-MV-0006 | G | Carbon capture | CO2 compressor train 1 |  | CCS MV switchgear building (VFDs) |  | CO2 compression 3 x ~19 MW + dehydration | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦750 | 1/C | 750 kcmil | 2 | 3 | 13800 | 19000 | 883 | Duct bank | 291 | 36 |  |  |  |  | ~19 MW per drawing
G-MV-0007 | G | Carbon capture | CO2 compressor train 2 |  | CCS MV switchgear building (VFDs) |  | CO2 compression 3 x ~19 MW + dehydration | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦750 | 1/C | 750 kcmil | 2 | 3 | 13800 | 19000 | 883 | Duct bank | 291 | 36 |  |  |  |  | ~19 MW per drawing
G-MV-0008 | G | Carbon capture | CO2 compressor train 3 |  | CCS MV switchgear building (VFDs) |  | CO2 compression 3 x ~19 MW + dehydration | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦750 | 1/C | 750 kcmil | 2 | 3 | 13800 | 19000 | 883 | Duct bank | 291 | 36 |  |  |  |  | ~19 MW per drawing
G-MV-0009 | G | Carbon capture | HP CO2 export compressor (conditional) |  | CCS MV switchgear building (VFDs) |  | CONDITIONAL: HP export compressor + metering | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦750 | 1/C | 750 kcmil | 1 | 3 | 13800 | 8000 | 372 | Duct bank | 303 | 34
G-MV-0010 | G | Carbon capture | CT MCC / VFD e-house transformer |  | CCS MV switchgear building (VFDs) |  | CT MCC / VFD e-house | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦1/0 | 1/C | 1/0 | 1 | 3 | 13800 | 3000 | 126 | Duct bank | 925 | 32
G-MV-0011 | G | Carbon capture | CT MCC / VFD e-house transformer |  | CCS MV switchgear building (VFDs) |  | CT MCC / VFD e-house | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦1/0 | 1/C | 1/0 | 1 | 3 | 13800 | 3000 | 126 | Duct bank | 925 | 32
G-MV-0012 | G | Carbon capture | CCS circulating-water pump 1 |  | CCS MV switchgear building (VFDs) |  | CCS circulating-water pumps | MV 5 kV | MV-105 5 kV 3/C Cu, EPR 133%, tape shield, gnd, PVC jacket | MV5¦3/C¦4/0 | 3/C | 4/0 | 1 | 1 | 4160 | 1200 | 185 | Duct bank | 925 | 72
G-MV-0013 | G | Carbon capture | CCS circulating-water pump 2 |  | CCS MV switchgear building (VFDs) |  | CCS circulating-water pumps | MV 5 kV | MV-105 5 kV 3/C Cu, EPR 133%, tape shield, gnd, PVC jacket | MV5¦3/C¦4/0 | 3/C | 4/0 | 1 | 1 | 4160 | 1200 | 185 | Duct bank | 925 | 72
G-MV-0014 | G | Carbon capture | CCS circulating-water pump 3 |  | CCS MV switchgear building (VFDs) |  | CCS circulating-water pumps | MV 5 kV | MV-105 5 kV 3/C Cu, EPR 133%, tape shield, gnd, PVC jacket | MV5¦3/C¦4/0 | 3/C | 4/0 | 1 | 1 | 4160 | 1200 | 185 | Duct bank | 925 | 72
G-MV-0015 | G | Carbon capture | CCS circulating-water pump 4 |  | CCS MV switchgear building (VFDs) |  | CCS circulating-water pumps | MV 5 kV | MV-105 5 kV 3/C Cu, EPR 133%, tape shield, gnd, PVC jacket | MV5¦3/C¦4/0 | 3/C | 4/0 | 1 | 1 | 4160 | 1200 | 185 | Duct bank | 925 | 72
G-MV-0016 | G | Carbon capture | Rich / lean amine pumps (A) |  | CCS MV switchgear building (VFDs) |  | Rich/lean pumps, cross exchanger, lean cooler A | MV 5 kV | MV-105 5 kV 3/C Cu, EPR 133%, tape shield, gnd, PVC jacket | MV5¦3/C¦2 | 3/C | 2 | 1 | 1 | 4160 | 450 | 69 | Tray | 465 | 112
G-MV-0017 | G | Carbon capture | Rich / lean amine pumps (A) |  | CCS MV switchgear building (VFDs) |  | Rich/lean pumps, cross exchanger, lean cooler A | MV 5 kV | MV-105 5 kV 3/C Cu, EPR 133%, tape shield, gnd, PVC jacket | MV5¦3/C¦2 | 3/C | 2 | 1 | 1 | 4160 | 450 | 69 | Tray | 465 | 112
G-MV-0018 | G | Carbon capture | Rich / lean amine pumps (B) |  | CCS MV switchgear building (VFDs) |  | Rich/lean pumps, cross exchanger, lean cooler B | MV 5 kV | MV-105 5 kV 3/C Cu, EPR 133%, tape shield, gnd, PVC jacket | MV5¦3/C¦2 | 3/C | 2 | 1 | 1 | 4160 | 450 | 69 | Tray | 305 | 112
G-MV-0019 | G | Carbon capture | Rich / lean amine pumps (B) |  | CCS MV switchgear building (VFDs) |  | Rich/lean pumps, cross exchanger, lean cooler B | MV 5 kV | MV-105 5 kV 3/C Cu, EPR 133%, tape shield, gnd, PVC jacket | MV5¦3/C¦2 | 3/C | 2 | 1 | 1 | 4160 | 450 | 69 | Tray | 305 | 112
G-MV-0020 | G | Carbon capture | Rich / lean amine pumps (C) |  | CCS MV switchgear building (VFDs) |  | Rich/lean pumps, cross exchanger, lean cooler C | MV 5 kV | MV-105 5 kV 3/C Cu, EPR 133%, tape shield, gnd, PVC jacket | MV5¦3/C¦2 | 3/C | 2 | 1 | 1 | 4160 | 450 | 69 | Duct bank | 0 | 69
G-MV-0021 | G | Carbon capture | Rich / lean amine pumps (C) |  | CCS MV switchgear building (VFDs) |  | Rich/lean pumps, cross exchanger, lean cooler C | MV 5 kV | MV-105 5 kV 3/C Cu, EPR 133%, tape shield, gnd, PVC jacket | MV5¦3/C¦2 | 3/C | 2 | 1 | 1 | 4160 | 450 | 69 | Duct bank | 0 | 69
H-L-0001 | H | BESS | Lighting, receptacles and small power branch circuits (allowance) |  | 34.5 kV collector e-house (arc-resistant) |  | 34.5 kV collector e-house (arc-resistant) | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | THHN¦1/C¦12 | 1/C | 12 | 1 | 1 | 277 |  |  | Conduit | 1280 | 0 |  |  |  |  | allowance: 1.6 ft of conductor per ft2 of floor
H-L-0002 | H | BESS | Lighting, receptacles and small power branch circuits (allowance) |  | BESS EMS / SCADA and revenue metering |  | BESS EMS / SCADA and revenue metering | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | THHN¦1/C¦12 | 1/C | 12 | 1 | 1 | 277 |  |  | Conduit | 384 | 0 |  |  |  |  | allowance: 1.6 ft of conductor per ft2 of floor
H-C-0001 | H | BESS | Control |  | BESS EMS / SCADA and revenue metering |  | 34.5 kV collector e-house (arc-resistant) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 68 | 37
H-C-0002 | H | BESS | Control |  | BESS EMS / SCADA and revenue metering |  | BESS EMS / SCADA and revenue metering | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 32
H-C-0003 | H | BESS | Motor 1 of 2: control / local station |  | BESS auxiliary transformer |  | BESS PCS / MV skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 318 | 103
H-C-0004 | H | BESS | Motor 2 of 2: control / local station |  | BESS auxiliary transformer |  | BESS PCS / MV skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 318 | 103
H-C-0005 | H | BESS | Motor 1 of 2: control / local station |  | BESS auxiliary transformer |  | BESS PCS / MV skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 178 | 123
H-C-0006 | H | BESS | Motor 2 of 2: control / local station |  | BESS auxiliary transformer |  | BESS PCS / MV skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 178 | 123
H-C-0007 | H | BESS | Motor 1 of 2: control / local station |  | BESS auxiliary transformer |  | BESS PCS / MV skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 74 | 107
H-C-0008 | H | BESS | Motor 2 of 2: control / local station |  | BESS auxiliary transformer |  | BESS PCS / MV skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 74 | 107
H-C-0009 | H | BESS | Motor 1 of 2: control / local station |  | BESS auxiliary transformer |  | BESS PCS / MV skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 318 | 161
H-C-0010 | H | BESS | Motor 2 of 2: control / local station |  | BESS auxiliary transformer |  | BESS PCS / MV skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 318 | 161
H-C-0011 | H | BESS | Motor 1 of 2: control / local station |  | BESS auxiliary transformer |  | BESS PCS / MV skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 178 | 181
H-C-0012 | H | BESS | Motor 2 of 2: control / local station |  | BESS auxiliary transformer |  | BESS PCS / MV skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 178 | 181
H-C-0013 | H | BESS | Motor 1 of 2: control / local station |  | BESS auxiliary transformer |  | BESS PCS / MV skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 74 | 165
H-C-0014 | H | BESS | Motor 2 of 2: control / local station |  | BESS auxiliary transformer |  | BESS PCS / MV skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 74 | 165
H-C-0015 | H | BESS | Motor 1 of 2: control / local station |  | BESS auxiliary transformer |  | BESS PCS / MV skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 318 | 219
H-C-0016 | H | BESS | Motor 2 of 2: control / local station |  | BESS auxiliary transformer |  | BESS PCS / MV skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 318 | 219
H-C-0017 | H | BESS | Motor 1 of 2: control / local station |  | BESS auxiliary transformer |  | BESS PCS / MV skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 178 | 239
H-C-0018 | H | BESS | Motor 2 of 2: control / local station |  | BESS auxiliary transformer |  | BESS PCS / MV skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 178 | 239
H-C-0019 | H | BESS | Motor 1 of 2: control / local station |  | BESS auxiliary transformer |  | BESS PCS / MV skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 380 | 149
H-C-0020 | H | BESS | Motor 2 of 2: control / local station |  | BESS auxiliary transformer |  | BESS PCS / MV skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 380 | 149
H-C-0021 | H | BESS | Motor 1 of 2: control / local station |  | BESS auxiliary transformer |  | BESS PCS / MV skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 620 | 91
H-C-0022 | H | BESS | Motor 2 of 2: control / local station |  | BESS auxiliary transformer |  | BESS PCS / MV skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 620 | 91
H-C-0023 | H | BESS | Motor 1 of 2: control / local station |  | BESS auxiliary transformer |  | BESS PCS / MV skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 500 | 91
H-C-0024 | H | BESS | Motor 2 of 2: control / local station |  | BESS auxiliary transformer |  | BESS PCS / MV skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 500 | 91
H-C-0025 | H | BESS | Motor 1 of 2: control / local station |  | BESS auxiliary transformer |  | BESS PCS / MV skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 380 | 91
H-C-0026 | H | BESS | Motor 2 of 2: control / local station |  | BESS auxiliary transformer |  | BESS PCS / MV skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 380 | 91
H-C-0027 | H | BESS | Motor 1 of 2: control / local station |  | BESS auxiliary transformer |  | BESS PCS / MV skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 620 | 37
H-C-0028 | H | BESS | Motor 2 of 2: control / local station |  | BESS auxiliary transformer |  | BESS PCS / MV skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 620 | 37
H-C-0029 | H | BESS | Motor 1 of 2: control / local station |  | BESS auxiliary transformer |  | BESS PCS / MV skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 500 | 37
H-C-0030 | H | BESS | Motor 2 of 2: control / local station |  | BESS auxiliary transformer |  | BESS PCS / MV skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 500 | 37
H-C-0031 | H | BESS | Motor 1 of 2: control / local station |  | BESS auxiliary transformer |  | BESS PCS / MV skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 380 | 37
H-C-0032 | H | BESS | Motor 2 of 2: control / local station |  | BESS auxiliary transformer |  | BESS PCS / MV skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 380 | 37
H-C-0033 | H | BESS | Control |  | BESS EMS / SCADA and revenue metering |  | BESS auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 38 | 32
H-C-0034 | H | BESS | Control |  | BESS EMS / SCADA and revenue metering |  | BESS auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 38 | 32
H-C-0035 | H | BESS | CT / VT |  | BESS EMS / SCADA and revenue metering |  | BESS auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 38 | 32
H-C-0036 | H | BESS | CT / VT |  | BESS EMS / SCADA and revenue metering |  | BESS auxiliary transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 38 | 32
H-C-0037 | H | BESS | Control |  | BESS EMS / SCADA and revenue metering | BESS | BESS blocks: 30 containers + 15 PCS / MV skids | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 336 | 32
H-C-0038 | H | BESS | Control |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 10 | 150
H-C-0039 | H | BESS | Control |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 160
H-C-0040 | H | BESS | Control |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 200
H-C-0041 | H | BESS | Control |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 200
H-C-0042 | H | BESS | Control |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 168
H-C-0043 | H | BESS | Control |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 168
H-C-0044 | H | BESS | Control |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 10 | 266
H-C-0045 | H | BESS | Control |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 276
H-C-0046 | H | BESS | Control |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 316
H-C-0047 | H | BESS | Control |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 316
H-C-0048 | H | BESS | Control |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 284
H-C-0049 | H | BESS | Control |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 284
H-C-0050 | H | BESS | Control |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 290
H-C-0051 | H | BESS | Control |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 290
H-C-0052 | H | BESS | Control |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 290
H-C-0053 | H | BESS | Control |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 290
H-C-0054 | H | BESS | Control |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 290
H-C-0055 | H | BESS | Control |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 290
H-C-0056 | H | BESS | Control |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 174
H-C-0057 | H | BESS | Control |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 174
H-C-0058 | H | BESS | Control |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 174
H-C-0059 | H | BESS | Control |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 174
H-C-0060 | H | BESS | Control |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 174
H-C-0061 | H | BESS | Control |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 174
H-C-0062 | H | BESS | Control |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 62
H-C-0063 | H | BESS | Control |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 62
H-C-0064 | H | BESS | Control |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 62
H-C-0065 | H | BESS | Control |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 62
H-C-0066 | H | BESS | Control |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 62
H-C-0067 | H | BESS | Control |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 62
H-C-0068 | H | BESS | Motor 1 of 6: control / local station |  | BESS auxiliary transformer | BESS MPT | BESS main power transformer 34.5/230 kV (to D4 upper) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 180 | 32
H-C-0069 | H | BESS | Motor 2 of 6: control / local station |  | BESS auxiliary transformer | BESS MPT | BESS main power transformer 34.5/230 kV (to D4 upper) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 180 | 32
H-C-0070 | H | BESS | Motor 3 of 6: control / local station |  | BESS auxiliary transformer | BESS MPT | BESS main power transformer 34.5/230 kV (to D4 upper) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 180 | 32
H-C-0071 | H | BESS | Motor 4 of 6: control / local station |  | BESS auxiliary transformer | BESS MPT | BESS main power transformer 34.5/230 kV (to D4 upper) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 180 | 32
H-C-0072 | H | BESS | Motor 5 of 6: control / local station |  | BESS auxiliary transformer | BESS MPT | BESS main power transformer 34.5/230 kV (to D4 upper) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 180 | 32
H-C-0073 | H | BESS | Motor 6 of 6: control / local station |  | BESS auxiliary transformer | BESS MPT | BESS main power transformer 34.5/230 kV (to D4 upper) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 180 | 32
H-C-0074 | H | BESS | Control |  | BESS EMS / SCADA and revenue metering | BESS MPT | BESS main power transformer 34.5/230 kV (to D4 upper) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 162 | 32
H-C-0075 | H | BESS | Control |  | BESS EMS / SCADA and revenue metering | BESS MPT | BESS main power transformer 34.5/230 kV (to D4 upper) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 162 | 32
H-C-0076 | H | BESS | CT / VT |  | BESS EMS / SCADA and revenue metering | BESS MPT | BESS main power transformer 34.5/230 kV (to D4 upper) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Duct bank | 162 | 32
H-C-0077 | H | BESS | CT / VT |  | BESS EMS / SCADA and revenue metering | BESS MPT | BESS main power transformer 34.5/230 kV (to D4 upper) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Duct bank | 162 | 32
H-C-0078 | H | BESS | Control |  | BESS EMS / SCADA and revenue metering |  | CONDITIONAL: grounding transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 280 | 87
H-C-0079 | H | BESS | Control |  | BESS EMS / SCADA and revenue metering |  | CONDITIONAL: grounding transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 280 | 87
H-C-0080 | H | BESS | CT / VT |  | BESS EMS / SCADA and revenue metering |  | CONDITIONAL: grounding transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Duct bank | 280 | 87
H-C-0081 | H | BESS | CT / VT |  | BESS EMS / SCADA and revenue metering |  | CONDITIONAL: grounding transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Duct bank | 280 | 87
H-DC-0001 | H | BESS | DC 1,500 V: container to PCS (2 x 1/C per pole pair) |  | BESS container (ISO 40 ft high cube) |  | BESS PCS / MV skid | DC 2 kV | PV / RHW-2 2 kV 1/C Cu, XLPE (DC) | PV¦1/C¦500 | 1/C | 500 kcmil | 4 | 2 | 1500 | 4000 |  | Duct bank | 10 | 150 |  |  |  |  | 4 sets of +/- per container (typ.)
H-DC-0002 | H | BESS | DC 1,500 V: container to PCS (2 x 1/C per pole pair) |  | BESS container (ISO 40 ft high cube) |  | BESS PCS / MV skid | DC 2 kV | PV / RHW-2 2 kV 1/C Cu, XLPE (DC) | PV¦1/C¦500 | 1/C | 500 kcmil | 4 | 2 | 1500 | 4000 |  | Tray | 0 | 160 |  |  |  |  | 4 sets of +/- per container (typ.)
H-DC-0003 | H | BESS | DC 1,500 V: container to PCS (2 x 1/C per pole pair) |  | BESS container (ISO 40 ft high cube) |  | BESS PCS / MV skid | DC 2 kV | PV / RHW-2 2 kV 1/C Cu, XLPE (DC) | PV¦1/C¦500 | 1/C | 500 kcmil | 4 | 2 | 1500 | 4000 |  | Tray | 0 | 200 |  |  |  |  | 4 sets of +/- per container (typ.)
H-DC-0004 | H | BESS | DC 1,500 V: container to PCS (2 x 1/C per pole pair) |  | BESS container (ISO 40 ft high cube) |  | BESS PCS / MV skid | DC 2 kV | PV / RHW-2 2 kV 1/C Cu, XLPE (DC) | PV¦1/C¦500 | 1/C | 500 kcmil | 4 | 2 | 1500 | 4000 |  | Tray | 0 | 200 |  |  |  |  | 4 sets of +/- per container (typ.)
H-DC-0005 | H | BESS | DC 1,500 V: container to PCS (2 x 1/C per pole pair) |  | BESS container (ISO 40 ft high cube) |  | BESS PCS / MV skid | DC 2 kV | PV / RHW-2 2 kV 1/C Cu, XLPE (DC) | PV¦1/C¦500 | 1/C | 500 kcmil | 4 | 2 | 1500 | 4000 |  | Tray | 0 | 168 |  |  |  |  | 4 sets of +/- per container (typ.)
H-DC-0006 | H | BESS | DC 1,500 V: container to PCS (2 x 1/C per pole pair) |  | BESS container (ISO 40 ft high cube) |  | BESS PCS / MV skid | DC 2 kV | PV / RHW-2 2 kV 1/C Cu, XLPE (DC) | PV¦1/C¦500 | 1/C | 500 kcmil | 4 | 2 | 1500 | 4000 |  | Duct bank | 10 | 158 |  |  |  |  | 4 sets of +/- per container (typ.)
H-DC-0007 | H | BESS | DC 1,500 V: container to PCS (2 x 1/C per pole pair) |  | BESS container (ISO 40 ft high cube) |  | BESS PCS / MV skid | DC 2 kV | PV / RHW-2 2 kV 1/C Cu, XLPE (DC) | PV¦1/C¦500 | 1/C | 500 kcmil | 4 | 2 | 1500 | 4000 |  | Duct bank | 10 | 266 |  |  |  |  | 4 sets of +/- per container (typ.)
H-DC-0008 | H | BESS | DC 1,500 V: container to PCS (2 x 1/C per pole pair) |  | BESS container (ISO 40 ft high cube) |  | BESS PCS / MV skid | DC 2 kV | PV / RHW-2 2 kV 1/C Cu, XLPE (DC) | PV¦1/C¦500 | 1/C | 500 kcmil | 4 | 2 | 1500 | 4000 |  | Tray | 0 | 276 |  |  |  |  | 4 sets of +/- per container (typ.)
H-DC-0009 | H | BESS | DC 1,500 V: container to PCS (2 x 1/C per pole pair) |  | BESS container (ISO 40 ft high cube) |  | BESS PCS / MV skid | DC 2 kV | PV / RHW-2 2 kV 1/C Cu, XLPE (DC) | PV¦1/C¦500 | 1/C | 500 kcmil | 4 | 2 | 1500 | 4000 |  | Tray | 0 | 316 |  |  |  |  | 4 sets of +/- per container (typ.)
H-DC-0010 | H | BESS | DC 1,500 V: container to PCS (2 x 1/C per pole pair) |  | BESS container (ISO 40 ft high cube) |  | BESS PCS / MV skid | DC 2 kV | PV / RHW-2 2 kV 1/C Cu, XLPE (DC) | PV¦1/C¦500 | 1/C | 500 kcmil | 4 | 2 | 1500 | 4000 |  | Tray | 0 | 316 |  |  |  |  | 4 sets of +/- per container (typ.)
H-DC-0011 | H | BESS | DC 1,500 V: container to PCS (2 x 1/C per pole pair) |  | BESS container (ISO 40 ft high cube) |  | BESS PCS / MV skid | DC 2 kV | PV / RHW-2 2 kV 1/C Cu, XLPE (DC) | PV¦1/C¦500 | 1/C | 500 kcmil | 4 | 2 | 1500 | 4000 |  | Tray | 0 | 284 |  |  |  |  | 4 sets of +/- per container (typ.)
H-DC-0012 | H | BESS | DC 1,500 V: container to PCS (2 x 1/C per pole pair) |  | BESS container (ISO 40 ft high cube) |  | BESS PCS / MV skid | DC 2 kV | PV / RHW-2 2 kV 1/C Cu, XLPE (DC) | PV¦1/C¦500 | 1/C | 500 kcmil | 4 | 2 | 1500 | 4000 |  | Duct bank | 10 | 274 |  |  |  |  | 4 sets of +/- per container (typ.)
H-DC-0013 | H | BESS | DC 1,500 V: container to PCS (2 x 1/C per pole pair) |  | BESS container (ISO 40 ft high cube) |  | BESS PCS / MV skid | DC 2 kV | PV / RHW-2 2 kV 1/C Cu, XLPE (DC) | PV¦1/C¦500 | 1/C | 500 kcmil | 4 | 2 | 1500 | 4000 |  | Tray | 0 | 290 |  |  |  |  | 4 sets of +/- per container (typ.)
H-DC-0014 | H | BESS | DC 1,500 V: container to PCS (2 x 1/C per pole pair) |  | BESS container (ISO 40 ft high cube) |  | BESS PCS / MV skid | DC 2 kV | PV / RHW-2 2 kV 1/C Cu, XLPE (DC) | PV¦1/C¦500 | 1/C | 500 kcmil | 4 | 2 | 1500 | 4000 |  | Tray | 0 | 290 |  |  |  |  | 4 sets of +/- per container (typ.)
H-DC-0015 | H | BESS | DC 1,500 V: container to PCS (2 x 1/C per pole pair) |  | BESS container (ISO 40 ft high cube) |  | BESS PCS / MV skid | DC 2 kV | PV / RHW-2 2 kV 1/C Cu, XLPE (DC) | PV¦1/C¦500 | 1/C | 500 kcmil | 4 | 2 | 1500 | 4000 |  | Tray | 0 | 290 |  |  |  |  | 4 sets of +/- per container (typ.)
H-DC-0016 | H | BESS | DC 1,500 V: container to PCS (2 x 1/C per pole pair) |  | BESS container (ISO 40 ft high cube) |  | BESS PCS / MV skid | DC 2 kV | PV / RHW-2 2 kV 1/C Cu, XLPE (DC) | PV¦1/C¦500 | 1/C | 500 kcmil | 4 | 2 | 1500 | 4000 |  | Tray | 0 | 290 |  |  |  |  | 4 sets of +/- per container (typ.)
H-DC-0017 | H | BESS | DC 1,500 V: container to PCS (2 x 1/C per pole pair) |  | BESS container (ISO 40 ft high cube) |  | BESS PCS / MV skid | DC 2 kV | PV / RHW-2 2 kV 1/C Cu, XLPE (DC) | PV¦1/C¦500 | 1/C | 500 kcmil | 4 | 2 | 1500 | 4000 |  | Tray | 0 | 290 |  |  |  |  | 4 sets of +/- per container (typ.)
H-DC-0018 | H | BESS | DC 1,500 V: container to PCS (2 x 1/C per pole pair) |  | BESS container (ISO 40 ft high cube) |  | BESS PCS / MV skid | DC 2 kV | PV / RHW-2 2 kV 1/C Cu, XLPE (DC) | PV¦1/C¦500 | 1/C | 500 kcmil | 4 | 2 | 1500 | 4000 |  | Tray | 27 | 263 |  |  |  |  | 4 sets of +/- per container (typ.)
H-DC-0019 | H | BESS | DC 1,500 V: container to PCS (2 x 1/C per pole pair) |  | BESS container (ISO 40 ft high cube) |  | BESS PCS / MV skid | DC 2 kV | PV / RHW-2 2 kV 1/C Cu, XLPE (DC) | PV¦1/C¦500 | 1/C | 500 kcmil | 4 | 2 | 1500 | 4000 |  | Tray | 0 | 174 |  |  |  |  | 4 sets of +/- per container (typ.)
H-DC-0020 | H | BESS | DC 1,500 V: container to PCS (2 x 1/C per pole pair) |  | BESS container (ISO 40 ft high cube) |  | BESS PCS / MV skid | DC 2 kV | PV / RHW-2 2 kV 1/C Cu, XLPE (DC) | PV¦1/C¦500 | 1/C | 500 kcmil | 4 | 2 | 1500 | 4000 |  | Tray | 0 | 174 |  |  |  |  | 4 sets of +/- per container (typ.)
H-DC-0021 | H | BESS | DC 1,500 V: container to PCS (2 x 1/C per pole pair) |  | BESS container (ISO 40 ft high cube) |  | BESS PCS / MV skid | DC 2 kV | PV / RHW-2 2 kV 1/C Cu, XLPE (DC) | PV¦1/C¦500 | 1/C | 500 kcmil | 4 | 2 | 1500 | 4000 |  | Tray | 0 | 174 |  |  |  |  | 4 sets of +/- per container (typ.)
H-DC-0022 | H | BESS | DC 1,500 V: container to PCS (2 x 1/C per pole pair) |  | BESS container (ISO 40 ft high cube) |  | BESS PCS / MV skid | DC 2 kV | PV / RHW-2 2 kV 1/C Cu, XLPE (DC) | PV¦1/C¦500 | 1/C | 500 kcmil | 4 | 2 | 1500 | 4000 |  | Tray | 0 | 174 |  |  |  |  | 4 sets of +/- per container (typ.)
H-DC-0023 | H | BESS | DC 1,500 V: container to PCS (2 x 1/C per pole pair) |  | BESS container (ISO 40 ft high cube) |  | BESS PCS / MV skid | DC 2 kV | PV / RHW-2 2 kV 1/C Cu, XLPE (DC) | PV¦1/C¦500 | 1/C | 500 kcmil | 4 | 2 | 1500 | 4000 |  | Tray | 0 | 174 |  |  |  |  | 4 sets of +/- per container (typ.)
H-DC-0024 | H | BESS | DC 1,500 V: container to PCS (2 x 1/C per pole pair) |  | BESS container (ISO 40 ft high cube) |  | BESS PCS / MV skid | DC 2 kV | PV / RHW-2 2 kV 1/C Cu, XLPE (DC) | PV¦1/C¦500 | 1/C | 500 kcmil | 4 | 2 | 1500 | 4000 |  | Tray | 0 | 174 |  |  |  |  | 4 sets of +/- per container (typ.)
H-DC-0025 | H | BESS | DC 1,500 V: container to PCS (2 x 1/C per pole pair) |  | BESS container (ISO 40 ft high cube) |  | BESS PCS / MV skid | DC 2 kV | PV / RHW-2 2 kV 1/C Cu, XLPE (DC) | PV¦1/C¦500 | 1/C | 500 kcmil | 4 | 2 | 1500 | 4000 |  | Tray | 0 | 62 |  |  |  |  | 4 sets of +/- per container (typ.)
H-DC-0026 | H | BESS | DC 1,500 V: container to PCS (2 x 1/C per pole pair) |  | BESS container (ISO 40 ft high cube) |  | BESS PCS / MV skid | DC 2 kV | PV / RHW-2 2 kV 1/C Cu, XLPE (DC) | PV¦1/C¦500 | 1/C | 500 kcmil | 4 | 2 | 1500 | 4000 |  | Tray | 0 | 62 |  |  |  |  | 4 sets of +/- per container (typ.)
H-DC-0027 | H | BESS | DC 1,500 V: container to PCS (2 x 1/C per pole pair) |  | BESS container (ISO 40 ft high cube) |  | BESS PCS / MV skid | DC 2 kV | PV / RHW-2 2 kV 1/C Cu, XLPE (DC) | PV¦1/C¦500 | 1/C | 500 kcmil | 4 | 2 | 1500 | 4000 |  | Tray | 0 | 62 |  |  |  |  | 4 sets of +/- per container (typ.)
H-DC-0028 | H | BESS | DC 1,500 V: container to PCS (2 x 1/C per pole pair) |  | BESS container (ISO 40 ft high cube) |  | BESS PCS / MV skid | DC 2 kV | PV / RHW-2 2 kV 1/C Cu, XLPE (DC) | PV¦1/C¦500 | 1/C | 500 kcmil | 4 | 2 | 1500 | 4000 |  | Tray | 0 | 62 |  |  |  |  | 4 sets of +/- per container (typ.)
H-DC-0029 | H | BESS | DC 1,500 V: container to PCS (2 x 1/C per pole pair) |  | BESS container (ISO 40 ft high cube) |  | BESS PCS / MV skid | DC 2 kV | PV / RHW-2 2 kV 1/C Cu, XLPE (DC) | PV¦1/C¦500 | 1/C | 500 kcmil | 4 | 2 | 1500 | 4000 |  | Tray | 0 | 62 |  |  |  |  | 4 sets of +/- per container (typ.)
H-DC-0030 | H | BESS | DC 1,500 V: container to PCS (2 x 1/C per pole pair) |  | BESS container (ISO 40 ft high cube) |  | BESS PCS / MV skid | DC 2 kV | PV / RHW-2 2 kV 1/C Cu, XLPE (DC) | PV¦1/C¦500 | 1/C | 500 kcmil | 4 | 2 | 1500 | 4000 |  | Tray | 0 | 62 |  |  |  |  | 4 sets of +/- per container (typ.)
H-F-0001 | H | BESS | Plant network / DCS fibre | CR | Control / admin building (main control room) |  | 34.5 kV collector e-house (arc-resistant) | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Trench | 2496 | 36
H-F-0002 | H | BESS | Plant network / DCS fibre | CR | Control / admin building (main control room) |  | BESS EMS / SCADA and revenue metering | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Trench | 2583 | 76
H-FA-0001 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering |  | 34.5 kV collector e-house (arc-resistant) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 68 | 37
H-FA-0002 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering |  | BESS EMS / SCADA and revenue metering | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 32
H-FA-0003 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering | BESS | BESS blocks: 30 containers + 15 PCS / MV skids | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 336 | 32
H-FA-0004 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering |  | BESS container (ISO 40 ft high cube) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 300 | 89
H-FA-0005 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering |  | BESS container (ISO 40 ft high cube) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 160 | 169
H-FA-0006 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering |  | BESS container (ISO 40 ft high cube) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 160 | 109
H-FA-0007 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering |  | BESS container (ISO 40 ft high cube) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 70 | 139
H-FA-0008 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering |  | BESS container (ISO 40 ft high cube) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 30 | 93
H-FA-0009 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering |  | BESS container (ISO 40 ft high cube) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 83
H-FA-0010 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering |  | BESS container (ISO 40 ft high cube) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 300 | 147
H-FA-0011 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering |  | BESS container (ISO 40 ft high cube) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 160 | 227
H-FA-0012 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering |  | BESS container (ISO 40 ft high cube) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 160 | 167
H-FA-0013 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering |  | BESS container (ISO 40 ft high cube) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 30 | 211
H-FA-0014 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering |  | BESS container (ISO 40 ft high cube) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 30 | 151
H-FA-0015 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering |  | BESS container (ISO 40 ft high cube) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 141
H-FA-0016 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering |  | BESS container (ISO 40 ft high cube) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 300 | 205
H-FA-0017 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering |  | BESS container (ISO 40 ft high cube) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 300 | 205
H-FA-0018 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering |  | BESS container (ISO 40 ft high cube) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 160 | 225
H-FA-0019 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering |  | BESS container (ISO 40 ft high cube) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 160 | 225
H-FA-0020 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering |  | BESS container (ISO 40 ft high cube) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 30 | 209
H-FA-0021 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering |  | BESS container (ISO 40 ft high cube) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 336 | 173
H-FA-0022 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering |  | BESS container (ISO 40 ft high cube) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 340 | 253
H-FA-0023 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering |  | BESS container (ISO 40 ft high cube) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 300 | 263
H-FA-0024 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering |  | BESS container (ISO 40 ft high cube) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 160 | 283
H-FA-0025 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering |  | BESS container (ISO 40 ft high cube) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 160 | 283
H-FA-0026 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering |  | BESS container (ISO 40 ft high cube) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 336 | 115
H-FA-0027 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering |  | BESS container (ISO 40 ft high cube) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 336 | 115
H-FA-0028 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering |  | BESS container (ISO 40 ft high cube) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 602 | 57
H-FA-0029 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering |  | BESS container (ISO 40 ft high cube) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 482 | 117
H-FA-0030 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering |  | BESS container (ISO 40 ft high cube) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 336 | 177
H-FA-0031 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering |  | BESS container (ISO 40 ft high cube) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 336 | 117
H-FA-0032 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering |  | BESS container (ISO 40 ft high cube) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 336 | 57
H-FA-0033 | H | BESS | Fire alarm / F&G loop (to the local FACP / F&G node) |  | BESS EMS / SCADA and revenue metering |  | BESS container (ISO 40 ft high cube) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 336 | 57
H-I-0001 | H | BESS | Analog instrument to JB JB-BESS PCS / MV skid-AI01: 6 x 1 pr (field cables) |  | BESS PCS / MV skid | JB-BESS PCS / MV skid-AI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0002 | H | BESS | Home run JB-BESS PCS / MV skid-AI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS PCS / MV skid-AI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 300 | 103
H-I-0003 | H | BESS | Discrete device to JB JB-BESS PCS / MV skid-DI01: 10 x 1 pr (field cables) |  | BESS PCS / MV skid | JB-BESS PCS / MV skid-DI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0004 | H | BESS | Home run JB-BESS PCS / MV skid-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS PCS / MV skid-DI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 300 | 103
H-I-0005 | H | BESS | Analog instrument to JB JB-BESS PCS / MV skid-AI01: 6 x 1 pr (field cables) |  | BESS PCS / MV skid | JB-BESS PCS / MV skid-AI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0006 | H | BESS | Home run JB-BESS PCS / MV skid-AI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS PCS / MV skid-AI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 160 | 123
H-I-0007 | H | BESS | Discrete device to JB JB-BESS PCS / MV skid-DI01: 10 x 1 pr (field cables) |  | BESS PCS / MV skid | JB-BESS PCS / MV skid-DI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0008 | H | BESS | Home run JB-BESS PCS / MV skid-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS PCS / MV skid-DI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 160 | 123
H-I-0009 | H | BESS | Analog instrument to JB JB-BESS PCS / MV skid-AI01: 6 x 1 pr (field cables) |  | BESS PCS / MV skid | JB-BESS PCS / MV skid-AI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0010 | H | BESS | Home run JB-BESS PCS / MV skid-AI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS PCS / MV skid-AI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 30 | 107
H-I-0011 | H | BESS | Discrete device to JB JB-BESS PCS / MV skid-DI01: 10 x 1 pr (field cables) |  | BESS PCS / MV skid | JB-BESS PCS / MV skid-DI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0012 | H | BESS | Home run JB-BESS PCS / MV skid-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS PCS / MV skid-DI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 30 | 107
H-I-0013 | H | BESS | Analog instrument to JB JB-BESS PCS / MV skid-AI01: 6 x 1 pr (field cables) |  | BESS PCS / MV skid | JB-BESS PCS / MV skid-AI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0014 | H | BESS | Home run JB-BESS PCS / MV skid-AI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS PCS / MV skid-AI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 300 | 161
H-I-0015 | H | BESS | Discrete device to JB JB-BESS PCS / MV skid-DI01: 10 x 1 pr (field cables) |  | BESS PCS / MV skid | JB-BESS PCS / MV skid-DI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0016 | H | BESS | Home run JB-BESS PCS / MV skid-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS PCS / MV skid-DI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 300 | 161
H-I-0017 | H | BESS | Analog instrument to JB JB-BESS PCS / MV skid-AI01: 6 x 1 pr (field cables) |  | BESS PCS / MV skid | JB-BESS PCS / MV skid-AI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0018 | H | BESS | Home run JB-BESS PCS / MV skid-AI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS PCS / MV skid-AI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 160 | 181
H-I-0019 | H | BESS | Discrete device to JB JB-BESS PCS / MV skid-DI01: 10 x 1 pr (field cables) |  | BESS PCS / MV skid | JB-BESS PCS / MV skid-DI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0020 | H | BESS | Home run JB-BESS PCS / MV skid-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS PCS / MV skid-DI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 160 | 181
H-I-0021 | H | BESS | Analog instrument to JB JB-BESS PCS / MV skid-AI01: 6 x 1 pr (field cables) |  | BESS PCS / MV skid | JB-BESS PCS / MV skid-AI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0022 | H | BESS | Home run JB-BESS PCS / MV skid-AI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS PCS / MV skid-AI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 30 | 165
H-I-0023 | H | BESS | Discrete device to JB JB-BESS PCS / MV skid-DI01: 10 x 1 pr (field cables) |  | BESS PCS / MV skid | JB-BESS PCS / MV skid-DI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0024 | H | BESS | Home run JB-BESS PCS / MV skid-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS PCS / MV skid-DI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 30 | 165
H-I-0025 | H | BESS | Analog instrument to JB JB-BESS PCS / MV skid-AI01: 6 x 1 pr (field cables) |  | BESS PCS / MV skid | JB-BESS PCS / MV skid-AI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0026 | H | BESS | Home run JB-BESS PCS / MV skid-AI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS PCS / MV skid-AI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 300 | 219
H-I-0027 | H | BESS | Discrete device to JB JB-BESS PCS / MV skid-DI01: 10 x 1 pr (field cables) |  | BESS PCS / MV skid | JB-BESS PCS / MV skid-DI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0028 | H | BESS | Home run JB-BESS PCS / MV skid-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS PCS / MV skid-DI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 300 | 219
H-I-0029 | H | BESS | Analog instrument to JB JB-BESS PCS / MV skid-AI01: 6 x 1 pr (field cables) |  | BESS PCS / MV skid | JB-BESS PCS / MV skid-AI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0030 | H | BESS | Home run JB-BESS PCS / MV skid-AI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS PCS / MV skid-AI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 160 | 239
H-I-0031 | H | BESS | Discrete device to JB JB-BESS PCS / MV skid-DI01: 10 x 1 pr (field cables) |  | BESS PCS / MV skid | JB-BESS PCS / MV skid-DI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0032 | H | BESS | Home run JB-BESS PCS / MV skid-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS PCS / MV skid-DI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 160 | 239
H-I-0033 | H | BESS | Analog instrument to JB JB-BESS PCS / MV skid-AI01: 6 x 1 pr (field cables) |  | BESS PCS / MV skid | JB-BESS PCS / MV skid-AI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0034 | H | BESS | Home run JB-BESS PCS / MV skid-AI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS PCS / MV skid-AI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 336 | 149
H-I-0035 | H | BESS | Discrete device to JB JB-BESS PCS / MV skid-DI01: 10 x 1 pr (field cables) |  | BESS PCS / MV skid | JB-BESS PCS / MV skid-DI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0036 | H | BESS | Home run JB-BESS PCS / MV skid-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS PCS / MV skid-DI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 336 | 149
H-I-0037 | H | BESS | Analog instrument to JB JB-BESS PCS / MV skid-AI01: 6 x 1 pr (field cables) |  | BESS PCS / MV skid | JB-BESS PCS / MV skid-AI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0038 | H | BESS | Home run JB-BESS PCS / MV skid-AI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS PCS / MV skid-AI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 602 | 91
H-I-0039 | H | BESS | Discrete device to JB JB-BESS PCS / MV skid-DI01: 10 x 1 pr (field cables) |  | BESS PCS / MV skid | JB-BESS PCS / MV skid-DI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0040 | H | BESS | Home run JB-BESS PCS / MV skid-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS PCS / MV skid-DI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 602 | 91
H-I-0041 | H | BESS | Analog instrument to JB JB-BESS PCS / MV skid-AI01: 6 x 1 pr (field cables) |  | BESS PCS / MV skid | JB-BESS PCS / MV skid-AI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0042 | H | BESS | Home run JB-BESS PCS / MV skid-AI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS PCS / MV skid-AI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 336 | 211
H-I-0043 | H | BESS | Discrete device to JB JB-BESS PCS / MV skid-DI01: 10 x 1 pr (field cables) |  | BESS PCS / MV skid | JB-BESS PCS / MV skid-DI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0044 | H | BESS | Home run JB-BESS PCS / MV skid-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS PCS / MV skid-DI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 336 | 211
H-I-0045 | H | BESS | Analog instrument to JB JB-BESS PCS / MV skid-AI01: 6 x 1 pr (field cables) |  | BESS PCS / MV skid | JB-BESS PCS / MV skid-AI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0046 | H | BESS | Home run JB-BESS PCS / MV skid-AI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS PCS / MV skid-AI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 336 | 91
H-I-0047 | H | BESS | Discrete device to JB JB-BESS PCS / MV skid-DI01: 10 x 1 pr (field cables) |  | BESS PCS / MV skid | JB-BESS PCS / MV skid-DI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0048 | H | BESS | Home run JB-BESS PCS / MV skid-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS PCS / MV skid-DI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 336 | 91
H-I-0049 | H | BESS | Analog instrument to JB JB-BESS PCS / MV skid-AI01: 6 x 1 pr (field cables) |  | BESS PCS / MV skid | JB-BESS PCS / MV skid-AI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0050 | H | BESS | Home run JB-BESS PCS / MV skid-AI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS PCS / MV skid-AI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 602 | 37
H-I-0051 | H | BESS | Discrete device to JB JB-BESS PCS / MV skid-DI01: 10 x 1 pr (field cables) |  | BESS PCS / MV skid | JB-BESS PCS / MV skid-DI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0052 | H | BESS | Home run JB-BESS PCS / MV skid-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS PCS / MV skid-DI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 602 | 37
H-I-0053 | H | BESS | Analog instrument to JB JB-BESS PCS / MV skid-AI01: 6 x 1 pr (field cables) |  | BESS PCS / MV skid | JB-BESS PCS / MV skid-AI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0054 | H | BESS | Home run JB-BESS PCS / MV skid-AI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS PCS / MV skid-AI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 336 | 157
H-I-0055 | H | BESS | Discrete device to JB JB-BESS PCS / MV skid-DI01: 10 x 1 pr (field cables) |  | BESS PCS / MV skid | JB-BESS PCS / MV skid-DI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0056 | H | BESS | Home run JB-BESS PCS / MV skid-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS PCS / MV skid-DI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 336 | 157
H-I-0057 | H | BESS | Analog instrument to JB JB-BESS PCS / MV skid-AI01: 6 x 1 pr (field cables) |  | BESS PCS / MV skid | JB-BESS PCS / MV skid-AI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0058 | H | BESS | Home run JB-BESS PCS / MV skid-AI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS PCS / MV skid-AI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 336 | 37
H-I-0059 | H | BESS | Discrete device to JB JB-BESS PCS / MV skid-DI01: 10 x 1 pr (field cables) |  | BESS PCS / MV skid | JB-BESS PCS / MV skid-DI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 43 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0060 | H | BESS | Home run JB-BESS PCS / MV skid-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS PCS / MV skid-DI01 | BESS PCS / MV skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 336 | 37
H-I-0061 | H | BESS | Instrumentation |  | BESS EMS / SCADA and revenue metering |  | BESS auxiliary transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 38 | 32
H-I-0062 | H | BESS | Instrumentation |  | BESS EMS / SCADA and revenue metering | BESS | BESS blocks: 30 containers + 15 PCS / MV skids | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Duct bank | 336 | 32
H-I-0063 | H | BESS | Instrumentation |  | BESS EMS / SCADA and revenue metering | BESS | BESS blocks: 30 containers + 15 PCS / MV skids | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Duct bank | 336 | 32
H-I-0064 | H | BESS | Thermocouples |  | BESS EMS / SCADA and revenue metering | BESS | BESS blocks: 30 containers + 15 PCS / MV skids | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦12 pr¦16 | 12 pr | 16 | 1 | 1 |  |  |  | Duct bank | 336 | 32
H-I-0065 | H | BESS | Thermocouples |  | BESS EMS / SCADA and revenue metering | BESS | BESS blocks: 30 containers + 15 PCS / MV skids | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦12 pr¦16 | 12 pr | 16 | 1 | 1 |  |  |  | Duct bank | 336 | 32
H-I-0066 | H | BESS | Instrumentation |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Duct bank | 10 | 150
H-I-0067 | H | BESS | Instrumentation |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 160
H-I-0068 | H | BESS | Instrumentation |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 200
H-I-0069 | H | BESS | Instrumentation |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 200
H-I-0070 | H | BESS | Instrumentation |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 168
H-I-0071 | H | BESS | Instrumentation |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 168
H-I-0072 | H | BESS | Instrumentation |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Duct bank | 10 | 266
H-I-0073 | H | BESS | Instrumentation |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 276
H-I-0074 | H | BESS | Instrumentation |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 316
H-I-0075 | H | BESS | Instrumentation |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 316
H-I-0076 | H | BESS | Instrumentation |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 284
H-I-0077 | H | BESS | Instrumentation |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 284
H-I-0078 | H | BESS | Instrumentation |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 290
H-I-0079 | H | BESS | Instrumentation |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 290
H-I-0080 | H | BESS | Instrumentation |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 290
H-I-0081 | H | BESS | Instrumentation |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 290
H-I-0082 | H | BESS | Instrumentation |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 290
H-I-0083 | H | BESS | Instrumentation |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 290
H-I-0084 | H | BESS | Instrumentation |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 174
H-I-0085 | H | BESS | Instrumentation |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 174
H-I-0086 | H | BESS | Instrumentation |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 174
H-I-0087 | H | BESS | Instrumentation |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 174
H-I-0088 | H | BESS | Instrumentation |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 174
H-I-0089 | H | BESS | Instrumentation |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 174
H-I-0090 | H | BESS | Instrumentation |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 62
H-I-0091 | H | BESS | Instrumentation |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 62
H-I-0092 | H | BESS | Instrumentation |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 62
H-I-0093 | H | BESS | Instrumentation |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 62
H-I-0094 | H | BESS | Instrumentation |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 62
H-I-0095 | H | BESS | Instrumentation |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 62
H-I-0096 | H | BESS | Discrete device to JB JB-BESS container (IS-DI01: 8 x 1 pr (field cables) |  | BESS container (ISO 40 ft high cube) | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0097 | H | BESS | Home run JB-BESS container (IS-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 300 | 89
H-I-0098 | H | BESS | Discrete device to JB JB-BESS container (IS-DI01: 8 x 1 pr (field cables) |  | BESS container (ISO 40 ft high cube) | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0099 | H | BESS | Home run JB-BESS container (IS-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 160 | 169
H-I-0100 | H | BESS | Discrete device to JB JB-BESS container (IS-DI01: 8 x 1 pr (field cables) |  | BESS container (ISO 40 ft high cube) | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0101 | H | BESS | Home run JB-BESS container (IS-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 160 | 109
H-I-0102 | H | BESS | Discrete device to JB JB-BESS container (IS-DI01: 8 x 1 pr (field cables) |  | BESS container (ISO 40 ft high cube) | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0103 | H | BESS | Home run JB-BESS container (IS-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 70 | 139
H-I-0104 | H | BESS | Discrete device to JB JB-BESS container (IS-DI01: 8 x 1 pr (field cables) |  | BESS container (ISO 40 ft high cube) | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0105 | H | BESS | Home run JB-BESS container (IS-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 30 | 93
H-I-0106 | H | BESS | Discrete device to JB JB-BESS container (IS-DI01: 8 x 1 pr (field cables) |  | BESS container (ISO 40 ft high cube) | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0107 | H | BESS | Home run JB-BESS container (IS-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 83
H-I-0108 | H | BESS | Discrete device to JB JB-BESS container (IS-DI01: 8 x 1 pr (field cables) |  | BESS container (ISO 40 ft high cube) | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0109 | H | BESS | Home run JB-BESS container (IS-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 300 | 147
H-I-0110 | H | BESS | Discrete device to JB JB-BESS container (IS-DI01: 8 x 1 pr (field cables) |  | BESS container (ISO 40 ft high cube) | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0111 | H | BESS | Home run JB-BESS container (IS-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 160 | 227
H-I-0112 | H | BESS | Discrete device to JB JB-BESS container (IS-DI01: 8 x 1 pr (field cables) |  | BESS container (ISO 40 ft high cube) | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0113 | H | BESS | Home run JB-BESS container (IS-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 160 | 167
H-I-0114 | H | BESS | Discrete device to JB JB-BESS container (IS-DI01: 8 x 1 pr (field cables) |  | BESS container (ISO 40 ft high cube) | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0115 | H | BESS | Home run JB-BESS container (IS-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 30 | 211
H-I-0116 | H | BESS | Discrete device to JB JB-BESS container (IS-DI01: 8 x 1 pr (field cables) |  | BESS container (ISO 40 ft high cube) | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0117 | H | BESS | Home run JB-BESS container (IS-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 30 | 151
H-I-0118 | H | BESS | Discrete device to JB JB-BESS container (IS-DI01: 8 x 1 pr (field cables) |  | BESS container (ISO 40 ft high cube) | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0119 | H | BESS | Home run JB-BESS container (IS-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 141
H-I-0120 | H | BESS | Discrete device to JB JB-BESS container (IS-DI01: 8 x 1 pr (field cables) |  | BESS container (ISO 40 ft high cube) | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0121 | H | BESS | Home run JB-BESS container (IS-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 300 | 205
H-I-0122 | H | BESS | Discrete device to JB JB-BESS container (IS-DI01: 8 x 1 pr (field cables) |  | BESS container (ISO 40 ft high cube) | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0123 | H | BESS | Home run JB-BESS container (IS-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 300 | 205
H-I-0124 | H | BESS | Discrete device to JB JB-BESS container (IS-DI01: 8 x 1 pr (field cables) |  | BESS container (ISO 40 ft high cube) | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0125 | H | BESS | Home run JB-BESS container (IS-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 160 | 225
H-I-0126 | H | BESS | Discrete device to JB JB-BESS container (IS-DI01: 8 x 1 pr (field cables) |  | BESS container (ISO 40 ft high cube) | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0127 | H | BESS | Home run JB-BESS container (IS-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 160 | 225
H-I-0128 | H | BESS | Discrete device to JB JB-BESS container (IS-DI01: 8 x 1 pr (field cables) |  | BESS container (ISO 40 ft high cube) | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0129 | H | BESS | Home run JB-BESS container (IS-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 30 | 209
H-I-0130 | H | BESS | Discrete device to JB JB-BESS container (IS-DI01: 8 x 1 pr (field cables) |  | BESS container (ISO 40 ft high cube) | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0131 | H | BESS | Home run JB-BESS container (IS-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 336 | 173
H-I-0132 | H | BESS | Discrete device to JB JB-BESS container (IS-DI01: 8 x 1 pr (field cables) |  | BESS container (ISO 40 ft high cube) | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0133 | H | BESS | Home run JB-BESS container (IS-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 340 | 253
H-I-0134 | H | BESS | Discrete device to JB JB-BESS container (IS-DI01: 8 x 1 pr (field cables) |  | BESS container (ISO 40 ft high cube) | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0135 | H | BESS | Home run JB-BESS container (IS-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 300 | 263
H-I-0136 | H | BESS | Discrete device to JB JB-BESS container (IS-DI01: 8 x 1 pr (field cables) |  | BESS container (ISO 40 ft high cube) | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0137 | H | BESS | Home run JB-BESS container (IS-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 160 | 283
H-I-0138 | H | BESS | Discrete device to JB JB-BESS container (IS-DI01: 8 x 1 pr (field cables) |  | BESS container (ISO 40 ft high cube) | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0139 | H | BESS | Home run JB-BESS container (IS-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 160 | 283
H-I-0140 | H | BESS | Discrete device to JB JB-BESS container (IS-DI01: 8 x 1 pr (field cables) |  | BESS container (ISO 40 ft high cube) | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0141 | H | BESS | Home run JB-BESS container (IS-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 336 | 115
H-I-0142 | H | BESS | Discrete device to JB JB-BESS container (IS-DI01: 8 x 1 pr (field cables) |  | BESS container (ISO 40 ft high cube) | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0143 | H | BESS | Home run JB-BESS container (IS-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 336 | 115
H-I-0144 | H | BESS | Discrete device to JB JB-BESS container (IS-DI01: 8 x 1 pr (field cables) |  | BESS container (ISO 40 ft high cube) | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0145 | H | BESS | Home run JB-BESS container (IS-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 602 | 57
H-I-0146 | H | BESS | Discrete device to JB JB-BESS container (IS-DI01: 8 x 1 pr (field cables) |  | BESS container (ISO 40 ft high cube) | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0147 | H | BESS | Home run JB-BESS container (IS-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 482 | 117
H-I-0148 | H | BESS | Discrete device to JB JB-BESS container (IS-DI01: 8 x 1 pr (field cables) |  | BESS container (ISO 40 ft high cube) | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0149 | H | BESS | Home run JB-BESS container (IS-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 336 | 177
H-I-0150 | H | BESS | Discrete device to JB JB-BESS container (IS-DI01: 8 x 1 pr (field cables) |  | BESS container (ISO 40 ft high cube) | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0151 | H | BESS | Home run JB-BESS container (IS-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 336 | 117
H-I-0152 | H | BESS | Discrete device to JB JB-BESS container (IS-DI01: 8 x 1 pr (field cables) |  | BESS container (ISO 40 ft high cube) | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0153 | H | BESS | Home run JB-BESS container (IS-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 336 | 57
H-I-0154 | H | BESS | Discrete device to JB JB-BESS container (IS-DI01: 8 x 1 pr (field cables) |  | BESS container (ISO 40 ft high cube) | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0155 | H | BESS | Home run JB-BESS container (IS-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS container (IS-DI01 | BESS container (ISO 40 ft high cube) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 336 | 57
H-I-0156 | H | BESS | Analog instrument to JB JB-BESS MPT-AI01: 8 x 1 pr (field cables) | BESS MPT | BESS main power transformer 34.5/230 kV (to D4 upper) | JB-BESS MPT-AI01 | BESS main power transformer 34.5/230 kV (to D4 upper) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 77 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0157 | H | BESS | Home run JB-BESS MPT-AI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS MPT-AI01 | BESS main power transformer 34.5/230 kV (to D4 upper) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 162 | 32
H-I-0158 | H | BESS | Discrete device to JB JB-BESS MPT-DI01: 16 x 1 pr (field cables) | BESS MPT | BESS main power transformer 34.5/230 kV (to D4 upper) | JB-BESS MPT-DI01 | BESS main power transformer 34.5/230 kV (to D4 upper) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 77 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
H-I-0159 | H | BESS | Home run JB-BESS MPT-DI01 to the control / marshalling room |  | BESS EMS / SCADA and revenue metering | JB-BESS MPT-DI01 | BESS main power transformer 34.5/230 kV (to D4 upper) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 162 | 32
H-I-0160 | H | BESS | Instrumentation |  | BESS EMS / SCADA and revenue metering |  | CONDITIONAL: grounding transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Duct bank | 280 | 87
H-P-0001 | H | BESS | LV panel / distribution feeder |  | BESS auxiliary transformer |  | 34.5 kV collector e-house (arc-resistant) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 30 | 37 |  |  |  |  | VD 0.6 %
H-P-0002 | H | BESS | LV panel / distribution feeder |  | BESS auxiliary transformer |  | BESS EMS / SCADA and revenue metering | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Tray | 0 | 70 |  |  |  |  | VD 0.6 %
H-P-0003 | H | BESS | Motor 1 of 2, 7 kW |  | BESS auxiliary transformer |  | BESS PCS / MV skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 318 | 103 |  |  |  |  | VD 2.0 %
H-P-0004 | H | BESS | Motor 2 of 2, 7 kW |  | BESS auxiliary transformer |  | BESS PCS / MV skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 318 | 103 |  |  |  |  | VD 2.0 %
H-P-0005 | H | BESS | Motor 1 of 2, 7 kW |  | BESS auxiliary transformer |  | BESS PCS / MV skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 178 | 123 |  |  |  |  | VD 1.4 %
H-P-0006 | H | BESS | Motor 2 of 2, 7 kW |  | BESS auxiliary transformer |  | BESS PCS / MV skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 178 | 123 |  |  |  |  | VD 1.4 %
H-P-0007 | H | BESS | Motor 1 of 2, 7 kW |  | BESS auxiliary transformer |  | BESS PCS / MV skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 74 | 107 |  |  |  |  | VD 0.9 %
H-P-0008 | H | BESS | Motor 2 of 2, 7 kW |  | BESS auxiliary transformer |  | BESS PCS / MV skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 74 | 107 |  |  |  |  | VD 0.9 %
H-P-0009 | H | BESS | Motor 1 of 2, 7 kW |  | BESS auxiliary transformer |  | BESS PCS / MV skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 318 | 161 |  |  |  |  | VD 2.3 %
H-P-0010 | H | BESS | Motor 2 of 2, 7 kW |  | BESS auxiliary transformer |  | BESS PCS / MV skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 318 | 161 |  |  |  |  | VD 2.3 %
H-P-0011 | H | BESS | Motor 1 of 2, 7 kW |  | BESS auxiliary transformer |  | BESS PCS / MV skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 178 | 181 |  |  |  |  | VD 1.7 %
H-P-0012 | H | BESS | Motor 2 of 2, 7 kW |  | BESS auxiliary transformer |  | BESS PCS / MV skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 178 | 181 |  |  |  |  | VD 1.7 %
H-P-0013 | H | BESS | Motor 1 of 2, 7 kW |  | BESS auxiliary transformer |  | BESS PCS / MV skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 74 | 165 |  |  |  |  | VD 1.1 %
H-P-0014 | H | BESS | Motor 2 of 2, 7 kW |  | BESS auxiliary transformer |  | BESS PCS / MV skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 74 | 165 |  |  |  |  | VD 1.1 %
H-P-0015 | H | BESS | Motor 1 of 2, 7 kW |  | BESS auxiliary transformer |  | BESS PCS / MV skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 318 | 219 |  |  |  |  | VD 2.6 %
H-P-0016 | H | BESS | Motor 2 of 2, 7 kW |  | BESS auxiliary transformer |  | BESS PCS / MV skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 318 | 219 |  |  |  |  | VD 2.6 %
H-P-0017 | H | BESS | Motor 1 of 2, 7 kW |  | BESS auxiliary transformer |  | BESS PCS / MV skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 178 | 239 |  |  |  |  | VD 2.0 %
H-P-0018 | H | BESS | Motor 2 of 2, 7 kW |  | BESS auxiliary transformer |  | BESS PCS / MV skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 178 | 239 |  |  |  |  | VD 2.0 %
H-P-0019 | H | BESS | Motor 1 of 2, 7 kW |  | BESS auxiliary transformer |  | BESS PCS / MV skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 380 | 149 |  |  |  |  | VD 2.5 %
H-P-0020 | H | BESS | Motor 2 of 2, 7 kW |  | BESS auxiliary transformer |  | BESS PCS / MV skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 380 | 149 |  |  |  |  | VD 2.5 %
H-P-0021 | H | BESS | Motor 1 of 2, 7 kW |  | BESS auxiliary transformer |  | BESS PCS / MV skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 620 | 91 |  |  |  |  | VD 2.1 %
H-P-0022 | H | BESS | Motor 2 of 2, 7 kW |  | BESS auxiliary transformer |  | BESS PCS / MV skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 620 | 91 |  |  |  |  | VD 2.1 %
H-P-0023 | H | BESS | Motor 1 of 2, 7 kW |  | BESS auxiliary transformer |  | BESS PCS / MV skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 500 | 91 |  |  |  |  | VD 2.8 %
H-P-0024 | H | BESS | Motor 2 of 2, 7 kW |  | BESS auxiliary transformer |  | BESS PCS / MV skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 500 | 91 |  |  |  |  | VD 2.8 %
H-P-0025 | H | BESS | Motor 1 of 2, 7 kW |  | BESS auxiliary transformer |  | BESS PCS / MV skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 380 | 91 |  |  |  |  | VD 2.2 %
H-P-0026 | H | BESS | Motor 2 of 2, 7 kW |  | BESS auxiliary transformer |  | BESS PCS / MV skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 380 | 91 |  |  |  |  | VD 2.2 %
H-P-0027 | H | BESS | Motor 1 of 2, 7 kW |  | BESS auxiliary transformer |  | BESS PCS / MV skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 620 | 37 |  |  |  |  | VD 2.0 %
H-P-0028 | H | BESS | Motor 2 of 2, 7 kW |  | BESS auxiliary transformer |  | BESS PCS / MV skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 620 | 37 |  |  |  |  | VD 2.0 %
H-P-0029 | H | BESS | Motor 1 of 2, 7 kW |  | BESS auxiliary transformer |  | BESS PCS / MV skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 500 | 37 |  |  |  |  | VD 2.6 %
H-P-0030 | H | BESS | Motor 2 of 2, 7 kW |  | BESS auxiliary transformer |  | BESS PCS / MV skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 500 | 37 |  |  |  |  | VD 2.6 %
H-P-0031 | H | BESS | Motor 1 of 2, 7 kW |  | BESS auxiliary transformer |  | BESS PCS / MV skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 380 | 37 |  |  |  |  | VD 2.0 %
H-P-0032 | H | BESS | Motor 2 of 2, 7 kW |  | BESS auxiliary transformer |  | BESS PCS / MV skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 380 | 37 |  |  |  |  | VD 2.0 %
H-P-0033 | H | BESS | Container auxiliary 480 V |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 85 | Duct bank | 10 | 150
H-P-0034 | H | BESS | Container auxiliary 480 V |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 85 | Tray | 0 | 160
H-P-0035 | H | BESS | Container auxiliary 480 V |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 85 | Tray | 0 | 200
H-P-0036 | H | BESS | Container auxiliary 480 V |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 85 | Tray | 0 | 200
H-P-0037 | H | BESS | Container auxiliary 480 V |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 85 | Tray | 0 | 168
H-P-0038 | H | BESS | Container auxiliary 480 V |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 85 | Tray | 0 | 168
H-P-0039 | H | BESS | Container auxiliary 480 V |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 85 | Duct bank | 10 | 266
H-P-0040 | H | BESS | Container auxiliary 480 V |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 85 | Tray | 0 | 276
H-P-0041 | H | BESS | Container auxiliary 480 V |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 85 | Tray | 0 | 316
H-P-0042 | H | BESS | Container auxiliary 480 V |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 85 | Tray | 0 | 316
H-P-0043 | H | BESS | Container auxiliary 480 V |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 85 | Tray | 0 | 284
H-P-0044 | H | BESS | Container auxiliary 480 V |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 85 | Tray | 0 | 284
H-P-0045 | H | BESS | Container auxiliary 480 V |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 85 | Tray | 0 | 290
H-P-0046 | H | BESS | Container auxiliary 480 V |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 85 | Tray | 0 | 290
H-P-0047 | H | BESS | Container auxiliary 480 V |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 85 | Tray | 0 | 290
H-P-0048 | H | BESS | Container auxiliary 480 V |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 85 | Tray | 0 | 290
H-P-0049 | H | BESS | Container auxiliary 480 V |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 85 | Tray | 0 | 290
H-P-0050 | H | BESS | Container auxiliary 480 V |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 85 | Tray | 0 | 290
H-P-0051 | H | BESS | Container auxiliary 480 V |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 85 | Tray | 0 | 174
H-P-0052 | H | BESS | Container auxiliary 480 V |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 85 | Tray | 0 | 174
H-P-0053 | H | BESS | Container auxiliary 480 V |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 85 | Tray | 0 | 174
H-P-0054 | H | BESS | Container auxiliary 480 V |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 85 | Tray | 0 | 174
H-P-0055 | H | BESS | Container auxiliary 480 V |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 85 | Tray | 0 | 174
H-P-0056 | H | BESS | Container auxiliary 480 V |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 85 | Tray | 0 | 174
H-P-0057 | H | BESS | Container auxiliary 480 V |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 85 | Tray | 0 | 62
H-P-0058 | H | BESS | Container auxiliary 480 V |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 85 | Tray | 0 | 62
H-P-0059 | H | BESS | Container auxiliary 480 V |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 85 | Tray | 0 | 62
H-P-0060 | H | BESS | Container auxiliary 480 V |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 85 | Tray | 0 | 62
H-P-0061 | H | BESS | Container auxiliary 480 V |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 85 | Tray | 0 | 62
H-P-0062 | H | BESS | Container auxiliary 480 V |  | BESS PCS / MV skid |  | BESS container (ISO 40 ft high cube) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 85 | Tray | 0 | 62
H-P-0063 | H | BESS | Motor 1 of 6, 2 kW |  | BESS auxiliary transformer | BESS MPT | BESS main power transformer 34.5/230 kV (to D4 upper) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 180 | 32 |  |  |  |  | VD 0.3 %
H-P-0064 | H | BESS | Motor 2 of 6, 2 kW |  | BESS auxiliary transformer | BESS MPT | BESS main power transformer 34.5/230 kV (to D4 upper) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 180 | 32 |  |  |  |  | VD 0.3 %
H-P-0065 | H | BESS | Motor 3 of 6, 2 kW |  | BESS auxiliary transformer | BESS MPT | BESS main power transformer 34.5/230 kV (to D4 upper) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 180 | 32 |  |  |  |  | VD 0.3 %
H-P-0066 | H | BESS | Motor 4 of 6, 2 kW |  | BESS auxiliary transformer | BESS MPT | BESS main power transformer 34.5/230 kV (to D4 upper) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 180 | 32 |  |  |  |  | VD 0.3 %
H-P-0067 | H | BESS | Motor 5 of 6, 2 kW |  | BESS auxiliary transformer | BESS MPT | BESS main power transformer 34.5/230 kV (to D4 upper) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 180 | 32 |  |  |  |  | VD 0.3 %
H-P-0068 | H | BESS | Motor 6 of 6, 2 kW |  | BESS auxiliary transformer | BESS MPT | BESS main power transformer 34.5/230 kV (to D4 upper) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 180 | 32 |  |  |  |  | VD 0.3 %
H-P-0069 | H | BESS | Yard lighting circuit 1 (10 floodlights) |  | BESS auxiliary transformer |  | BESS yard: surfacing, fence, gate, signage, lighting | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 4 | 6 | Buried | 900 | 30 |  |  |  |  | pole to pole, buried
H-P-0070 | H | BESS | Yard lighting circuit 2 (10 floodlights) |  | BESS auxiliary transformer |  | BESS yard: surfacing, fence, gate, signage, lighting | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 4 | 6 | Buried | 900 | 30 |  |  |  |  | pole to pole, buried
H-P-0071 | H | BESS | Yard lighting circuit 3 (4 floodlights) |  | BESS auxiliary transformer |  | BESS yard: surfacing, fence, gate, signage, lighting | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 4 | 6 | Buried | 900 | 30 |  |  |  |  | pole to pole, buried
H-MV-0001 | H | BESS | 34.5 kV collection loop 1 |  | BESS PCS / MV skid |  | 34.5 kV collector e-house (arc-resistant) | MV 35 kV | MV-105 35 kV 1/C Al, EPR 133%, 1/3 concentric neutral, LLDPE jacket | MV35¦1/C¦350 | 1/C | 350 kcmil | 2 | 3 | 34500 | 25000 | 418 | Duct bank | 556 | 37
H-MV-0002 | H | BESS | 34.5 kV collection loop 2 |  | BESS PCS / MV skid |  | 34.5 kV collector e-house (arc-resistant) | MV 35 kV | MV-105 35 kV 1/C Al, EPR 133%, 1/3 concentric neutral, LLDPE jacket | MV35¦1/C¦350 | 1/C | 350 kcmil | 2 | 3 | 34500 | 25000 | 418 | Duct bank | 436 | 37
H-MV-0003 | H | BESS | 34.5 kV collection loop 3 |  | BESS PCS / MV skid |  | 34.5 kV collector e-house (arc-resistant) | MV 35 kV | MV-105 35 kV 1/C Al, EPR 133%, 1/3 concentric neutral, LLDPE jacket | MV35¦1/C¦350 | 1/C | 350 kcmil | 2 | 3 | 34500 | 25000 | 418 | Duct bank | 350 | 42
H-MV-0004 | H | BESS | 34.5 kV collection loop 1 |  | 34.5 kV collector e-house (arc-resistant) |  | BESS PCS / MV skid | MV 35 kV | MV-105 35 kV 1/C Al, EPR 133%, 1/3 concentric neutral, LLDPE jacket | MV35¦1/C¦350 | 1/C | 350 kcmil | 2 | 3 | 34500 | 25000 | 418 | Duct bank | 254 | 103
H-MV-0005 | H | BESS | 34.5 kV collection loop 1 |  | BESS PCS / MV skid |  | BESS PCS / MV skid | MV 35 kV | MV-105 35 kV 1/C Al, EPR 133%, 1/3 concentric neutral, LLDPE jacket | MV35¦1/C¦350 | 1/C | 350 kcmil | 2 | 3 | 34500 | 25000 | 418 | Tray | 0 | 232
H-MV-0006 | H | BESS | 34.5 kV collection loop 1 |  | BESS PCS / MV skid |  | BESS PCS / MV skid | MV 35 kV | MV-105 35 kV 1/C Al, EPR 133%, 1/3 concentric neutral, LLDPE jacket | MV35¦1/C¦350 | 1/C | 350 kcmil | 2 | 3 | 34500 | 25000 | 418 | Tray | 0 | 348
H-MV-0007 | H | BESS | 34.5 kV collection loop 1 |  | BESS PCS / MV skid |  | BESS PCS / MV skid | MV 35 kV | MV-105 35 kV 1/C Al, EPR 133%, 1/3 concentric neutral, LLDPE jacket | MV35¦1/C¦350 | 1/C | 350 kcmil | 2 | 3 | 34500 | 25000 | 418 | Tray | 0 | 208
H-MV-0008 | H | BESS | 34.5 kV collection loop 1 |  | BESS PCS / MV skid |  | BESS PCS / MV skid | MV 35 kV | MV-105 35 kV 1/C Al, EPR 133%, 1/3 concentric neutral, LLDPE jacket | MV35¦1/C¦350 | 1/C | 350 kcmil | 2 | 3 | 34500 | 25000 | 418 | Tray | 0 | 96
H-MV-0009 | H | BESS | 34.5 kV collection loop 2 |  | 34.5 kV collector e-house (arc-resistant) |  | BESS PCS / MV skid | MV 35 kV | MV-105 35 kV 1/C Al, EPR 133%, 1/3 concentric neutral, LLDPE jacket | MV35¦1/C¦350 | 1/C | 350 kcmil | 2 | 3 | 34500 | 25000 | 418 | Duct bank | 35 | 185
H-MV-0010 | H | BESS | 34.5 kV collection loop 2 |  | BESS PCS / MV skid |  | BESS PCS / MV skid | MV 35 kV | MV-105 35 kV 1/C Al, EPR 133%, 1/3 concentric neutral, LLDPE jacket | MV35¦1/C¦350 | 1/C | 350 kcmil | 2 | 3 | 34500 | 25000 | 418 | Tray | 0 | 272
H-MV-0011 | H | BESS | 34.5 kV collection loop 2 |  | BESS PCS / MV skid |  | BESS PCS / MV skid | MV 35 kV | MV-105 35 kV 1/C Al, EPR 133%, 1/3 concentric neutral, LLDPE jacket | MV35¦1/C¦350 | 1/C | 350 kcmil | 2 | 3 | 34500 | 25000 | 418 | Tray | 0 | 388
H-MV-0012 | H | BESS | 34.5 kV collection loop 2 |  | BESS PCS / MV skid |  | BESS PCS / MV skid | MV 35 kV | MV-105 35 kV 1/C Al, EPR 133%, 1/3 concentric neutral, LLDPE jacket | MV35¦1/C¦350 | 1/C | 350 kcmil | 2 | 3 | 34500 | 25000 | 418 | Tray | 0 | 208
H-MV-0013 | H | BESS | 34.5 kV collection loop 2 |  | BESS PCS / MV skid |  | BESS PCS / MV skid | MV 35 kV | MV-105 35 kV 1/C Al, EPR 133%, 1/3 concentric neutral, LLDPE jacket | MV35¦1/C¦350 | 1/C | 350 kcmil | 2 | 3 | 34500 | 25000 | 418 | Tray | 0 | 96
H-MV-0014 | H | BESS | 34.5 kV collection loop 3 |  | 34.5 kV collector e-house (arc-resistant) |  | BESS PCS / MV skid | MV 35 kV | MV-105 35 kV 1/C Al, EPR 133%, 1/3 concentric neutral, LLDPE jacket | MV35¦1/C¦350 | 1/C | 350 kcmil | 2 | 3 | 34500 | 25000 | 418 | Duct bank | 24 | 123
H-MV-0015 | H | BESS | 34.5 kV collection loop 3 |  | BESS PCS / MV skid |  | BESS PCS / MV skid | MV 35 kV | MV-105 35 kV 1/C Al, EPR 133%, 1/3 concentric neutral, LLDPE jacket | MV35¦1/C¦350 | 1/C | 350 kcmil | 2 | 3 | 34500 | 25000 | 418 | Tray | 0 | 240
H-MV-0016 | H | BESS | 34.5 kV collection loop 3 |  | BESS PCS / MV skid |  | BESS PCS / MV skid | MV 35 kV | MV-105 35 kV 1/C Al, EPR 133%, 1/3 concentric neutral, LLDPE jacket | MV35¦1/C¦350 | 1/C | 350 kcmil | 2 | 3 | 34500 | 25000 | 418 | Duct bank | 306 | 282
H-MV-0017 | H | BESS | 34.5 kV collection loop 3 |  | BESS PCS / MV skid |  | BESS PCS / MV skid | MV 35 kV | MV-105 35 kV 1/C Al, EPR 133%, 1/3 concentric neutral, LLDPE jacket | MV35¦1/C¦350 | 1/C | 350 kcmil | 2 | 3 | 34500 | 25000 | 418 | Tray | 0 | 208
H-MV-0018 | H | BESS | 34.5 kV collection loop 3 |  | BESS PCS / MV skid |  | BESS PCS / MV skid | MV 35 kV | MV-105 35 kV 1/C Al, EPR 133%, 1/3 concentric neutral, LLDPE jacket | MV35¦1/C¦350 | 1/C | 350 kcmil | 2 | 3 | 34500 | 25000 | 418 | Tray | 0 | 96
H-MV-0019 | H | BESS | BESS MPT 34.5 kV side |  | 34.5 kV collector e-house (arc-resistant) | BESS MPT | BESS main power transformer 34.5/230 kV (to D4 upper) | MV 35 kV | MV-105 35 kV 1/C Al, EPR 133%, 1/3 concentric neutral, LLDPE jacket | MV35¦1/C¦750 | 1/C | 750 kcmil | 5 | 3 | 34500 | 100000 | 1674 | Duct bank | 35 | 32 |  |  |  |  | 100 MVA (typ.)
H-MV-0020 | H | BESS | Grounding transformer connection (34.5 kV) |  | 34.5 kV collector e-house (arc-resistant) |  | CONDITIONAL: grounding transformer | MV 35 kV | MV-105 35 kV 1/C Al, EPR 133%, 1/3 concentric neutral, LLDPE jacket | MV35¦1/C¦2 | 1/C | 2 | 1 | 3 | 34500 | 2000 | 33 | Duct bank | 234 | 87
I-L-0001 | I | Modular / portable power | Lighting, receptacles and small power branch circuits (allowance) |  | Lube oil / starting air / oily water building |  | Lube oil / starting air / oily water building | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | THHN¦1/C¦12 | 1/C | 12 | 1 | 1 | 277 |  |  | Conduit | 10560 | 0 |  |  |  |  | allowance: 1.6 ft of conductor per ft2 of floor
I-L-0002 | I | Modular / portable power | Lighting, receptacles and small power branch circuits (allowance) | MOD-EH | MOD-EH: 13.8 kV modular collector e-house | MOD-EH | MOD-EH: 13.8 kV modular collector e-house | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | THHN¦1/C¦12 | 1/C | 12 | 1 | 1 | 277 |  |  | Conduit | 2560 | 0 |  |  |  |  | allowance: 1.6 ft of conductor per ft2 of floor
I-L-0003 | I | Modular / portable power | Lighting, receptacles and small power branch circuits (allowance) |  | PCM: power control module |  | PCM: power control module | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | THHN¦1/C¦12 | 1/C | 12 | 1 | 1 | 277 |  |  | Conduit | 5120 | 0 |  |  |  |  | allowance: 1.6 ft of conductor per ft2 of floor
I-L-0004 | I | Modular / portable power | Lighting, receptacles and small power branch circuits (allowance) |  | RICE CEMS |  | RICE CEMS | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | THHN¦1/C¦12 | 1/C | 12 | 1 | 1 | 277 |  |  | Conduit | 256 | 0 |  |  |  |  | allowance: 1.6 ft of conductor per ft2 of floor
I-C-0001 | I | Modular / portable power | Control |  | PCM: power control module |  | BS black-start switchgear | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 562 | 64
I-C-0002 | I | Modular / portable power | Control |  | PCM: power control module |  | CONDITIONAL: BESS black-start alternative | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 550 | 32
I-C-0003 | I | Modular / portable power | Control |  | PCM: power control module |  | CONDITIONAL: SC-1 inlet chiller / evaporative cooler | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 40 | 52
I-C-0004 | I | Modular / portable power | Control |  | PCM: power control module |  | CONDITIONAL: SC-2 inlet chiller / evaporative cooler | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | HV duct bank | 4528 | 38
I-C-0005 | I | Modular / portable power | Control | PAD-EH | PAD-EH 13.8 kV switchgear e-house |  | FC-5..12 inverter / AC cabinet / desulfurizer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Surface | 202 | 37
I-C-0006 | I | Modular / portable power | Control |  | PCM: power control module |  | Fuel-cell inverter / AC cabinet / desulfurizer | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 1032 | 34
I-C-0007 | I | Modular / portable power | Motor 1 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | Fuel-gas compressors 3 x 100% electric | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | HV duct bank | 4396 | 40
I-C-0008 | I | Modular / portable power | Motor 2 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | Fuel-gas compressors 3 x 100% electric | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | HV duct bank | 4396 | 40
I-C-0009 | I | Modular / portable power | Motor 3 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | Fuel-gas compressors 3 x 100% electric | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | HV duct bank | 4396 | 40
I-C-0010 | I | Modular / portable power | Motor 4 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | Fuel-gas compressors 3 x 100% electric | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | HV duct bank | 4396 | 40
I-C-0011 | I | Modular / portable power | Motor 5 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | Fuel-gas compressors 3 x 100% electric | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | HV duct bank | 4396 | 40
I-C-0012 | I | Modular / portable power | Motor 6 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | Fuel-gas compressors 3 x 100% electric | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | HV duct bank | 4396 | 40
I-C-0013 | I | Modular / portable power | Control | PAD-EH | PAD-EH 13.8 kV switchgear e-house | GSP-1 | GSP-1: generator breaker / protection | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Surface | 269 | 66
I-C-0014 | I | Modular / portable power | Control | PAD-EH | PAD-EH 13.8 kV switchgear e-house | GSP-1 | GSP-1: generator breaker / protection | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Surface | 269 | 66
I-C-0015 | I | Modular / portable power | Control | PAD-EH | PAD-EH 13.8 kV switchgear e-house | GSP-1 | GSP-1: generator breaker / protection | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Surface | 269 | 66
I-C-0016 | I | Modular / portable power | CT / VT | PAD-EH | PAD-EH 13.8 kV switchgear e-house | GSP-1 | GSP-1: generator breaker / protection | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Surface | 269 | 66
I-C-0017 | I | Modular / portable power | CT / VT | PAD-EH | PAD-EH 13.8 kV switchgear e-house | GSP-1 | GSP-1: generator breaker / protection | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Surface | 269 | 66
I-C-0018 | I | Modular / portable power | CT / VT | PAD-EH | PAD-EH 13.8 kV switchgear e-house | GSP-1 | GSP-1: generator breaker / protection | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Surface | 269 | 66
I-C-0019 | I | Modular / portable power | CT / VT | PAD-EH | PAD-EH 13.8 kV switchgear e-house | GSP-1 | GSP-1: generator breaker / protection | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Surface | 269 | 66
I-C-0020 | I | Modular / portable power | Control | PAD-EH | PAD-EH 13.8 kV switchgear e-house | GSP-2 | GSP-2: generator breaker / protection | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Surface | 269 | 37
I-C-0021 | I | Modular / portable power | Control | PAD-EH | PAD-EH 13.8 kV switchgear e-house | GSP-2 | GSP-2: generator breaker / protection | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Surface | 269 | 37
I-C-0022 | I | Modular / portable power | Control | PAD-EH | PAD-EH 13.8 kV switchgear e-house | GSP-2 | GSP-2: generator breaker / protection | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Surface | 269 | 37
I-C-0023 | I | Modular / portable power | CT / VT | PAD-EH | PAD-EH 13.8 kV switchgear e-house | GSP-2 | GSP-2: generator breaker / protection | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Surface | 269 | 37
I-C-0024 | I | Modular / portable power | CT / VT | PAD-EH | PAD-EH 13.8 kV switchgear e-house | GSP-2 | GSP-2: generator breaker / protection | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Surface | 269 | 37
I-C-0025 | I | Modular / portable power | CT / VT | PAD-EH | PAD-EH 13.8 kV switchgear e-house | GSP-2 | GSP-2: generator breaker / protection | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Surface | 269 | 37
I-C-0026 | I | Modular / portable power | CT / VT | PAD-EH | PAD-EH 13.8 kV switchgear e-house | GSP-2 | GSP-2: generator breaker / protection | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Surface | 269 | 37
I-C-0027 | I | Modular / portable power | Control |  | PCM: power control module |  | Gas conditioning skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 32 | 94
I-C-0028 | I | Modular / portable power | Control | PAD-EH | PAD-EH 13.8 kV switchgear e-house | LB | LB: commissioning load bank (trailer) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Surface | 169 | 73
I-C-0029 | I | Modular / portable power | Control |  | PCM: power control module |  | Lube oil / starting air / oily water building | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 32 | 164
I-C-0030 | I | Modular / portable power | Control |  | PCM: power control module | MOD-EH | MOD-EH: 13.8 kV modular collector e-house | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 355 | 32
I-C-0031 | I | Modular / portable power | Control |  | PCM: power control module |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 773 | 34
I-C-0032 | I | Modular / portable power | Control |  | PCM: power control module |  | PCM: power control module | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 32
I-C-0033 | I | Modular / portable power | Motor 1 of 1: control / local station |  | PCM: power control module |  | RICE 1 SCR + oxidation catalyst and stack | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 470 | 160
I-C-0034 | I | Modular / portable power | Motor 1 of 5: control / local station |  | PCM: power control module |  | RICE 1 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 745 | 139
I-C-0035 | I | Modular / portable power | Motor 2 of 5: control / local station |  | PCM: power control module |  | RICE 1 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 745 | 139
I-C-0036 | I | Modular / portable power | Motor 3 of 5: control / local station |  | PCM: power control module |  | RICE 1 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 745 | 139
I-C-0037 | I | Modular / portable power | Motor 4 of 5: control / local station |  | PCM: power control module |  | RICE 1 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 745 | 139
I-C-0038 | I | Modular / portable power | Motor 5 of 5: control / local station |  | PCM: power control module |  | RICE 1 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 745 | 139
I-C-0039 | I | Modular / portable power | Motor 1 of 1: control / local station |  | PCM: power control module |  | RICE 2 SCR + oxidation catalyst and stack | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 470 | 132
I-C-0040 | I | Modular / portable power | Motor 1 of 5: control / local station |  | PCM: power control module |  | RICE 2 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 550 | 192
I-C-0041 | I | Modular / portable power | Motor 2 of 5: control / local station |  | PCM: power control module |  | RICE 2 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 550 | 192
I-C-0042 | I | Modular / portable power | Motor 3 of 5: control / local station |  | PCM: power control module |  | RICE 2 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 550 | 192
I-C-0043 | I | Modular / portable power | Motor 4 of 5: control / local station |  | PCM: power control module |  | RICE 2 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 550 | 192
I-C-0044 | I | Modular / portable power | Motor 5 of 5: control / local station |  | PCM: power control module |  | RICE 2 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 550 | 192
I-C-0045 | I | Modular / portable power | Motor 1 of 1: control / local station |  | PCM: power control module |  | RICE 3 SCR + oxidation catalyst and stack | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 470 | 104
I-C-0046 | I | Modular / portable power | Motor 1 of 5: control / local station |  | PCM: power control module |  | RICE 3 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 32 | 232
I-C-0047 | I | Modular / portable power | Motor 2 of 5: control / local station |  | PCM: power control module |  | RICE 3 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 32 | 232
I-C-0048 | I | Modular / portable power | Motor 3 of 5: control / local station |  | PCM: power control module |  | RICE 3 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 32 | 232
I-C-0049 | I | Modular / portable power | Motor 4 of 5: control / local station |  | PCM: power control module |  | RICE 3 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 32 | 232
I-C-0050 | I | Modular / portable power | Motor 5 of 5: control / local station |  | PCM: power control module |  | RICE 3 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 32 | 232
I-C-0051 | I | Modular / portable power | Motor 1 of 1: control / local station |  | PCM: power control module |  | RICE 4 SCR + oxidation catalyst and stack | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 470 | 76
I-C-0052 | I | Modular / portable power | Motor 1 of 5: control / local station |  | PCM: power control module |  | RICE 4 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 206
I-C-0053 | I | Modular / portable power | Motor 2 of 5: control / local station |  | PCM: power control module |  | RICE 4 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 206
I-C-0054 | I | Modular / portable power | Motor 3 of 5: control / local station |  | PCM: power control module |  | RICE 4 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 206
I-C-0055 | I | Modular / portable power | Motor 4 of 5: control / local station |  | PCM: power control module |  | RICE 4 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 206
I-C-0056 | I | Modular / portable power | Motor 5 of 5: control / local station |  | PCM: power control module |  | RICE 4 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 206
I-C-0057 | I | Modular / portable power | Motor 1 of 1: control / local station |  | PCM: power control module |  | RICE 5 SCR + oxidation catalyst and stack | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 322 | 196
I-C-0058 | I | Modular / portable power | Motor 1 of 5: control / local station |  | PCM: power control module |  | RICE 5 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 178
I-C-0059 | I | Modular / portable power | Motor 2 of 5: control / local station |  | PCM: power control module |  | RICE 5 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 178
I-C-0060 | I | Modular / portable power | Motor 3 of 5: control / local station |  | PCM: power control module |  | RICE 5 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 178
I-C-0061 | I | Modular / portable power | Motor 4 of 5: control / local station |  | PCM: power control module |  | RICE 5 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 178
I-C-0062 | I | Modular / portable power | Motor 5 of 5: control / local station |  | PCM: power control module |  | RICE 5 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 178
I-C-0063 | I | Modular / portable power | Motor 1 of 1: control / local station |  | PCM: power control module |  | RICE 6 SCR + oxidation catalyst and stack | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 322 | 168
I-C-0064 | I | Modular / portable power | Motor 1 of 5: control / local station |  | PCM: power control module |  | RICE 6 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 150
I-C-0065 | I | Modular / portable power | Motor 2 of 5: control / local station |  | PCM: power control module |  | RICE 6 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 150
I-C-0066 | I | Modular / portable power | Motor 3 of 5: control / local station |  | PCM: power control module |  | RICE 6 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 150
I-C-0067 | I | Modular / portable power | Motor 4 of 5: control / local station |  | PCM: power control module |  | RICE 6 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 150
I-C-0068 | I | Modular / portable power | Motor 5 of 5: control / local station |  | PCM: power control module |  | RICE 6 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 150
I-C-0069 | I | Modular / portable power | Motor 1 of 1: control / local station |  | PCM: power control module |  | RICE 7 SCR + oxidation catalyst and stack | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 322 | 140
I-C-0070 | I | Modular / portable power | Motor 1 of 5: control / local station |  | PCM: power control module |  | RICE 7 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 122
I-C-0071 | I | Modular / portable power | Motor 2 of 5: control / local station |  | PCM: power control module |  | RICE 7 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 122
I-C-0072 | I | Modular / portable power | Motor 3 of 5: control / local station |  | PCM: power control module |  | RICE 7 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 122
I-C-0073 | I | Modular / portable power | Motor 4 of 5: control / local station |  | PCM: power control module |  | RICE 7 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 122
I-C-0074 | I | Modular / portable power | Motor 5 of 5: control / local station |  | PCM: power control module |  | RICE 7 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 122
I-C-0075 | I | Modular / portable power | Motor 1 of 1: control / local station |  | PCM: power control module |  | RICE 8 SCR + oxidation catalyst and stack | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 322 | 112
I-C-0076 | I | Modular / portable power | Motor 1 of 5: control / local station |  | PCM: power control module |  | RICE 8 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 94
I-C-0077 | I | Modular / portable power | Motor 2 of 5: control / local station |  | PCM: power control module |  | RICE 8 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 94
I-C-0078 | I | Modular / portable power | Motor 3 of 5: control / local station |  | PCM: power control module |  | RICE 8 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 94
I-C-0079 | I | Modular / portable power | Motor 4 of 5: control / local station |  | PCM: power control module |  | RICE 8 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 94
I-C-0080 | I | Modular / portable power | Motor 5 of 5: control / local station |  | PCM: power control module |  | RICE 8 radiators (5) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 94
I-C-0081 | I | Modular / portable power | Control |  | PCM: power control module |  | RICE CEMS | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 260 | 131
I-C-0082 | I | Modular / portable power | Control |  | PCM: power control module | RICE | RICE engine hall (8 engines) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 367 | 95
I-C-0083 | I | Modular / portable power | Control |  | PCM: power control module | RICE | RICE engine hall (8 engines) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 367 | 95
I-C-0084 | I | Modular / portable power | Control |  | PCM: power control module | RICE | RICE engine hall (8 engines) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 367 | 95
I-C-0085 | I | Modular / portable power | Control |  | PCM: power control module | RICE | RICE engine hall (8 engines) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 367 | 95
I-C-0086 | I | Modular / portable power | Control |  | PCM: power control module | RICE | RICE engine hall (8 engines) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 367 | 95
I-C-0087 | I | Modular / portable power | Control |  | PCM: power control module | RICE | RICE engine hall (8 engines) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 367 | 95
I-C-0088 | I | Modular / portable power | Control |  | PCM: power control module | RICE | RICE engine hall (8 engines) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 367 | 95
I-C-0089 | I | Modular / portable power | Control |  | PCM: power control module | RICE | RICE engine hall (8 engines) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 367 | 95
I-C-0090 | I | Modular / portable power | Motor 1 of 6: control / local station |  | PCM: power control module | RICE-1 | RICE engine-generator 1 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 550 | 137
I-C-0091 | I | Modular / portable power | Motor 2 of 6: control / local station |  | PCM: power control module | RICE-1 | RICE engine-generator 1 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 550 | 137
I-C-0092 | I | Modular / portable power | Motor 3 of 6: control / local station |  | PCM: power control module | RICE-1 | RICE engine-generator 1 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 550 | 137
I-C-0093 | I | Modular / portable power | Motor 4 of 6: control / local station |  | PCM: power control module | RICE-1 | RICE engine-generator 1 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 550 | 137
I-C-0094 | I | Modular / portable power | Motor 5 of 6: control / local station |  | PCM: power control module | RICE-1 | RICE engine-generator 1 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 550 | 137
I-C-0095 | I | Modular / portable power | Motor 6 of 6: control / local station |  | PCM: power control module | RICE-1 | RICE engine-generator 1 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 550 | 137
I-C-0096 | I | Modular / portable power | Motor 1 of 6: control / local station |  | PCM: power control module | RICE-2 | RICE engine-generator 2 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 550 | 109
I-C-0097 | I | Modular / portable power | Motor 2 of 6: control / local station |  | PCM: power control module | RICE-2 | RICE engine-generator 2 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 550 | 109
I-C-0098 | I | Modular / portable power | Motor 3 of 6: control / local station |  | PCM: power control module | RICE-2 | RICE engine-generator 2 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 550 | 109
I-C-0099 | I | Modular / portable power | Motor 4 of 6: control / local station |  | PCM: power control module | RICE-2 | RICE engine-generator 2 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 550 | 109
I-C-0100 | I | Modular / portable power | Motor 5 of 6: control / local station |  | PCM: power control module | RICE-2 | RICE engine-generator 2 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 550 | 109
I-C-0101 | I | Modular / portable power | Motor 6 of 6: control / local station |  | PCM: power control module | RICE-2 | RICE engine-generator 2 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 550 | 109
I-C-0102 | I | Modular / portable power | Motor 1 of 6: control / local station |  | PCM: power control module | RICE-3 | RICE engine-generator 3 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 550 | 81
I-C-0103 | I | Modular / portable power | Motor 2 of 6: control / local station |  | PCM: power control module | RICE-3 | RICE engine-generator 3 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 550 | 81
I-C-0104 | I | Modular / portable power | Motor 3 of 6: control / local station |  | PCM: power control module | RICE-3 | RICE engine-generator 3 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 550 | 81
I-C-0105 | I | Modular / portable power | Motor 4 of 6: control / local station |  | PCM: power control module | RICE-3 | RICE engine-generator 3 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 550 | 81
I-C-0106 | I | Modular / portable power | Motor 5 of 6: control / local station |  | PCM: power control module | RICE-3 | RICE engine-generator 3 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 550 | 81
I-C-0107 | I | Modular / portable power | Motor 6 of 6: control / local station |  | PCM: power control module | RICE-3 | RICE engine-generator 3 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 550 | 81
I-C-0108 | I | Modular / portable power | Motor 1 of 6: control / local station |  | PCM: power control module | RICE-4 | RICE engine-generator 4 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 550 | 53
I-C-0109 | I | Modular / portable power | Motor 2 of 6: control / local station |  | PCM: power control module | RICE-4 | RICE engine-generator 4 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 550 | 53
I-C-0110 | I | Modular / portable power | Motor 3 of 6: control / local station |  | PCM: power control module | RICE-4 | RICE engine-generator 4 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 550 | 53
I-C-0111 | I | Modular / portable power | Motor 4 of 6: control / local station |  | PCM: power control module | RICE-4 | RICE engine-generator 4 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 550 | 53
I-C-0112 | I | Modular / portable power | Motor 5 of 6: control / local station |  | PCM: power control module | RICE-4 | RICE engine-generator 4 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 550 | 53
I-C-0113 | I | Modular / portable power | Motor 6 of 6: control / local station |  | PCM: power control module | RICE-4 | RICE engine-generator 4 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 550 | 53
I-C-0114 | I | Modular / portable power | Motor 1 of 6: control / local station |  | PCM: power control module | RICE-5 | RICE engine-generator 5 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 367 | 208
I-C-0115 | I | Modular / portable power | Motor 2 of 6: control / local station |  | PCM: power control module | RICE-5 | RICE engine-generator 5 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 367 | 208
I-C-0116 | I | Modular / portable power | Motor 3 of 6: control / local station |  | PCM: power control module | RICE-5 | RICE engine-generator 5 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 367 | 208
I-C-0117 | I | Modular / portable power | Motor 4 of 6: control / local station |  | PCM: power control module | RICE-5 | RICE engine-generator 5 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 367 | 208
I-C-0118 | I | Modular / portable power | Motor 5 of 6: control / local station |  | PCM: power control module | RICE-5 | RICE engine-generator 5 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 367 | 208
I-C-0119 | I | Modular / portable power | Motor 6 of 6: control / local station |  | PCM: power control module | RICE-5 | RICE engine-generator 5 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 367 | 208
I-C-0120 | I | Modular / portable power | Motor 1 of 6: control / local station |  | PCM: power control module | RICE-6 | RICE engine-generator 6 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 367 | 180
I-C-0121 | I | Modular / portable power | Motor 2 of 6: control / local station |  | PCM: power control module | RICE-6 | RICE engine-generator 6 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 367 | 180
I-C-0122 | I | Modular / portable power | Motor 3 of 6: control / local station |  | PCM: power control module | RICE-6 | RICE engine-generator 6 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 367 | 180
I-C-0123 | I | Modular / portable power | Motor 4 of 6: control / local station |  | PCM: power control module | RICE-6 | RICE engine-generator 6 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 367 | 180
I-C-0124 | I | Modular / portable power | Motor 5 of 6: control / local station |  | PCM: power control module | RICE-6 | RICE engine-generator 6 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 367 | 180
I-C-0125 | I | Modular / portable power | Motor 6 of 6: control / local station |  | PCM: power control module | RICE-6 | RICE engine-generator 6 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 367 | 180
I-C-0126 | I | Modular / portable power | Motor 1 of 6: control / local station |  | PCM: power control module | RICE-7 | RICE engine-generator 7 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 189
I-C-0127 | I | Modular / portable power | Motor 2 of 6: control / local station |  | PCM: power control module | RICE-7 | RICE engine-generator 7 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 189
I-C-0128 | I | Modular / portable power | Motor 3 of 6: control / local station |  | PCM: power control module | RICE-7 | RICE engine-generator 7 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 189
I-C-0129 | I | Modular / portable power | Motor 4 of 6: control / local station |  | PCM: power control module | RICE-7 | RICE engine-generator 7 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 189
I-C-0130 | I | Modular / portable power | Motor 5 of 6: control / local station |  | PCM: power control module | RICE-7 | RICE engine-generator 7 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 189
I-C-0131 | I | Modular / portable power | Motor 6 of 6: control / local station |  | PCM: power control module | RICE-7 | RICE engine-generator 7 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 189
I-C-0132 | I | Modular / portable power | Motor 1 of 6: control / local station |  | PCM: power control module | RICE-8 | RICE engine-generator 8 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 161
I-C-0133 | I | Modular / portable power | Motor 2 of 6: control / local station |  | PCM: power control module | RICE-8 | RICE engine-generator 8 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 161
I-C-0134 | I | Modular / portable power | Motor 3 of 6: control / local station |  | PCM: power control module | RICE-8 | RICE engine-generator 8 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 161
I-C-0135 | I | Modular / portable power | Motor 4 of 6: control / local station |  | PCM: power control module | RICE-8 | RICE engine-generator 8 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 161
I-C-0136 | I | Modular / portable power | Motor 5 of 6: control / local station |  | PCM: power control module | RICE-8 | RICE engine-generator 8 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 161
I-C-0137 | I | Modular / portable power | Motor 6 of 6: control / local station |  | PCM: power control module | RICE-8 | RICE engine-generator 8 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 161
I-C-0138 | I | Modular / portable power | Control |  | PCM: power control module |  | Reagent storage | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 32 | 32
I-C-0139 | I | Modular / portable power | Motor 1 of 2: control / local station |  | PCM: power control module |  | SC-1 SCR / CO catalyst | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 40 | 142
I-C-0140 | I | Modular / portable power | Motor 2 of 2: control / local station |  | PCM: power control module |  | SC-1 SCR / CO catalyst | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 40 | 142
I-C-0141 | I | Modular / portable power | Motor 1 of 4: control / local station |  | PCM: power control module |  | SC-1 lube-oil fin-fan cooler | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 82 | 82
I-C-0142 | I | Modular / portable power | Motor 2 of 4: control / local station |  | PCM: power control module |  | SC-1 lube-oil fin-fan cooler | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 82 | 82
I-C-0143 | I | Modular / portable power | Motor 3 of 4: control / local station |  | PCM: power control module |  | SC-1 lube-oil fin-fan cooler | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 82 | 82
I-C-0144 | I | Modular / portable power | Motor 4 of 4: control / local station |  | PCM: power control module |  | SC-1 lube-oil fin-fan cooler | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 82 | 82
I-C-0145 | I | Modular / portable power | Motor 1 of 10: control / local station |  | PCM: power control module | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 40 | 52
I-C-0146 | I | Modular / portable power | Motor 2 of 10: control / local station |  | PCM: power control module | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 40 | 52
I-C-0147 | I | Modular / portable power | Motor 3 of 10: control / local station |  | PCM: power control module | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 40 | 52
I-C-0148 | I | Modular / portable power | Motor 4 of 10: control / local station |  | PCM: power control module | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 40 | 52
I-C-0149 | I | Modular / portable power | Motor 5 of 10: control / local station |  | PCM: power control module | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 40 | 52
I-C-0150 | I | Modular / portable power | Motor 6 of 10: control / local station |  | PCM: power control module | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 40 | 52
I-C-0151 | I | Modular / portable power | Motor 7 of 10: control / local station |  | PCM: power control module | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 40 | 52
I-C-0152 | I | Modular / portable power | Motor 8 of 10: control / local station |  | PCM: power control module | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 40 | 52
I-C-0153 | I | Modular / portable power | Motor 9 of 10: control / local station |  | PCM: power control module | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 40 | 52
I-C-0154 | I | Modular / portable power | Motor 10 of 10: control / local station |  | PCM: power control module | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 40 | 52
I-C-0155 | I | Modular / portable power | Motor 1 of 2: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | SC-2 SCR / CO catalyst | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | HV duct bank | 4341 | 60
I-C-0156 | I | Modular / portable power | Motor 2 of 2: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | SC-2 SCR / CO catalyst | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | HV duct bank | 4341 | 60
I-C-0157 | I | Modular / portable power | Motor 1 of 4: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | SC-2 lube-oil fin-fan cooler | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | HV duct bank | 4329 | 95
I-C-0158 | I | Modular / portable power | Motor 2 of 4: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | SC-2 lube-oil fin-fan cooler | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | HV duct bank | 4329 | 95
I-C-0159 | I | Modular / portable power | Motor 3 of 4: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | SC-2 lube-oil fin-fan cooler | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | HV duct bank | 4329 | 95
I-C-0160 | I | Modular / portable power | Motor 4 of 4: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | SC-2 lube-oil fin-fan cooler | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | HV duct bank | 4329 | 95
I-C-0161 | I | Modular / portable power | Motor 1 of 10: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | HV duct bank | 4441 | 40
I-C-0162 | I | Modular / portable power | Motor 2 of 10: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | HV duct bank | 4441 | 40
I-C-0163 | I | Modular / portable power | Motor 3 of 10: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | HV duct bank | 4441 | 40
I-C-0164 | I | Modular / portable power | Motor 4 of 10: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | HV duct bank | 4441 | 40
I-C-0165 | I | Modular / portable power | Motor 5 of 10: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | HV duct bank | 4441 | 40
I-C-0166 | I | Modular / portable power | Motor 6 of 10: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | HV duct bank | 4441 | 40
I-C-0167 | I | Modular / portable power | Motor 7 of 10: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | HV duct bank | 4441 | 40
I-C-0168 | I | Modular / portable power | Motor 8 of 10: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | HV duct bank | 4441 | 40
I-C-0169 | I | Modular / portable power | Motor 9 of 10: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | HV duct bank | 4441 | 40
I-C-0170 | I | Modular / portable power | Motor 10 of 10: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | HV duct bank | 4441 | 40
I-C-0171 | I | Modular / portable power | Motor 1 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | T-MOD 230 kV take-off gantry with arresters | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 386 | 130
I-C-0172 | I | Modular / portable power | Motor 2 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | T-MOD 230 kV take-off gantry with arresters | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 386 | 130
I-C-0173 | I | Modular / portable power | Motor 3 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | T-MOD 230 kV take-off gantry with arresters | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 386 | 130
I-C-0174 | I | Modular / portable power | Motor 4 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | T-MOD 230 kV take-off gantry with arresters | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 386 | 130
I-C-0175 | I | Modular / portable power | Motor 5 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | T-MOD 230 kV take-off gantry with arresters | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 386 | 130
I-C-0176 | I | Modular / portable power | Motor 6 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | T-MOD 230 kV take-off gantry with arresters | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 386 | 130
I-C-0177 | I | Modular / portable power | Motor 1 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | T-MOD-1 / T-MOD-2 firewall | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 378 | 132
I-C-0178 | I | Modular / portable power | Motor 2 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | T-MOD-1 / T-MOD-2 firewall | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 378 | 132
I-C-0179 | I | Modular / portable power | Motor 3 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | T-MOD-1 / T-MOD-2 firewall | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 378 | 132
I-C-0180 | I | Modular / portable power | Motor 4 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | T-MOD-1 / T-MOD-2 firewall | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 378 | 132
I-C-0181 | I | Modular / portable power | Motor 5 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | T-MOD-1 / T-MOD-2 firewall | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 378 | 132
I-C-0182 | I | Modular / portable power | Motor 6 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | T-MOD-1 / T-MOD-2 firewall | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 378 | 132
I-C-0183 | I | Modular / portable power | Motor 1 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | T-MOD-1 | T-MOD-1: 13.8/230 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 378 | 84
I-C-0184 | I | Modular / portable power | Motor 2 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | T-MOD-1 | T-MOD-1: 13.8/230 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 378 | 84
I-C-0185 | I | Modular / portable power | Motor 3 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | T-MOD-1 | T-MOD-1: 13.8/230 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 378 | 84
I-C-0186 | I | Modular / portable power | Motor 4 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | T-MOD-1 | T-MOD-1: 13.8/230 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 378 | 84
I-C-0187 | I | Modular / portable power | Motor 5 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | T-MOD-1 | T-MOD-1: 13.8/230 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 378 | 84
I-C-0188 | I | Modular / portable power | Motor 6 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | T-MOD-1 | T-MOD-1: 13.8/230 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 378 | 84
I-C-0189 | I | Modular / portable power | Motor 1 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | T-MOD-2 | T-MOD-2: 13.8/230 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 189
I-C-0190 | I | Modular / portable power | Motor 2 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | T-MOD-2 | T-MOD-2: 13.8/230 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 189
I-C-0191 | I | Modular / portable power | Motor 3 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | T-MOD-2 | T-MOD-2: 13.8/230 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 189
I-C-0192 | I | Modular / portable power | Motor 4 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | T-MOD-2 | T-MOD-2: 13.8/230 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 189
I-C-0193 | I | Modular / portable power | Motor 5 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | T-MOD-2 | T-MOD-2: 13.8/230 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 189
I-C-0194 | I | Modular / portable power | Motor 6 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | T-MOD-2 | T-MOD-2: 13.8/230 kV | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 189
I-C-0195 | I | Modular / portable power | Motor 1 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | TM-1 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 3194 | 70
I-C-0196 | I | Modular / portable power | Motor 2 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | TM-1 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 3194 | 70
I-C-0197 | I | Modular / portable power | Motor 3 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | TM-1 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 3194 | 70
I-C-0198 | I | Modular / portable power | Motor 4 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | TM-1 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 3194 | 70
I-C-0199 | I | Modular / portable power | Motor 5 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | TM-1 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 3194 | 70
I-C-0200 | I | Modular / portable power | Motor 6 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | TM-1 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 3194 | 70
I-C-0201 | I | Modular / portable power | Motor 1 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | TM-2 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 3194 | 76
I-C-0202 | I | Modular / portable power | Motor 2 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | TM-2 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 3194 | 76
I-C-0203 | I | Modular / portable power | Motor 3 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | TM-2 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 3194 | 76
I-C-0204 | I | Modular / portable power | Motor 4 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | TM-2 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 3194 | 76
I-C-0205 | I | Modular / portable power | Motor 5 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | TM-2 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 3194 | 76
I-C-0206 | I | Modular / portable power | Motor 6 of 6: control / local station |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | TM-2 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 3194 | 76
I-C-0207 | I | Modular / portable power | Control |  | PCM: power control module |  | Water-injection skid | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | HV duct bank | 4299 | 87
I-F-0001 | I | Modular / portable power | Plant network / DCS fibre | CR | Control / admin building (main control room) |  | Lube oil / starting air / oily water building | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Duct bank | 2703 | 394
I-F-0002 | I | Modular / portable power | Plant network / DCS fibre | CR | Control / admin building (main control room) | MOD-EH | MOD-EH: 13.8 kV modular collector e-house | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Trench | 4273 | 36
I-F-0003 | I | Modular / portable power | Plant network / DCS fibre | CR | Control / admin building (main control room) |  | PCM: power control module | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Duct bank | 4696 | 36
I-F-0004 | I | Modular / portable power | Plant network / DCS fibre | CR | Control / admin building (main control room) |  | RICE CEMS | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Duct bank | 4436 | 135
I-F-0005 | I | Modular / portable power | Plant network / DCS fibre | CR | Control / admin building (main control room) | RICE | RICE engine hall (8 engines) | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Tray | 2186 | 334
I-F-0006 | I | Modular / portable power | Plant network / DCS fibre | CR | Control / admin building (main control room) | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Duct bank | 4656 | 56
I-F-0007 | I | Modular / portable power | Plant network / DCS fibre | CR | Control / admin building (main control room) | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Trench | 4681 | 36
I-F-0008 | I | Modular / portable power | Plant network / DCS fibre | CR | Control / admin building (main control room) | TM-1 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Trench | 3434 | 66
I-F-0009 | I | Modular / portable power | Plant network / DCS fibre | CR | Control / admin building (main control room) | TM-2 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Trench | 3434 | 72
I-FA-0001 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) |  | PCM: power control module |  | BS black-start switchgear | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 562 | 64
I-FA-0002 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) |  | PCM: power control module |  | Black-start genset (proposed; requires study) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 624 | 32
I-FA-0003 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) |  | PCM: power control module |  | Black-start genset (proposed; requires study) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 624 | 40
I-FA-0004 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) |  | PCM: power control module |  | CONDITIONAL: BESS black-start alternative | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 550 | 32
I-FA-0005 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) |  | PCM: power control module |  | CONDITIONAL: SC-1 inlet chiller / evaporative cooler | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 40 | 52
I-FA-0006 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) |  | PCM: power control module |  | CONDITIONAL: SC-2 inlet chiller / evaporative cooler | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | HV duct bank | 4528 | 38
I-FA-0007 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) | PAD-EH | PAD-EH 13.8 kV switchgear e-house | CONT-1 | CONT-1: containerized genset 13.8 kV (40 ft) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Surface | 298 | 37
I-FA-0008 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) | PAD-EH | PAD-EH 13.8 kV switchgear e-house | CONT-2 | CONT-2: containerized genset 13.8 kV (40 ft) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Surface | 267 | 37
I-FA-0009 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) | PAD-EH | PAD-EH 13.8 kV switchgear e-house | CONT-3 | CONT-3: containerized gas genset 13.8 kV (40 ft) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Surface | 191 | 32
I-FA-0010 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) | PAD-EH | PAD-EH 13.8 kV switchgear e-house | CONT-4 | CONT-4: containerized gas genset 13.8 kV (40 ft) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 62 | 81
I-FA-0011 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) | PAD-EH | PAD-EH 13.8 kV switchgear e-house | CONT-5 | CONT-5: containerized gas genset 13.8 kV (40 ft) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 25 | 58
I-FA-0012 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) | PAD-EH | PAD-EH 13.8 kV switchgear e-house | CONT-6 | CONT-6: containerized gas genset 13.8 kV (40 ft) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Surface | 228 | 46
I-FA-0013 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) | PAD-EH | PAD-EH 13.8 kV switchgear e-house | CONT-7 | CONT-7: containerized gas genset 13.8 kV (40 ft) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Surface | 228 | 46
I-FA-0014 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) | PAD-EH | PAD-EH 13.8 kV switchgear e-house | CONT-8 | CONT-8: containerized gas genset 13.8 kV (40 ft) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Surface | 16 | 117
I-FA-0015 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) | PAD-EH | PAD-EH 13.8 kV switchgear e-house | FC-10 | FC-10: SOFC module (Bloom ES5 class, 200-300 kW) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 286 | 50
I-FA-0016 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) | PAD-EH | PAD-EH 13.8 kV switchgear e-house | FC-11 | FC-11: SOFC module (Bloom ES5 class, 200-300 kW) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 272 | 50
I-FA-0017 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) | PAD-EH | PAD-EH 13.8 kV switchgear e-house | FC-12 | FC-12: SOFC module (Bloom ES5 class, 200-300 kW) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 272 | 41
I-FA-0018 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) |  | PCM: power control module |  | FC-1: SOFC module (Bloom ES5 class, 200-300 kW) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 1048 | 96
I-FA-0019 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) |  | PCM: power control module |  | FC-2: SOFC module (Bloom ES5 class, 200-300 kW) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 1048 | 82
I-FA-0020 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) |  | PCM: power control module |  | FC-3: SOFC module (Bloom ES5 class, 200-300 kW) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 1048 | 68
I-FA-0021 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) |  | PCM: power control module |  | FC-4: SOFC module (Bloom ES5 class, 200-300 kW) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 1048 | 54
I-FA-0022 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) | PAD-EH | PAD-EH 13.8 kV switchgear e-house |  | FC-5..12 inverter / AC cabinet / desulfurizer | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Surface | 202 | 37
I-FA-0023 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) | PAD-EH | PAD-EH 13.8 kV switchgear e-house | FC-5 | FC-5: SOFC module (Bloom ES5 class, 200-300 kW) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 356 | 50
I-FA-0024 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) | PAD-EH | PAD-EH 13.8 kV switchgear e-house | FC-6 | FC-6: SOFC module (Bloom ES5 class, 200-300 kW) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 342 | 50
I-FA-0025 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) | PAD-EH | PAD-EH 13.8 kV switchgear e-house | FC-7 | FC-7: SOFC module (Bloom ES5 class, 200-300 kW) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 328 | 50
I-FA-0026 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) | PAD-EH | PAD-EH 13.8 kV switchgear e-house | FC-8 | FC-8: SOFC module (Bloom ES5 class, 200-300 kW) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 314 | 50
I-FA-0027 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) | PAD-EH | PAD-EH 13.8 kV switchgear e-house | FC-9 | FC-9: SOFC module (Bloom ES5 class, 200-300 kW) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 300 | 50
I-FA-0028 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) |  | PCM: power control module |  | Fuel-cell inverter / AC cabinet / desulfurizer | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 1032 | 34
I-FA-0029 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) | PAD-EH | PAD-EH 13.8 kV switchgear e-house | GEN-E | GEN-E: enclosed industrial gas genset 2 MW | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Surface | 153 | 32
I-FA-0030 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) | PAD-EH | PAD-EH 13.8 kV switchgear e-house | GEN-O | GEN-O: open engine-generator skid | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Surface | 153 | 79
I-FA-0031 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) |  | PCM: power control module |  | Lube oil / starting air / oily water building | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 32 | 164
I-FA-0032 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) | PAD-EH | PAD-EH 13.8 kV switchgear e-house | MOB-1 | MOB-1: trailer genset | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Surface | 113 | 160
I-FA-0033 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) |  | PCM: power control module | MOD-EH | MOD-EH: 13.8 kV modular collector e-house | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 355 | 32
I-FA-0034 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) |  | PCM: power control module |  | MT-1: microturbine 1 MW (Capstone C1000 class) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 807 | 117
I-FA-0035 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) |  | PCM: power control module |  | MT-2: microturbine 1 MW (Capstone C1000 class) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 807 | 131
I-FA-0036 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) |  | PCM: power control module |  | MT-3: microturbine 1 MW (Capstone C1000 class) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 807 | 145
I-FA-0037 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) | PAD-EH | PAD-EH 13.8 kV switchgear e-house | MT-4 | MT-4: microturbine 1 MW (Capstone C1000 class) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Surface | 198 | 47
I-FA-0038 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) | PAD-EH | PAD-EH 13.8 kV switchgear e-house | MT-5 | MT-5: microturbine 1 MW (Capstone C1000 class) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Surface | 198 | 37
I-FA-0039 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) | PAD-EH | PAD-EH 13.8 kV switchgear e-house | MT-6 | MT-6: microturbine 1 MW (Capstone C1000 class) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Surface | 67 | 90
I-FA-0040 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) |  | PCM: power control module |  | PCM: power control module | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 32
I-FA-0041 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) |  | PCM: power control module |  | RICE CEMS | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 260 | 131
I-FA-0042 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) |  | PCM: power control module | RICE | RICE engine hall (8 engines) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 367 | 95
I-FA-0043 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) |  | PCM: power control module | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 40 | 52
I-FA-0044 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) |  | PCM: power control module | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | HV duct bank | 4478 | 38
I-FA-0045 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) | PAD-EH | PAD-EH 13.8 kV switchgear e-house | TM-1 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Surface | 382 | 50
I-FA-0046 | I | Modular / portable power | Fire alarm / F&G loop (to the local FACP / F&G node) | PAD-EH | PAD-EH 13.8 kV switchgear e-house | TM-2 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Surface | 386 | 52
I-I-0001 | I | Modular / portable power | Instrumentation |  | PCM: power control module |  | Aqueous ammonia (SC units) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | HV duct bank | 4299 | 38
I-I-0002 | I | Modular / portable power | Analog instrument to JB JB-Black-start genset-AI01: 20 x 1 pr (field cables) |  | Black-start genset (proposed; requires study) | JB-Black-start genset-AI01 | Black-start genset (proposed; requires study) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 59 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0003 | I | Modular / portable power | Home run JB-Black-start genset-AI01 to the control / marshalling room |  | PCM: power control module | JB-Black-start genset-AI01 | Black-start genset (proposed; requires study) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 624 | 32
I-I-0004 | I | Modular / portable power | Discrete device to JB JB-Black-start genset-DI01: 20 x 1 pr (field cables) |  | Black-start genset (proposed; requires study) | JB-Black-start genset-DI01 | Black-start genset (proposed; requires study) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 59 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0005 | I | Modular / portable power | Home run JB-Black-start genset-DI01 to the control / marshalling room |  | PCM: power control module | JB-Black-start genset-DI01 | Black-start genset (proposed; requires study) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 624 | 32
I-I-0006 | I | Modular / portable power | Analog instrument to JB JB-Black-start genset-AI01: 20 x 1 pr (field cables) |  | Black-start genset (proposed; requires study) | JB-Black-start genset-AI01 | Black-start genset (proposed; requires study) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 59 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0007 | I | Modular / portable power | Home run JB-Black-start genset-AI01 to the control / marshalling room |  | PCM: power control module | JB-Black-start genset-AI01 | Black-start genset (proposed; requires study) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 624 | 40
I-I-0008 | I | Modular / portable power | Discrete device to JB JB-Black-start genset-DI01: 20 x 1 pr (field cables) |  | Black-start genset (proposed; requires study) | JB-Black-start genset-DI01 | Black-start genset (proposed; requires study) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 59 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0009 | I | Modular / portable power | Home run JB-Black-start genset-DI01 to the control / marshalling room |  | PCM: power control module | JB-Black-start genset-DI01 | Black-start genset (proposed; requires study) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 624 | 40
I-I-0010 | I | Modular / portable power | Instrumentation |  | PCM: power control module |  | CONDITIONAL: BESS black-start alternative | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 32
I-I-0011 | I | Modular / portable power | Thermocouples |  | PCM: power control module |  | CONDITIONAL: BESS black-start alternative | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦12 pr¦16 | 12 pr | 16 | 1 | 1 |  |  |  | Duct bank | 550 | 32
I-I-0012 | I | Modular / portable power | Thermocouples |  | PCM: power control module |  | CONDITIONAL: BESS black-start alternative | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦12 pr¦16 | 12 pr | 16 | 1 | 1 |  |  |  | Duct bank | 550 | 32
I-I-0013 | I | Modular / portable power | Instrumentation |  | PCM: power control module |  | CONDITIONAL: SC-1 inlet chiller / evaporative cooler | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Duct bank | 40 | 52
I-I-0014 | I | Modular / portable power | Thermocouples |  | PCM: power control module |  | CONDITIONAL: SC-1 inlet chiller / evaporative cooler | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦12 pr¦16 | 12 pr | 16 | 1 | 1 |  |  |  | Duct bank | 40 | 52
I-I-0015 | I | Modular / portable power | Thermocouples |  | PCM: power control module |  | CONDITIONAL: SC-1 inlet chiller / evaporative cooler | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦12 pr¦16 | 12 pr | 16 | 1 | 1 |  |  |  | Duct bank | 40 | 52
I-I-0016 | I | Modular / portable power | Instrumentation |  | PCM: power control module |  | CONDITIONAL: SC-2 inlet chiller / evaporative cooler | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | HV duct bank | 4528 | 38
I-I-0017 | I | Modular / portable power | Thermocouples |  | PCM: power control module |  | CONDITIONAL: SC-2 inlet chiller / evaporative cooler | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦12 pr¦16 | 12 pr | 16 | 1 | 1 |  |  |  | HV duct bank | 4528 | 38
I-I-0018 | I | Modular / portable power | Thermocouples |  | PCM: power control module |  | CONDITIONAL: SC-2 inlet chiller / evaporative cooler | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦12 pr¦16 | 12 pr | 16 | 1 | 1 |  |  |  | HV duct bank | 4528 | 38
I-I-0019 | I | Modular / portable power | Analog instrument to JB JB-CONT-1-AI01: 20 x 1 pr (field cables) | CONT-1 | CONT-1: containerized genset 13.8 kV (40 ft) | JB-CONT-1-AI01 | CONT-1: containerized genset 13.8 kV (40 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0020 | I | Modular / portable power | Home run JB-CONT-1-AI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-CONT-1-AI01 | CONT-1: containerized genset 13.8 kV (40 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 298 | 37
I-I-0021 | I | Modular / portable power | Discrete device to JB JB-CONT-1-DI01: 20 x 1 pr (field cables) | CONT-1 | CONT-1: containerized genset 13.8 kV (40 ft) | JB-CONT-1-DI01 | CONT-1: containerized genset 13.8 kV (40 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0022 | I | Modular / portable power | Home run JB-CONT-1-DI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-CONT-1-DI01 | CONT-1: containerized genset 13.8 kV (40 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 298 | 37
I-I-0023 | I | Modular / portable power | Analog instrument to JB JB-CONT-2-AI01: 20 x 1 pr (field cables) | CONT-2 | CONT-2: containerized genset 13.8 kV (40 ft) | JB-CONT-2-AI01 | CONT-2: containerized genset 13.8 kV (40 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0024 | I | Modular / portable power | Home run JB-CONT-2-AI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-CONT-2-AI01 | CONT-2: containerized genset 13.8 kV (40 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 267 | 37
I-I-0025 | I | Modular / portable power | Discrete device to JB JB-CONT-2-DI01: 20 x 1 pr (field cables) | CONT-2 | CONT-2: containerized genset 13.8 kV (40 ft) | JB-CONT-2-DI01 | CONT-2: containerized genset 13.8 kV (40 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0026 | I | Modular / portable power | Home run JB-CONT-2-DI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-CONT-2-DI01 | CONT-2: containerized genset 13.8 kV (40 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 267 | 37
I-I-0027 | I | Modular / portable power | Analog instrument to JB JB-CONT-3-AI01: 20 x 1 pr (field cables) | CONT-3 | CONT-3: containerized gas genset 13.8 kV (40 ft) | JB-CONT-3-AI01 | CONT-3: containerized gas genset 13.8 kV (40 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0028 | I | Modular / portable power | Home run JB-CONT-3-AI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-CONT-3-AI01 | CONT-3: containerized gas genset 13.8 kV (40 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 191 | 32
I-I-0029 | I | Modular / portable power | Discrete device to JB JB-CONT-3-DI01: 20 x 1 pr (field cables) | CONT-3 | CONT-3: containerized gas genset 13.8 kV (40 ft) | JB-CONT-3-DI01 | CONT-3: containerized gas genset 13.8 kV (40 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0030 | I | Modular / portable power | Home run JB-CONT-3-DI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-CONT-3-DI01 | CONT-3: containerized gas genset 13.8 kV (40 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 191 | 32
I-I-0031 | I | Modular / portable power | Analog instrument to JB JB-CONT-4-AI01: 20 x 1 pr (field cables) | CONT-4 | CONT-4: containerized gas genset 13.8 kV (40 ft) | JB-CONT-4-AI01 | CONT-4: containerized gas genset 13.8 kV (40 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0032 | I | Modular / portable power | Home run JB-CONT-4-AI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-CONT-4-AI01 | CONT-4: containerized gas genset 13.8 kV (40 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 62 | 81
I-I-0033 | I | Modular / portable power | Discrete device to JB JB-CONT-4-DI01: 20 x 1 pr (field cables) | CONT-4 | CONT-4: containerized gas genset 13.8 kV (40 ft) | JB-CONT-4-DI01 | CONT-4: containerized gas genset 13.8 kV (40 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0034 | I | Modular / portable power | Home run JB-CONT-4-DI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-CONT-4-DI01 | CONT-4: containerized gas genset 13.8 kV (40 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 62 | 81
I-I-0035 | I | Modular / portable power | Analog instrument to JB JB-CONT-5-AI01: 20 x 1 pr (field cables) | CONT-5 | CONT-5: containerized gas genset 13.8 kV (40 ft) | JB-CONT-5-AI01 | CONT-5: containerized gas genset 13.8 kV (40 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0036 | I | Modular / portable power | Home run JB-CONT-5-AI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-CONT-5-AI01 | CONT-5: containerized gas genset 13.8 kV (40 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 25 | 58
I-I-0037 | I | Modular / portable power | Discrete device to JB JB-CONT-5-DI01: 20 x 1 pr (field cables) | CONT-5 | CONT-5: containerized gas genset 13.8 kV (40 ft) | JB-CONT-5-DI01 | CONT-5: containerized gas genset 13.8 kV (40 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0038 | I | Modular / portable power | Home run JB-CONT-5-DI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-CONT-5-DI01 | CONT-5: containerized gas genset 13.8 kV (40 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 25 | 58
I-I-0039 | I | Modular / portable power | Analog instrument to JB JB-CONT-6-AI01: 20 x 1 pr (field cables) | CONT-6 | CONT-6: containerized gas genset 13.8 kV (40 ft) | JB-CONT-6-AI01 | CONT-6: containerized gas genset 13.8 kV (40 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0040 | I | Modular / portable power | Home run JB-CONT-6-AI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-CONT-6-AI01 | CONT-6: containerized gas genset 13.8 kV (40 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 228 | 46
I-I-0041 | I | Modular / portable power | Discrete device to JB JB-CONT-6-DI01: 20 x 1 pr (field cables) | CONT-6 | CONT-6: containerized gas genset 13.8 kV (40 ft) | JB-CONT-6-DI01 | CONT-6: containerized gas genset 13.8 kV (40 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0042 | I | Modular / portable power | Home run JB-CONT-6-DI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-CONT-6-DI01 | CONT-6: containerized gas genset 13.8 kV (40 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 228 | 46
I-I-0043 | I | Modular / portable power | Analog instrument to JB JB-CONT-7-AI01: 20 x 1 pr (field cables) | CONT-7 | CONT-7: containerized gas genset 13.8 kV (40 ft) | JB-CONT-7-AI01 | CONT-7: containerized gas genset 13.8 kV (40 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0044 | I | Modular / portable power | Home run JB-CONT-7-AI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-CONT-7-AI01 | CONT-7: containerized gas genset 13.8 kV (40 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 228 | 46
I-I-0045 | I | Modular / portable power | Discrete device to JB JB-CONT-7-DI01: 20 x 1 pr (field cables) | CONT-7 | CONT-7: containerized gas genset 13.8 kV (40 ft) | JB-CONT-7-DI01 | CONT-7: containerized gas genset 13.8 kV (40 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0046 | I | Modular / portable power | Home run JB-CONT-7-DI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-CONT-7-DI01 | CONT-7: containerized gas genset 13.8 kV (40 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 228 | 46
I-I-0047 | I | Modular / portable power | Analog instrument to JB JB-CONT-8-AI01: 20 x 1 pr (field cables) | CONT-8 | CONT-8: containerized gas genset 13.8 kV (40 ft) | JB-CONT-8-AI01 | CONT-8: containerized gas genset 13.8 kV (40 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0048 | I | Modular / portable power | Home run JB-CONT-8-AI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-CONT-8-AI01 | CONT-8: containerized gas genset 13.8 kV (40 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 16 | 117
I-I-0049 | I | Modular / portable power | Discrete device to JB JB-CONT-8-DI01: 20 x 1 pr (field cables) | CONT-8 | CONT-8: containerized gas genset 13.8 kV (40 ft) | JB-CONT-8-DI01 | CONT-8: containerized gas genset 13.8 kV (40 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0050 | I | Modular / portable power | Home run JB-CONT-8-DI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-CONT-8-DI01 | CONT-8: containerized gas genset 13.8 kV (40 ft) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 16 | 117
I-I-0051 | I | Modular / portable power | Analog instrument to JB JB-Demin tank + trail-AI01: 4 x 1 pr (field cables) |  | Demin tank + trailer pad | JB-Demin tank + trail-AI01 | Demin tank + trailer pad | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 78 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0052 | I | Modular / portable power | Home run JB-Demin tank + trail-AI01 to the control / marshalling room |  | PCM: power control module | JB-Demin tank + trail-AI01 | Demin tank + trailer pad | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | HV duct bank | 4353 | 73
I-I-0053 | I | Modular / portable power | Discrete device to JB JB-Demin tank + trail-DI01: 4 x 1 pr (field cables) |  | Demin tank + trailer pad | JB-Demin tank + trail-DI01 | Demin tank + trailer pad | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 78 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0054 | I | Modular / portable power | Home run JB-Demin tank + trail-DI01 to the control / marshalling room |  | PCM: power control module | JB-Demin tank + trail-DI01 | Demin tank + trailer pad | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | HV duct bank | 4353 | 73
I-I-0055 | I | Modular / portable power | Analog instrument to JB JB-FC-10-AI01: 10 x 1 pr (field cables) | FC-10 | FC-10: SOFC module (Bloom ES5 class, 200-300 kW) | JB-FC-10-AI01 | FC-10: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0056 | I | Modular / portable power | Home run JB-FC-10-AI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-FC-10-AI01 | FC-10: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 286 | 50
I-I-0057 | I | Modular / portable power | Discrete device to JB JB-FC-10-DI01: 10 x 1 pr (field cables) | FC-10 | FC-10: SOFC module (Bloom ES5 class, 200-300 kW) | JB-FC-10-DI01 | FC-10: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0058 | I | Modular / portable power | Home run JB-FC-10-DI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-FC-10-DI01 | FC-10: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 286 | 50
I-I-0059 | I | Modular / portable power | Analog instrument to JB JB-FC-11-AI01: 10 x 1 pr (field cables) | FC-11 | FC-11: SOFC module (Bloom ES5 class, 200-300 kW) | JB-FC-11-AI01 | FC-11: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0060 | I | Modular / portable power | Home run JB-FC-11-AI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-FC-11-AI01 | FC-11: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 272 | 50
I-I-0061 | I | Modular / portable power | Discrete device to JB JB-FC-11-DI01: 10 x 1 pr (field cables) | FC-11 | FC-11: SOFC module (Bloom ES5 class, 200-300 kW) | JB-FC-11-DI01 | FC-11: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0062 | I | Modular / portable power | Home run JB-FC-11-DI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-FC-11-DI01 | FC-11: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 272 | 50
I-I-0063 | I | Modular / portable power | Analog instrument to JB JB-FC-12-AI01: 10 x 1 pr (field cables) | FC-12 | FC-12: SOFC module (Bloom ES5 class, 200-300 kW) | JB-FC-12-AI01 | FC-12: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0064 | I | Modular / portable power | Home run JB-FC-12-AI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-FC-12-AI01 | FC-12: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 272 | 41
I-I-0065 | I | Modular / portable power | Discrete device to JB JB-FC-12-DI01: 10 x 1 pr (field cables) | FC-12 | FC-12: SOFC module (Bloom ES5 class, 200-300 kW) | JB-FC-12-DI01 | FC-12: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0066 | I | Modular / portable power | Home run JB-FC-12-DI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-FC-12-DI01 | FC-12: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 272 | 41
I-I-0067 | I | Modular / portable power | Analog instrument to JB JB-FC-1: SOFC module -AI01: 10 x 1 pr (field cables) |  | FC-1: SOFC module (Bloom ES5 class, 200-300 kW) | JB-FC-1: SOFC module -AI01 | FC-1: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0068 | I | Modular / portable power | Home run JB-FC-1: SOFC module -AI01 to the control / marshalling room |  | PCM: power control module | JB-FC-1: SOFC module -AI01 | FC-1: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1048 | 96
I-I-0069 | I | Modular / portable power | Discrete device to JB JB-FC-1: SOFC module -DI01: 10 x 1 pr (field cables) |  | FC-1: SOFC module (Bloom ES5 class, 200-300 kW) | JB-FC-1: SOFC module -DI01 | FC-1: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0070 | I | Modular / portable power | Home run JB-FC-1: SOFC module -DI01 to the control / marshalling room |  | PCM: power control module | JB-FC-1: SOFC module -DI01 | FC-1: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1048 | 96
I-I-0071 | I | Modular / portable power | Analog instrument to JB JB-FC-2: SOFC module -AI01: 10 x 1 pr (field cables) |  | FC-2: SOFC module (Bloom ES5 class, 200-300 kW) | JB-FC-2: SOFC module -AI01 | FC-2: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0072 | I | Modular / portable power | Home run JB-FC-2: SOFC module -AI01 to the control / marshalling room |  | PCM: power control module | JB-FC-2: SOFC module -AI01 | FC-2: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1048 | 82
I-I-0073 | I | Modular / portable power | Discrete device to JB JB-FC-2: SOFC module -DI01: 10 x 1 pr (field cables) |  | FC-2: SOFC module (Bloom ES5 class, 200-300 kW) | JB-FC-2: SOFC module -DI01 | FC-2: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0074 | I | Modular / portable power | Home run JB-FC-2: SOFC module -DI01 to the control / marshalling room |  | PCM: power control module | JB-FC-2: SOFC module -DI01 | FC-2: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1048 | 82
I-I-0075 | I | Modular / portable power | Analog instrument to JB JB-FC-3: SOFC module -AI01: 10 x 1 pr (field cables) |  | FC-3: SOFC module (Bloom ES5 class, 200-300 kW) | JB-FC-3: SOFC module -AI01 | FC-3: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0076 | I | Modular / portable power | Home run JB-FC-3: SOFC module -AI01 to the control / marshalling room |  | PCM: power control module | JB-FC-3: SOFC module -AI01 | FC-3: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1048 | 68
I-I-0077 | I | Modular / portable power | Discrete device to JB JB-FC-3: SOFC module -DI01: 10 x 1 pr (field cables) |  | FC-3: SOFC module (Bloom ES5 class, 200-300 kW) | JB-FC-3: SOFC module -DI01 | FC-3: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0078 | I | Modular / portable power | Home run JB-FC-3: SOFC module -DI01 to the control / marshalling room |  | PCM: power control module | JB-FC-3: SOFC module -DI01 | FC-3: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1048 | 68
I-I-0079 | I | Modular / portable power | Analog instrument to JB JB-FC-4: SOFC module -AI01: 10 x 1 pr (field cables) |  | FC-4: SOFC module (Bloom ES5 class, 200-300 kW) | JB-FC-4: SOFC module -AI01 | FC-4: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0080 | I | Modular / portable power | Home run JB-FC-4: SOFC module -AI01 to the control / marshalling room |  | PCM: power control module | JB-FC-4: SOFC module -AI01 | FC-4: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1048 | 54
I-I-0081 | I | Modular / portable power | Discrete device to JB JB-FC-4: SOFC module -DI01: 10 x 1 pr (field cables) |  | FC-4: SOFC module (Bloom ES5 class, 200-300 kW) | JB-FC-4: SOFC module -DI01 | FC-4: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0082 | I | Modular / portable power | Home run JB-FC-4: SOFC module -DI01 to the control / marshalling room |  | PCM: power control module | JB-FC-4: SOFC module -DI01 | FC-4: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1048 | 54
I-I-0083 | I | Modular / portable power | Instrumentation | PAD-EH | PAD-EH 13.8 kV switchgear e-house |  | FC-5..12 inverter / AC cabinet / desulfurizer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Surface | 202 | 37
I-I-0084 | I | Modular / portable power | Thermocouples | PAD-EH | PAD-EH 13.8 kV switchgear e-house |  | FC-5..12 inverter / AC cabinet / desulfurizer | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦12 pr¦16 | 12 pr | 16 | 1 | 1 |  |  |  | Surface | 202 | 37
I-I-0085 | I | Modular / portable power | Thermocouples | PAD-EH | PAD-EH 13.8 kV switchgear e-house |  | FC-5..12 inverter / AC cabinet / desulfurizer | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦12 pr¦16 | 12 pr | 16 | 1 | 1 |  |  |  | Surface | 202 | 37
I-I-0086 | I | Modular / portable power | Analog instrument to JB JB-FC-5-AI01: 10 x 1 pr (field cables) | FC-5 | FC-5: SOFC module (Bloom ES5 class, 200-300 kW) | JB-FC-5-AI01 | FC-5: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0087 | I | Modular / portable power | Home run JB-FC-5-AI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-FC-5-AI01 | FC-5: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 356 | 50
I-I-0088 | I | Modular / portable power | Discrete device to JB JB-FC-5-DI01: 10 x 1 pr (field cables) | FC-5 | FC-5: SOFC module (Bloom ES5 class, 200-300 kW) | JB-FC-5-DI01 | FC-5: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0089 | I | Modular / portable power | Home run JB-FC-5-DI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-FC-5-DI01 | FC-5: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 356 | 50
I-I-0090 | I | Modular / portable power | Analog instrument to JB JB-FC-6-AI01: 10 x 1 pr (field cables) | FC-6 | FC-6: SOFC module (Bloom ES5 class, 200-300 kW) | JB-FC-6-AI01 | FC-6: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0091 | I | Modular / portable power | Home run JB-FC-6-AI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-FC-6-AI01 | FC-6: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 342 | 50
I-I-0092 | I | Modular / portable power | Discrete device to JB JB-FC-6-DI01: 10 x 1 pr (field cables) | FC-6 | FC-6: SOFC module (Bloom ES5 class, 200-300 kW) | JB-FC-6-DI01 | FC-6: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0093 | I | Modular / portable power | Home run JB-FC-6-DI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-FC-6-DI01 | FC-6: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 342 | 50
I-I-0094 | I | Modular / portable power | Analog instrument to JB JB-FC-7-AI01: 10 x 1 pr (field cables) | FC-7 | FC-7: SOFC module (Bloom ES5 class, 200-300 kW) | JB-FC-7-AI01 | FC-7: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0095 | I | Modular / portable power | Home run JB-FC-7-AI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-FC-7-AI01 | FC-7: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 328 | 50
I-I-0096 | I | Modular / portable power | Discrete device to JB JB-FC-7-DI01: 10 x 1 pr (field cables) | FC-7 | FC-7: SOFC module (Bloom ES5 class, 200-300 kW) | JB-FC-7-DI01 | FC-7: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0097 | I | Modular / portable power | Home run JB-FC-7-DI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-FC-7-DI01 | FC-7: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 328 | 50
I-I-0098 | I | Modular / portable power | Analog instrument to JB JB-FC-8-AI01: 10 x 1 pr (field cables) | FC-8 | FC-8: SOFC module (Bloom ES5 class, 200-300 kW) | JB-FC-8-AI01 | FC-8: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0099 | I | Modular / portable power | Home run JB-FC-8-AI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-FC-8-AI01 | FC-8: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 314 | 50
I-I-0100 | I | Modular / portable power | Discrete device to JB JB-FC-8-DI01: 10 x 1 pr (field cables) | FC-8 | FC-8: SOFC module (Bloom ES5 class, 200-300 kW) | JB-FC-8-DI01 | FC-8: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0101 | I | Modular / portable power | Home run JB-FC-8-DI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-FC-8-DI01 | FC-8: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 314 | 50
I-I-0102 | I | Modular / portable power | Analog instrument to JB JB-FC-9-AI01: 10 x 1 pr (field cables) | FC-9 | FC-9: SOFC module (Bloom ES5 class, 200-300 kW) | JB-FC-9-AI01 | FC-9: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0103 | I | Modular / portable power | Home run JB-FC-9-AI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-FC-9-AI01 | FC-9: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 300 | 50
I-I-0104 | I | Modular / portable power | Discrete device to JB JB-FC-9-DI01: 10 x 1 pr (field cables) | FC-9 | FC-9: SOFC module (Bloom ES5 class, 200-300 kW) | JB-FC-9-DI01 | FC-9: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0105 | I | Modular / portable power | Home run JB-FC-9-DI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-FC-9-DI01 | FC-9: SOFC module (Bloom ES5 class, 200-300 kW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 300 | 50
I-I-0106 | I | Modular / portable power | Instrumentation |  | PCM: power control module |  | Fuel-cell inverter / AC cabinet / desulfurizer | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Duct bank | 1032 | 34
I-I-0107 | I | Modular / portable power | Thermocouples |  | PCM: power control module |  | Fuel-cell inverter / AC cabinet / desulfurizer | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦12 pr¦16 | 12 pr | 16 | 1 | 1 |  |  |  | Duct bank | 1032 | 34
I-I-0108 | I | Modular / portable power | Thermocouples |  | PCM: power control module |  | Fuel-cell inverter / AC cabinet / desulfurizer | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦12 pr¦16 | 12 pr | 16 | 1 | 1 |  |  |  | Duct bank | 1032 | 34
I-I-0109 | I | Modular / portable power | Analog instrument to JB JB-Fuel-gas compresso-AI01: 20 x 1 pr (field cables) |  | Fuel-gas compressors 3 x 100% electric | JB-Fuel-gas compresso-AI01 | Fuel-gas compressors 3 x 100% electric | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 103 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0110 | I | Modular / portable power | Home run JB-Fuel-gas compresso-AI01 to the control / marshalling room |  | PCM: power control module | JB-Fuel-gas compresso-AI01 | Fuel-gas compressors 3 x 100% electric | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | HV duct bank | 4433 | 38
I-I-0111 | I | Modular / portable power | Analog instrument to JB JB-Fuel-gas compresso-AI02: 10 x 1 pr (field cables) |  | Fuel-gas compressors 3 x 100% electric | JB-Fuel-gas compresso-AI02 | Fuel-gas compressors 3 x 100% electric | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 103 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0112 | I | Modular / portable power | Home run JB-Fuel-gas compresso-AI02 to the control / marshalling room |  | PCM: power control module | JB-Fuel-gas compresso-AI02 | Fuel-gas compressors 3 x 100% electric | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | HV duct bank | 4433 | 38
I-I-0113 | I | Modular / portable power | Discrete device to JB JB-Fuel-gas compresso-DI01: 20 x 1 pr (field cables) |  | Fuel-gas compressors 3 x 100% electric | JB-Fuel-gas compresso-DI01 | Fuel-gas compressors 3 x 100% electric | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 103 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0114 | I | Modular / portable power | Home run JB-Fuel-gas compresso-DI01 to the control / marshalling room |  | PCM: power control module | JB-Fuel-gas compresso-DI01 | Fuel-gas compressors 3 x 100% electric | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | HV duct bank | 4433 | 38
I-I-0115 | I | Modular / portable power | RTD to JB JB-Fuel-gas compresso-RTD01: 10 x 1 tri (field cables) |  | Fuel-gas compressors 3 x 100% electric | JB-Fuel-gas compresso-RTD01 | Fuel-gas compressors 3 x 100% electric | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 103 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0116 | I | Modular / portable power | Home run JB-Fuel-gas compresso-RTD01 to the control / marshalling room |  | PCM: power control module | JB-Fuel-gas compresso-RTD01 | Fuel-gas compressors 3 x 100% electric | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | HV duct bank | 4433 | 38
I-I-0117 | I | Modular / portable power | RTD to JB JB-Fuel-gas compresso-RTD02: 2 x 1 tri (field cables) |  | Fuel-gas compressors 3 x 100% electric | JB-Fuel-gas compresso-RTD02 | Fuel-gas compressors 3 x 100% electric | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 2 | 1 |  |  |  | Tray / conduit | 103 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0118 | I | Modular / portable power | Home run JB-Fuel-gas compresso-RTD02 to the control / marshalling room |  | PCM: power control module | JB-Fuel-gas compresso-RTD02 | Fuel-gas compressors 3 x 100% electric | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | HV duct bank | 4433 | 38
I-I-0119 | I | Modular / portable power | Analog instrument to JB JB-GEN-E-AI01: 20 x 1 pr (field cables) | GEN-E | GEN-E: enclosed industrial gas genset 2 MW | JB-GEN-E-AI01 | GEN-E: enclosed industrial gas genset 2 MW | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 60 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0120 | I | Modular / portable power | Home run JB-GEN-E-AI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-GEN-E-AI01 | GEN-E: enclosed industrial gas genset 2 MW | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 153 | 32
I-I-0121 | I | Modular / portable power | Discrete device to JB JB-GEN-E-DI01: 20 x 1 pr (field cables) | GEN-E | GEN-E: enclosed industrial gas genset 2 MW | JB-GEN-E-DI01 | GEN-E: enclosed industrial gas genset 2 MW | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 60 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0122 | I | Modular / portable power | Home run JB-GEN-E-DI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-GEN-E-DI01 | GEN-E: enclosed industrial gas genset 2 MW | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 153 | 32
I-I-0123 | I | Modular / portable power | Analog instrument to JB JB-GEN-O-AI01: 20 x 1 pr (field cables) | GEN-O | GEN-O: open engine-generator skid | JB-GEN-O-AI01 | GEN-O: open engine-generator skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0124 | I | Modular / portable power | Home run JB-GEN-O-AI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-GEN-O-AI01 | GEN-O: open engine-generator skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 153 | 79
I-I-0125 | I | Modular / portable power | Discrete device to JB JB-GEN-O-DI01: 20 x 1 pr (field cables) | GEN-O | GEN-O: open engine-generator skid | JB-GEN-O-DI01 | GEN-O: open engine-generator skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0126 | I | Modular / portable power | Home run JB-GEN-O-DI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-GEN-O-DI01 | GEN-O: open engine-generator skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 153 | 79
I-I-0127 | I | Modular / portable power | Instrumentation |  | PCM: power control module |  | Gas conditioning skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 32 | 94
I-I-0128 | I | Modular / portable power | Instrumentation |  | PCM: power control module |  | Gas conditioning skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Tray | 32 | 94
I-I-0129 | I | Modular / portable power | Analog instrument to JB JB-MOB-1-AI01: 20 x 1 pr (field cables) | MOB-1 | MOB-1: trailer genset | JB-MOB-1-AI01 | MOB-1: trailer genset | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 61 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0130 | I | Modular / portable power | Home run JB-MOB-1-AI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-MOB-1-AI01 | MOB-1: trailer genset | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 113 | 160
I-I-0131 | I | Modular / portable power | Discrete device to JB JB-MOB-1-DI01: 20 x 1 pr (field cables) | MOB-1 | MOB-1: trailer genset | JB-MOB-1-DI01 | MOB-1: trailer genset | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 61 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0132 | I | Modular / portable power | Home run JB-MOB-1-DI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-MOB-1-DI01 | MOB-1: trailer genset | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 113 | 160
I-I-0133 | I | Modular / portable power | Instrumentation |  | PCM: power control module |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Duct bank | 773 | 34
I-I-0134 | I | Modular / portable power | Analog instrument to JB JB-MT-1: microturbine-AI01: 6 x 1 pr (field cables) |  | MT-1: microturbine 1 MW (Capstone C1000 class) | JB-MT-1: microturbine-AI01 | MT-1: microturbine 1 MW (Capstone C1000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 47 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0135 | I | Modular / portable power | Home run JB-MT-1: microturbine-AI01 to the control / marshalling room |  | PCM: power control module | JB-MT-1: microturbine-AI01 | MT-1: microturbine 1 MW (Capstone C1000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 807 | 117
I-I-0136 | I | Modular / portable power | Discrete device to JB JB-MT-1: microturbine-DI01: 6 x 1 pr (field cables) |  | MT-1: microturbine 1 MW (Capstone C1000 class) | JB-MT-1: microturbine-DI01 | MT-1: microturbine 1 MW (Capstone C1000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 47 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0137 | I | Modular / portable power | Home run JB-MT-1: microturbine-DI01 to the control / marshalling room |  | PCM: power control module | JB-MT-1: microturbine-DI01 | MT-1: microturbine 1 MW (Capstone C1000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 807 | 117
I-I-0138 | I | Modular / portable power | Analog instrument to JB JB-MT-2: microturbine-AI01: 6 x 1 pr (field cables) |  | MT-2: microturbine 1 MW (Capstone C1000 class) | JB-MT-2: microturbine-AI01 | MT-2: microturbine 1 MW (Capstone C1000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 47 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0139 | I | Modular / portable power | Home run JB-MT-2: microturbine-AI01 to the control / marshalling room |  | PCM: power control module | JB-MT-2: microturbine-AI01 | MT-2: microturbine 1 MW (Capstone C1000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 807 | 131
I-I-0140 | I | Modular / portable power | Discrete device to JB JB-MT-2: microturbine-DI01: 6 x 1 pr (field cables) |  | MT-2: microturbine 1 MW (Capstone C1000 class) | JB-MT-2: microturbine-DI01 | MT-2: microturbine 1 MW (Capstone C1000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 47 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0141 | I | Modular / portable power | Home run JB-MT-2: microturbine-DI01 to the control / marshalling room |  | PCM: power control module | JB-MT-2: microturbine-DI01 | MT-2: microturbine 1 MW (Capstone C1000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 807 | 131
I-I-0142 | I | Modular / portable power | Analog instrument to JB JB-MT-3: microturbine-AI01: 6 x 1 pr (field cables) |  | MT-3: microturbine 1 MW (Capstone C1000 class) | JB-MT-3: microturbine-AI01 | MT-3: microturbine 1 MW (Capstone C1000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 47 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0143 | I | Modular / portable power | Home run JB-MT-3: microturbine-AI01 to the control / marshalling room |  | PCM: power control module | JB-MT-3: microturbine-AI01 | MT-3: microturbine 1 MW (Capstone C1000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 807 | 145
I-I-0144 | I | Modular / portable power | Discrete device to JB JB-MT-3: microturbine-DI01: 6 x 1 pr (field cables) |  | MT-3: microturbine 1 MW (Capstone C1000 class) | JB-MT-3: microturbine-DI01 | MT-3: microturbine 1 MW (Capstone C1000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 47 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0145 | I | Modular / portable power | Home run JB-MT-3: microturbine-DI01 to the control / marshalling room |  | PCM: power control module | JB-MT-3: microturbine-DI01 | MT-3: microturbine 1 MW (Capstone C1000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 807 | 145
I-I-0146 | I | Modular / portable power | Analog instrument to JB JB-MT-4-AI01: 6 x 1 pr (field cables) | MT-4 | MT-4: microturbine 1 MW (Capstone C1000 class) | JB-MT-4-AI01 | MT-4: microturbine 1 MW (Capstone C1000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 47 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0147 | I | Modular / portable power | Home run JB-MT-4-AI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-MT-4-AI01 | MT-4: microturbine 1 MW (Capstone C1000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 198 | 47
I-I-0148 | I | Modular / portable power | Discrete device to JB JB-MT-4-DI01: 6 x 1 pr (field cables) | MT-4 | MT-4: microturbine 1 MW (Capstone C1000 class) | JB-MT-4-DI01 | MT-4: microturbine 1 MW (Capstone C1000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 47 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0149 | I | Modular / portable power | Home run JB-MT-4-DI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-MT-4-DI01 | MT-4: microturbine 1 MW (Capstone C1000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 198 | 47
I-I-0150 | I | Modular / portable power | Analog instrument to JB JB-MT-5-AI01: 6 x 1 pr (field cables) | MT-5 | MT-5: microturbine 1 MW (Capstone C1000 class) | JB-MT-5-AI01 | MT-5: microturbine 1 MW (Capstone C1000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 47 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0151 | I | Modular / portable power | Home run JB-MT-5-AI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-MT-5-AI01 | MT-5: microturbine 1 MW (Capstone C1000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 198 | 37
I-I-0152 | I | Modular / portable power | Discrete device to JB JB-MT-5-DI01: 6 x 1 pr (field cables) | MT-5 | MT-5: microturbine 1 MW (Capstone C1000 class) | JB-MT-5-DI01 | MT-5: microturbine 1 MW (Capstone C1000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 47 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0153 | I | Modular / portable power | Home run JB-MT-5-DI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-MT-5-DI01 | MT-5: microturbine 1 MW (Capstone C1000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 198 | 37
I-I-0154 | I | Modular / portable power | Analog instrument to JB JB-MT-6-AI01: 6 x 1 pr (field cables) | MT-6 | MT-6: microturbine 1 MW (Capstone C1000 class) | JB-MT-6-AI01 | MT-6: microturbine 1 MW (Capstone C1000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 47 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0155 | I | Modular / portable power | Home run JB-MT-6-AI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-MT-6-AI01 | MT-6: microturbine 1 MW (Capstone C1000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 67 | 90
I-I-0156 | I | Modular / portable power | Discrete device to JB JB-MT-6-DI01: 6 x 1 pr (field cables) | MT-6 | MT-6: microturbine 1 MW (Capstone C1000 class) | JB-MT-6-DI01 | MT-6: microturbine 1 MW (Capstone C1000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 47 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0157 | I | Modular / portable power | Home run JB-MT-6-DI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-MT-6-DI01 | MT-6: microturbine 1 MW (Capstone C1000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 67 | 90
I-I-0158 | I | Modular / portable power | Analog instrument to JB JB-RICE 1 SCR + oxida-AI01: 10 x 1 pr (field cables) |  | RICE 1 SCR + oxidation catalyst and stack | JB-RICE 1 SCR + oxida-AI01 | RICE 1 SCR + oxidation catalyst and stack | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 92 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0159 | I | Modular / portable power | Home run JB-RICE 1 SCR + oxida-AI01 to the control / marshalling room |  | PCM: power control module | JB-RICE 1 SCR + oxida-AI01 | RICE 1 SCR + oxidation catalyst and stack | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 470 | 160
I-I-0160 | I | Modular / portable power | Discrete device to JB JB-RICE 1 SCR + oxida-DI01: 6 x 1 pr (field cables) |  | RICE 1 SCR + oxidation catalyst and stack | JB-RICE 1 SCR + oxida-DI01 | RICE 1 SCR + oxidation catalyst and stack | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 92 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0161 | I | Modular / portable power | Home run JB-RICE 1 SCR + oxida-DI01 to the control / marshalling room |  | PCM: power control module | JB-RICE 1 SCR + oxida-DI01 | RICE 1 SCR + oxidation catalyst and stack | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 470 | 160
I-I-0162 | I | Modular / portable power | Analog instrument to JB JB-RICE 1 radiators (-AI01: 5 x 1 pr (field cables) |  | RICE 1 radiators (5) | JB-RICE 1 radiators (-AI01 | RICE 1 radiators (5) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 5 | 1 |  |  |  | Tray / conduit | 80 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0163 | I | Modular / portable power | Home run JB-RICE 1 radiators (-AI01 to the control / marshalling room |  | PCM: power control module | JB-RICE 1 radiators (-AI01 | RICE 1 radiators (5) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 745 | 139
I-I-0164 | I | Modular / portable power | Discrete device to JB JB-RICE 1 radiators (-DI01: 10 x 1 pr (field cables) |  | RICE 1 radiators (5) | JB-RICE 1 radiators (-DI01 | RICE 1 radiators (5) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 80 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0165 | I | Modular / portable power | Home run JB-RICE 1 radiators (-DI01 to the control / marshalling room |  | PCM: power control module | JB-RICE 1 radiators (-DI01 | RICE 1 radiators (5) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 745 | 139
I-I-0166 | I | Modular / portable power | Analog instrument to JB JB-RICE 2 SCR + oxida-AI01: 10 x 1 pr (field cables) |  | RICE 2 SCR + oxidation catalyst and stack | JB-RICE 2 SCR + oxida-AI01 | RICE 2 SCR + oxidation catalyst and stack | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 92 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0167 | I | Modular / portable power | Home run JB-RICE 2 SCR + oxida-AI01 to the control / marshalling room |  | PCM: power control module | JB-RICE 2 SCR + oxida-AI01 | RICE 2 SCR + oxidation catalyst and stack | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 470 | 132
I-I-0168 | I | Modular / portable power | Discrete device to JB JB-RICE 2 SCR + oxida-DI01: 6 x 1 pr (field cables) |  | RICE 2 SCR + oxidation catalyst and stack | JB-RICE 2 SCR + oxida-DI01 | RICE 2 SCR + oxidation catalyst and stack | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 92 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0169 | I | Modular / portable power | Home run JB-RICE 2 SCR + oxida-DI01 to the control / marshalling room |  | PCM: power control module | JB-RICE 2 SCR + oxida-DI01 | RICE 2 SCR + oxidation catalyst and stack | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 470 | 132
I-I-0170 | I | Modular / portable power | Analog instrument to JB JB-RICE 2 radiators (-AI01: 5 x 1 pr (field cables) |  | RICE 2 radiators (5) | JB-RICE 2 radiators (-AI01 | RICE 2 radiators (5) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 5 | 1 |  |  |  | Tray / conduit | 80 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0171 | I | Modular / portable power | Home run JB-RICE 2 radiators (-AI01 to the control / marshalling room |  | PCM: power control module | JB-RICE 2 radiators (-AI01 | RICE 2 radiators (5) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 192
I-I-0172 | I | Modular / portable power | Discrete device to JB JB-RICE 2 radiators (-DI01: 10 x 1 pr (field cables) |  | RICE 2 radiators (5) | JB-RICE 2 radiators (-DI01 | RICE 2 radiators (5) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 80 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0173 | I | Modular / portable power | Home run JB-RICE 2 radiators (-DI01 to the control / marshalling room |  | PCM: power control module | JB-RICE 2 radiators (-DI01 | RICE 2 radiators (5) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 192
I-I-0174 | I | Modular / portable power | Analog instrument to JB JB-RICE 3 SCR + oxida-AI01: 10 x 1 pr (field cables) |  | RICE 3 SCR + oxidation catalyst and stack | JB-RICE 3 SCR + oxida-AI01 | RICE 3 SCR + oxidation catalyst and stack | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 92 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0175 | I | Modular / portable power | Home run JB-RICE 3 SCR + oxida-AI01 to the control / marshalling room |  | PCM: power control module | JB-RICE 3 SCR + oxida-AI01 | RICE 3 SCR + oxidation catalyst and stack | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 470 | 104
I-I-0176 | I | Modular / portable power | Discrete device to JB JB-RICE 3 SCR + oxida-DI01: 6 x 1 pr (field cables) |  | RICE 3 SCR + oxidation catalyst and stack | JB-RICE 3 SCR + oxida-DI01 | RICE 3 SCR + oxidation catalyst and stack | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 92 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0177 | I | Modular / portable power | Home run JB-RICE 3 SCR + oxida-DI01 to the control / marshalling room |  | PCM: power control module | JB-RICE 3 SCR + oxida-DI01 | RICE 3 SCR + oxidation catalyst and stack | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 470 | 104
I-I-0178 | I | Modular / portable power | Analog instrument to JB JB-RICE 3 radiators (-AI01: 5 x 1 pr (field cables) |  | RICE 3 radiators (5) | JB-RICE 3 radiators (-AI01 | RICE 3 radiators (5) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 5 | 1 |  |  |  | Tray / conduit | 80 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0179 | I | Modular / portable power | Home run JB-RICE 3 radiators (-AI01 to the control / marshalling room |  | PCM: power control module | JB-RICE 3 radiators (-AI01 | RICE 3 radiators (5) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 32 | 232
I-I-0180 | I | Modular / portable power | Discrete device to JB JB-RICE 3 radiators (-DI01: 10 x 1 pr (field cables) |  | RICE 3 radiators (5) | JB-RICE 3 radiators (-DI01 | RICE 3 radiators (5) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 80 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0181 | I | Modular / portable power | Home run JB-RICE 3 radiators (-DI01 to the control / marshalling room |  | PCM: power control module | JB-RICE 3 radiators (-DI01 | RICE 3 radiators (5) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 32 | 232
I-I-0182 | I | Modular / portable power | Analog instrument to JB JB-RICE 4 SCR + oxida-AI01: 10 x 1 pr (field cables) |  | RICE 4 SCR + oxidation catalyst and stack | JB-RICE 4 SCR + oxida-AI01 | RICE 4 SCR + oxidation catalyst and stack | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 92 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0183 | I | Modular / portable power | Home run JB-RICE 4 SCR + oxida-AI01 to the control / marshalling room |  | PCM: power control module | JB-RICE 4 SCR + oxida-AI01 | RICE 4 SCR + oxidation catalyst and stack | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 470 | 76
I-I-0184 | I | Modular / portable power | Discrete device to JB JB-RICE 4 SCR + oxida-DI01: 6 x 1 pr (field cables) |  | RICE 4 SCR + oxidation catalyst and stack | JB-RICE 4 SCR + oxida-DI01 | RICE 4 SCR + oxidation catalyst and stack | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 92 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0185 | I | Modular / portable power | Home run JB-RICE 4 SCR + oxida-DI01 to the control / marshalling room |  | PCM: power control module | JB-RICE 4 SCR + oxida-DI01 | RICE 4 SCR + oxidation catalyst and stack | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 470 | 76
I-I-0186 | I | Modular / portable power | Analog instrument to JB JB-RICE 4 radiators (-AI01: 5 x 1 pr (field cables) |  | RICE 4 radiators (5) | JB-RICE 4 radiators (-AI01 | RICE 4 radiators (5) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 5 | 1 |  |  |  | Tray / conduit | 80 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0187 | I | Modular / portable power | Home run JB-RICE 4 radiators (-AI01 to the control / marshalling room |  | PCM: power control module | JB-RICE 4 radiators (-AI01 | RICE 4 radiators (5) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 206
I-I-0188 | I | Modular / portable power | Discrete device to JB JB-RICE 4 radiators (-DI01: 10 x 1 pr (field cables) |  | RICE 4 radiators (5) | JB-RICE 4 radiators (-DI01 | RICE 4 radiators (5) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 80 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0189 | I | Modular / portable power | Home run JB-RICE 4 radiators (-DI01 to the control / marshalling room |  | PCM: power control module | JB-RICE 4 radiators (-DI01 | RICE 4 radiators (5) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 206
I-I-0190 | I | Modular / portable power | Analog instrument to JB JB-RICE 5 SCR + oxida-AI01: 10 x 1 pr (field cables) |  | RICE 5 SCR + oxidation catalyst and stack | JB-RICE 5 SCR + oxida-AI01 | RICE 5 SCR + oxidation catalyst and stack | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 92 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0191 | I | Modular / portable power | Home run JB-RICE 5 SCR + oxida-AI01 to the control / marshalling room |  | PCM: power control module | JB-RICE 5 SCR + oxida-AI01 | RICE 5 SCR + oxidation catalyst and stack | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 322 | 196
I-I-0192 | I | Modular / portable power | Discrete device to JB JB-RICE 5 SCR + oxida-DI01: 6 x 1 pr (field cables) |  | RICE 5 SCR + oxidation catalyst and stack | JB-RICE 5 SCR + oxida-DI01 | RICE 5 SCR + oxidation catalyst and stack | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 92 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0193 | I | Modular / portable power | Home run JB-RICE 5 SCR + oxida-DI01 to the control / marshalling room |  | PCM: power control module | JB-RICE 5 SCR + oxida-DI01 | RICE 5 SCR + oxidation catalyst and stack | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 322 | 196
I-I-0194 | I | Modular / portable power | Analog instrument to JB JB-RICE 5 radiators (-AI01: 5 x 1 pr (field cables) |  | RICE 5 radiators (5) | JB-RICE 5 radiators (-AI01 | RICE 5 radiators (5) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 5 | 1 |  |  |  | Tray / conduit | 80 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0195 | I | Modular / portable power | Home run JB-RICE 5 radiators (-AI01 to the control / marshalling room |  | PCM: power control module | JB-RICE 5 radiators (-AI01 | RICE 5 radiators (5) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 178
I-I-0196 | I | Modular / portable power | Discrete device to JB JB-RICE 5 radiators (-DI01: 10 x 1 pr (field cables) |  | RICE 5 radiators (5) | JB-RICE 5 radiators (-DI01 | RICE 5 radiators (5) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 80 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0197 | I | Modular / portable power | Home run JB-RICE 5 radiators (-DI01 to the control / marshalling room |  | PCM: power control module | JB-RICE 5 radiators (-DI01 | RICE 5 radiators (5) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 178
I-I-0198 | I | Modular / portable power | Analog instrument to JB JB-RICE 6 SCR + oxida-AI01: 10 x 1 pr (field cables) |  | RICE 6 SCR + oxidation catalyst and stack | JB-RICE 6 SCR + oxida-AI01 | RICE 6 SCR + oxidation catalyst and stack | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 92 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0199 | I | Modular / portable power | Home run JB-RICE 6 SCR + oxida-AI01 to the control / marshalling room |  | PCM: power control module | JB-RICE 6 SCR + oxida-AI01 | RICE 6 SCR + oxidation catalyst and stack | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 322 | 168
I-I-0200 | I | Modular / portable power | Discrete device to JB JB-RICE 6 SCR + oxida-DI01: 6 x 1 pr (field cables) |  | RICE 6 SCR + oxidation catalyst and stack | JB-RICE 6 SCR + oxida-DI01 | RICE 6 SCR + oxidation catalyst and stack | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 92 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0201 | I | Modular / portable power | Home run JB-RICE 6 SCR + oxida-DI01 to the control / marshalling room |  | PCM: power control module | JB-RICE 6 SCR + oxida-DI01 | RICE 6 SCR + oxidation catalyst and stack | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 322 | 168
I-I-0202 | I | Modular / portable power | Analog instrument to JB JB-RICE 6 radiators (-AI01: 5 x 1 pr (field cables) |  | RICE 6 radiators (5) | JB-RICE 6 radiators (-AI01 | RICE 6 radiators (5) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 5 | 1 |  |  |  | Tray / conduit | 80 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0203 | I | Modular / portable power | Home run JB-RICE 6 radiators (-AI01 to the control / marshalling room |  | PCM: power control module | JB-RICE 6 radiators (-AI01 | RICE 6 radiators (5) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 150
I-I-0204 | I | Modular / portable power | Discrete device to JB JB-RICE 6 radiators (-DI01: 10 x 1 pr (field cables) |  | RICE 6 radiators (5) | JB-RICE 6 radiators (-DI01 | RICE 6 radiators (5) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 80 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0205 | I | Modular / portable power | Home run JB-RICE 6 radiators (-DI01 to the control / marshalling room |  | PCM: power control module | JB-RICE 6 radiators (-DI01 | RICE 6 radiators (5) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 150
I-I-0206 | I | Modular / portable power | Analog instrument to JB JB-RICE 7 SCR + oxida-AI01: 10 x 1 pr (field cables) |  | RICE 7 SCR + oxidation catalyst and stack | JB-RICE 7 SCR + oxida-AI01 | RICE 7 SCR + oxidation catalyst and stack | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 92 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0207 | I | Modular / portable power | Home run JB-RICE 7 SCR + oxida-AI01 to the control / marshalling room |  | PCM: power control module | JB-RICE 7 SCR + oxida-AI01 | RICE 7 SCR + oxidation catalyst and stack | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 322 | 140
I-I-0208 | I | Modular / portable power | Discrete device to JB JB-RICE 7 SCR + oxida-DI01: 6 x 1 pr (field cables) |  | RICE 7 SCR + oxidation catalyst and stack | JB-RICE 7 SCR + oxida-DI01 | RICE 7 SCR + oxidation catalyst and stack | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 92 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0209 | I | Modular / portable power | Home run JB-RICE 7 SCR + oxida-DI01 to the control / marshalling room |  | PCM: power control module | JB-RICE 7 SCR + oxida-DI01 | RICE 7 SCR + oxidation catalyst and stack | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 322 | 140
I-I-0210 | I | Modular / portable power | Analog instrument to JB JB-RICE 7 radiators (-AI01: 5 x 1 pr (field cables) |  | RICE 7 radiators (5) | JB-RICE 7 radiators (-AI01 | RICE 7 radiators (5) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 5 | 1 |  |  |  | Tray / conduit | 80 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0211 | I | Modular / portable power | Home run JB-RICE 7 radiators (-AI01 to the control / marshalling room |  | PCM: power control module | JB-RICE 7 radiators (-AI01 | RICE 7 radiators (5) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 122
I-I-0212 | I | Modular / portable power | Discrete device to JB JB-RICE 7 radiators (-DI01: 10 x 1 pr (field cables) |  | RICE 7 radiators (5) | JB-RICE 7 radiators (-DI01 | RICE 7 radiators (5) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 80 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0213 | I | Modular / portable power | Home run JB-RICE 7 radiators (-DI01 to the control / marshalling room |  | PCM: power control module | JB-RICE 7 radiators (-DI01 | RICE 7 radiators (5) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 122
I-I-0214 | I | Modular / portable power | Analog instrument to JB JB-RICE 8 SCR + oxida-AI01: 10 x 1 pr (field cables) |  | RICE 8 SCR + oxidation catalyst and stack | JB-RICE 8 SCR + oxida-AI01 | RICE 8 SCR + oxidation catalyst and stack | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 92 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0215 | I | Modular / portable power | Home run JB-RICE 8 SCR + oxida-AI01 to the control / marshalling room |  | PCM: power control module | JB-RICE 8 SCR + oxida-AI01 | RICE 8 SCR + oxidation catalyst and stack | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 322 | 112
I-I-0216 | I | Modular / portable power | Discrete device to JB JB-RICE 8 SCR + oxida-DI01: 6 x 1 pr (field cables) |  | RICE 8 SCR + oxidation catalyst and stack | JB-RICE 8 SCR + oxida-DI01 | RICE 8 SCR + oxidation catalyst and stack | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 6 | 1 |  |  |  | Tray / conduit | 92 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0217 | I | Modular / portable power | Home run JB-RICE 8 SCR + oxida-DI01 to the control / marshalling room |  | PCM: power control module | JB-RICE 8 SCR + oxida-DI01 | RICE 8 SCR + oxidation catalyst and stack | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 322 | 112
I-I-0218 | I | Modular / portable power | Analog instrument to JB JB-RICE 8 radiators (-AI01: 5 x 1 pr (field cables) |  | RICE 8 radiators (5) | JB-RICE 8 radiators (-AI01 | RICE 8 radiators (5) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 5 | 1 |  |  |  | Tray / conduit | 80 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0219 | I | Modular / portable power | Home run JB-RICE 8 radiators (-AI01 to the control / marshalling room |  | PCM: power control module | JB-RICE 8 radiators (-AI01 | RICE 8 radiators (5) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 94
I-I-0220 | I | Modular / portable power | Discrete device to JB JB-RICE 8 radiators (-DI01: 10 x 1 pr (field cables) |  | RICE 8 radiators (5) | JB-RICE 8 radiators (-DI01 | RICE 8 radiators (5) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 80 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0221 | I | Modular / portable power | Home run JB-RICE 8 radiators (-DI01 to the control / marshalling room |  | PCM: power control module | JB-RICE 8 radiators (-DI01 | RICE 8 radiators (5) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 94
I-I-0222 | I | Modular / portable power | Instrumentation |  | PCM: power control module | RICE | RICE engine hall (8 engines) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Duct bank | 367 | 95
I-I-0223 | I | Modular / portable power | Instrumentation |  | PCM: power control module | RICE | RICE engine hall (8 engines) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Duct bank | 367 | 95
I-I-0224 | I | Modular / portable power | Instrumentation |  | PCM: power control module | RICE | RICE engine hall (8 engines) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Duct bank | 367 | 95
I-I-0225 | I | Modular / portable power | Instrumentation |  | PCM: power control module | RICE | RICE engine hall (8 engines) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Duct bank | 367 | 95
I-I-0226 | I | Modular / portable power | Instrumentation |  | PCM: power control module | RICE | RICE engine hall (8 engines) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Duct bank | 367 | 95
I-I-0227 | I | Modular / portable power | Instrumentation |  | PCM: power control module | RICE | RICE engine hall (8 engines) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Duct bank | 367 | 95
I-I-0228 | I | Modular / portable power | Instrumentation |  | PCM: power control module | RICE | RICE engine hall (8 engines) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Duct bank | 367 | 95
I-I-0229 | I | Modular / portable power | Instrumentation |  | PCM: power control module | RICE | RICE engine hall (8 engines) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Duct bank | 367 | 95
I-I-0230 | I | Modular / portable power | Instrumentation |  | PCM: power control module | RICE | RICE engine hall (8 engines) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Duct bank | 367 | 95
I-I-0231 | I | Modular / portable power | Instrumentation |  | PCM: power control module | RICE | RICE engine hall (8 engines) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Duct bank | 367 | 95
I-I-0232 | I | Modular / portable power | Thermocouples |  | PCM: power control module | RICE | RICE engine hall (8 engines) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦12 pr¦16 | 12 pr | 16 | 1 | 1 |  |  |  | Duct bank | 367 | 95
I-I-0233 | I | Modular / portable power | Thermocouples |  | PCM: power control module | RICE | RICE engine hall (8 engines) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦12 pr¦16 | 12 pr | 16 | 1 | 1 |  |  |  | Duct bank | 367 | 95
I-I-0234 | I | Modular / portable power | Thermocouples |  | PCM: power control module | RICE | RICE engine hall (8 engines) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦12 pr¦16 | 12 pr | 16 | 1 | 1 |  |  |  | Duct bank | 367 | 95
I-I-0235 | I | Modular / portable power | Thermocouples |  | PCM: power control module | RICE | RICE engine hall (8 engines) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦12 pr¦16 | 12 pr | 16 | 1 | 1 |  |  |  | Duct bank | 367 | 95
I-I-0236 | I | Modular / portable power | Thermocouples |  | PCM: power control module | RICE | RICE engine hall (8 engines) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦12 pr¦16 | 12 pr | 16 | 1 | 1 |  |  |  | Duct bank | 367 | 95
I-I-0237 | I | Modular / portable power | Thermocouples |  | PCM: power control module | RICE | RICE engine hall (8 engines) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦12 pr¦16 | 12 pr | 16 | 1 | 1 |  |  |  | Duct bank | 367 | 95
I-I-0238 | I | Modular / portable power | Analog instrument to JB JB-RICE-1-AI01: 20 x 1 pr (field cables) | RICE-1 | RICE engine-generator 1 | JB-RICE-1-AI01 | RICE engine-generator 1 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0239 | I | Modular / portable power | Home run JB-RICE-1-AI01 to the control / marshalling room |  | PCM: power control module | JB-RICE-1-AI01 | RICE engine-generator 1 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 137
I-I-0240 | I | Modular / portable power | Analog instrument to JB JB-RICE-1-AI02: 20 x 1 pr (field cables) | RICE-1 | RICE engine-generator 1 | JB-RICE-1-AI02 | RICE engine-generator 1 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0241 | I | Modular / portable power | Home run JB-RICE-1-AI02 to the control / marshalling room |  | PCM: power control module | JB-RICE-1-AI02 | RICE engine-generator 1 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 137
I-I-0242 | I | Modular / portable power | Analog instrument to JB JB-RICE-1-AI03: 20 x 1 pr (field cables) | RICE-1 | RICE engine-generator 1 | JB-RICE-1-AI03 | RICE engine-generator 1 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0243 | I | Modular / portable power | Home run JB-RICE-1-AI03 to the control / marshalling room |  | PCM: power control module | JB-RICE-1-AI03 | RICE engine-generator 1 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 137
I-I-0244 | I | Modular / portable power | Analog instrument to JB JB-RICE-1-AI04: 20 x 1 pr (field cables) | RICE-1 | RICE engine-generator 1 | JB-RICE-1-AI04 | RICE engine-generator 1 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0245 | I | Modular / portable power | Home run JB-RICE-1-AI04 to the control / marshalling room |  | PCM: power control module | JB-RICE-1-AI04 | RICE engine-generator 1 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 137
I-I-0246 | I | Modular / portable power | Discrete device to JB JB-RICE-1-DI01: 20 x 1 pr (field cables) | RICE-1 | RICE engine-generator 1 | JB-RICE-1-DI01 | RICE engine-generator 1 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0247 | I | Modular / portable power | Home run JB-RICE-1-DI01 to the control / marshalling room |  | PCM: power control module | JB-RICE-1-DI01 | RICE engine-generator 1 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 137
I-I-0248 | I | Modular / portable power | Discrete device to JB JB-RICE-1-DI02: 20 x 1 pr (field cables) | RICE-1 | RICE engine-generator 1 | JB-RICE-1-DI02 | RICE engine-generator 1 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0249 | I | Modular / portable power | Home run JB-RICE-1-DI02 to the control / marshalling room |  | PCM: power control module | JB-RICE-1-DI02 | RICE engine-generator 1 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 137
I-I-0250 | I | Modular / portable power | Discrete device to JB JB-RICE-1-DI03: 20 x 1 pr (field cables) | RICE-1 | RICE engine-generator 1 | JB-RICE-1-DI03 | RICE engine-generator 1 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0251 | I | Modular / portable power | Home run JB-RICE-1-DI03 to the control / marshalling room |  | PCM: power control module | JB-RICE-1-DI03 | RICE engine-generator 1 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 137
I-I-0252 | I | Modular / portable power | Thermocouple to TC JB JB-RICE-1-TC01: 20 x 1 pr (field cables) | RICE-1 | RICE engine-generator 1 | JB-RICE-1-TC01 | RICE engine-generator 1 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0253 | I | Modular / portable power | Home run JB-RICE-1-TC01 to the control / marshalling room |  | PCM: power control module | JB-RICE-1-TC01 | RICE engine-generator 1 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Duct bank | 550 | 137
I-I-0254 | I | Modular / portable power | Thermocouple to TC JB JB-RICE-1-TC02: 10 x 1 pr (field cables) | RICE-1 | RICE engine-generator 1 | JB-RICE-1-TC02 | RICE engine-generator 1 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0255 | I | Modular / portable power | Home run JB-RICE-1-TC02 to the control / marshalling room |  | PCM: power control module | JB-RICE-1-TC02 | RICE engine-generator 1 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Duct bank | 550 | 137
I-I-0256 | I | Modular / portable power | RTD to JB JB-RICE-1-RTD01: 10 x 1 tri (field cables) | RICE-1 | RICE engine-generator 1 | JB-RICE-1-RTD01 | RICE engine-generator 1 | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0257 | I | Modular / portable power | Home run JB-RICE-1-RTD01 to the control / marshalling room |  | PCM: power control module | JB-RICE-1-RTD01 | RICE engine-generator 1 | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 137
I-I-0258 | I | Modular / portable power | RTD to JB JB-RICE-1-RTD02: 2 x 1 tri (field cables) | RICE-1 | RICE engine-generator 1 | JB-RICE-1-RTD02 | RICE engine-generator 1 | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 2 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0259 | I | Modular / portable power | Home run JB-RICE-1-RTD02 to the control / marshalling room |  | PCM: power control module | JB-RICE-1-RTD02 | RICE engine-generator 1 | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 137
I-I-0260 | I | Modular / portable power | Analog instrument to JB JB-RICE-2-AI01: 20 x 1 pr (field cables) | RICE-2 | RICE engine-generator 2 | JB-RICE-2-AI01 | RICE engine-generator 2 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0261 | I | Modular / portable power | Home run JB-RICE-2-AI01 to the control / marshalling room |  | PCM: power control module | JB-RICE-2-AI01 | RICE engine-generator 2 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 109
I-I-0262 | I | Modular / portable power | Analog instrument to JB JB-RICE-2-AI02: 20 x 1 pr (field cables) | RICE-2 | RICE engine-generator 2 | JB-RICE-2-AI02 | RICE engine-generator 2 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0263 | I | Modular / portable power | Home run JB-RICE-2-AI02 to the control / marshalling room |  | PCM: power control module | JB-RICE-2-AI02 | RICE engine-generator 2 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 109
I-I-0264 | I | Modular / portable power | Analog instrument to JB JB-RICE-2-AI03: 20 x 1 pr (field cables) | RICE-2 | RICE engine-generator 2 | JB-RICE-2-AI03 | RICE engine-generator 2 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0265 | I | Modular / portable power | Home run JB-RICE-2-AI03 to the control / marshalling room |  | PCM: power control module | JB-RICE-2-AI03 | RICE engine-generator 2 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 109
I-I-0266 | I | Modular / portable power | Analog instrument to JB JB-RICE-2-AI04: 20 x 1 pr (field cables) | RICE-2 | RICE engine-generator 2 | JB-RICE-2-AI04 | RICE engine-generator 2 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0267 | I | Modular / portable power | Home run JB-RICE-2-AI04 to the control / marshalling room |  | PCM: power control module | JB-RICE-2-AI04 | RICE engine-generator 2 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 109
I-I-0268 | I | Modular / portable power | Discrete device to JB JB-RICE-2-DI01: 20 x 1 pr (field cables) | RICE-2 | RICE engine-generator 2 | JB-RICE-2-DI01 | RICE engine-generator 2 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0269 | I | Modular / portable power | Home run JB-RICE-2-DI01 to the control / marshalling room |  | PCM: power control module | JB-RICE-2-DI01 | RICE engine-generator 2 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 109
I-I-0270 | I | Modular / portable power | Discrete device to JB JB-RICE-2-DI02: 20 x 1 pr (field cables) | RICE-2 | RICE engine-generator 2 | JB-RICE-2-DI02 | RICE engine-generator 2 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0271 | I | Modular / portable power | Home run JB-RICE-2-DI02 to the control / marshalling room |  | PCM: power control module | JB-RICE-2-DI02 | RICE engine-generator 2 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 109
I-I-0272 | I | Modular / portable power | Discrete device to JB JB-RICE-2-DI03: 20 x 1 pr (field cables) | RICE-2 | RICE engine-generator 2 | JB-RICE-2-DI03 | RICE engine-generator 2 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0273 | I | Modular / portable power | Home run JB-RICE-2-DI03 to the control / marshalling room |  | PCM: power control module | JB-RICE-2-DI03 | RICE engine-generator 2 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 109
I-I-0274 | I | Modular / portable power | Thermocouple to TC JB JB-RICE-2-TC01: 20 x 1 pr (field cables) | RICE-2 | RICE engine-generator 2 | JB-RICE-2-TC01 | RICE engine-generator 2 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0275 | I | Modular / portable power | Home run JB-RICE-2-TC01 to the control / marshalling room |  | PCM: power control module | JB-RICE-2-TC01 | RICE engine-generator 2 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Duct bank | 550 | 109
I-I-0276 | I | Modular / portable power | Thermocouple to TC JB JB-RICE-2-TC02: 10 x 1 pr (field cables) | RICE-2 | RICE engine-generator 2 | JB-RICE-2-TC02 | RICE engine-generator 2 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0277 | I | Modular / portable power | Home run JB-RICE-2-TC02 to the control / marshalling room |  | PCM: power control module | JB-RICE-2-TC02 | RICE engine-generator 2 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Duct bank | 550 | 109
I-I-0278 | I | Modular / portable power | RTD to JB JB-RICE-2-RTD01: 10 x 1 tri (field cables) | RICE-2 | RICE engine-generator 2 | JB-RICE-2-RTD01 | RICE engine-generator 2 | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0279 | I | Modular / portable power | Home run JB-RICE-2-RTD01 to the control / marshalling room |  | PCM: power control module | JB-RICE-2-RTD01 | RICE engine-generator 2 | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 109
I-I-0280 | I | Modular / portable power | RTD to JB JB-RICE-2-RTD02: 2 x 1 tri (field cables) | RICE-2 | RICE engine-generator 2 | JB-RICE-2-RTD02 | RICE engine-generator 2 | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 2 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0281 | I | Modular / portable power | Home run JB-RICE-2-RTD02 to the control / marshalling room |  | PCM: power control module | JB-RICE-2-RTD02 | RICE engine-generator 2 | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 109
I-I-0282 | I | Modular / portable power | Analog instrument to JB JB-RICE-3-AI01: 20 x 1 pr (field cables) | RICE-3 | RICE engine-generator 3 | JB-RICE-3-AI01 | RICE engine-generator 3 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0283 | I | Modular / portable power | Home run JB-RICE-3-AI01 to the control / marshalling room |  | PCM: power control module | JB-RICE-3-AI01 | RICE engine-generator 3 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 81
I-I-0284 | I | Modular / portable power | Analog instrument to JB JB-RICE-3-AI02: 20 x 1 pr (field cables) | RICE-3 | RICE engine-generator 3 | JB-RICE-3-AI02 | RICE engine-generator 3 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0285 | I | Modular / portable power | Home run JB-RICE-3-AI02 to the control / marshalling room |  | PCM: power control module | JB-RICE-3-AI02 | RICE engine-generator 3 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 81
I-I-0286 | I | Modular / portable power | Analog instrument to JB JB-RICE-3-AI03: 20 x 1 pr (field cables) | RICE-3 | RICE engine-generator 3 | JB-RICE-3-AI03 | RICE engine-generator 3 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0287 | I | Modular / portable power | Home run JB-RICE-3-AI03 to the control / marshalling room |  | PCM: power control module | JB-RICE-3-AI03 | RICE engine-generator 3 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 81
I-I-0288 | I | Modular / portable power | Analog instrument to JB JB-RICE-3-AI04: 20 x 1 pr (field cables) | RICE-3 | RICE engine-generator 3 | JB-RICE-3-AI04 | RICE engine-generator 3 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0289 | I | Modular / portable power | Home run JB-RICE-3-AI04 to the control / marshalling room |  | PCM: power control module | JB-RICE-3-AI04 | RICE engine-generator 3 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 81
I-I-0290 | I | Modular / portable power | Discrete device to JB JB-RICE-3-DI01: 20 x 1 pr (field cables) | RICE-3 | RICE engine-generator 3 | JB-RICE-3-DI01 | RICE engine-generator 3 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0291 | I | Modular / portable power | Home run JB-RICE-3-DI01 to the control / marshalling room |  | PCM: power control module | JB-RICE-3-DI01 | RICE engine-generator 3 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 81
I-I-0292 | I | Modular / portable power | Discrete device to JB JB-RICE-3-DI02: 20 x 1 pr (field cables) | RICE-3 | RICE engine-generator 3 | JB-RICE-3-DI02 | RICE engine-generator 3 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0293 | I | Modular / portable power | Home run JB-RICE-3-DI02 to the control / marshalling room |  | PCM: power control module | JB-RICE-3-DI02 | RICE engine-generator 3 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 81
I-I-0294 | I | Modular / portable power | Discrete device to JB JB-RICE-3-DI03: 20 x 1 pr (field cables) | RICE-3 | RICE engine-generator 3 | JB-RICE-3-DI03 | RICE engine-generator 3 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0295 | I | Modular / portable power | Home run JB-RICE-3-DI03 to the control / marshalling room |  | PCM: power control module | JB-RICE-3-DI03 | RICE engine-generator 3 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 81
I-I-0296 | I | Modular / portable power | Thermocouple to TC JB JB-RICE-3-TC01: 20 x 1 pr (field cables) | RICE-3 | RICE engine-generator 3 | JB-RICE-3-TC01 | RICE engine-generator 3 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0297 | I | Modular / portable power | Home run JB-RICE-3-TC01 to the control / marshalling room |  | PCM: power control module | JB-RICE-3-TC01 | RICE engine-generator 3 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Duct bank | 550 | 81
I-I-0298 | I | Modular / portable power | Thermocouple to TC JB JB-RICE-3-TC02: 10 x 1 pr (field cables) | RICE-3 | RICE engine-generator 3 | JB-RICE-3-TC02 | RICE engine-generator 3 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0299 | I | Modular / portable power | Home run JB-RICE-3-TC02 to the control / marshalling room |  | PCM: power control module | JB-RICE-3-TC02 | RICE engine-generator 3 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Duct bank | 550 | 81
I-I-0300 | I | Modular / portable power | RTD to JB JB-RICE-3-RTD01: 10 x 1 tri (field cables) | RICE-3 | RICE engine-generator 3 | JB-RICE-3-RTD01 | RICE engine-generator 3 | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0301 | I | Modular / portable power | Home run JB-RICE-3-RTD01 to the control / marshalling room |  | PCM: power control module | JB-RICE-3-RTD01 | RICE engine-generator 3 | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 81
I-I-0302 | I | Modular / portable power | RTD to JB JB-RICE-3-RTD02: 2 x 1 tri (field cables) | RICE-3 | RICE engine-generator 3 | JB-RICE-3-RTD02 | RICE engine-generator 3 | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 2 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0303 | I | Modular / portable power | Home run JB-RICE-3-RTD02 to the control / marshalling room |  | PCM: power control module | JB-RICE-3-RTD02 | RICE engine-generator 3 | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 81
I-I-0304 | I | Modular / portable power | Analog instrument to JB JB-RICE-4-AI01: 20 x 1 pr (field cables) | RICE-4 | RICE engine-generator 4 | JB-RICE-4-AI01 | RICE engine-generator 4 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0305 | I | Modular / portable power | Home run JB-RICE-4-AI01 to the control / marshalling room |  | PCM: power control module | JB-RICE-4-AI01 | RICE engine-generator 4 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 53
I-I-0306 | I | Modular / portable power | Analog instrument to JB JB-RICE-4-AI02: 20 x 1 pr (field cables) | RICE-4 | RICE engine-generator 4 | JB-RICE-4-AI02 | RICE engine-generator 4 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0307 | I | Modular / portable power | Home run JB-RICE-4-AI02 to the control / marshalling room |  | PCM: power control module | JB-RICE-4-AI02 | RICE engine-generator 4 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 53
I-I-0308 | I | Modular / portable power | Analog instrument to JB JB-RICE-4-AI03: 20 x 1 pr (field cables) | RICE-4 | RICE engine-generator 4 | JB-RICE-4-AI03 | RICE engine-generator 4 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0309 | I | Modular / portable power | Home run JB-RICE-4-AI03 to the control / marshalling room |  | PCM: power control module | JB-RICE-4-AI03 | RICE engine-generator 4 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 53
I-I-0310 | I | Modular / portable power | Analog instrument to JB JB-RICE-4-AI04: 20 x 1 pr (field cables) | RICE-4 | RICE engine-generator 4 | JB-RICE-4-AI04 | RICE engine-generator 4 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0311 | I | Modular / portable power | Home run JB-RICE-4-AI04 to the control / marshalling room |  | PCM: power control module | JB-RICE-4-AI04 | RICE engine-generator 4 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 53
I-I-0312 | I | Modular / portable power | Discrete device to JB JB-RICE-4-DI01: 20 x 1 pr (field cables) | RICE-4 | RICE engine-generator 4 | JB-RICE-4-DI01 | RICE engine-generator 4 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0313 | I | Modular / portable power | Home run JB-RICE-4-DI01 to the control / marshalling room |  | PCM: power control module | JB-RICE-4-DI01 | RICE engine-generator 4 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 53
I-I-0314 | I | Modular / portable power | Discrete device to JB JB-RICE-4-DI02: 20 x 1 pr (field cables) | RICE-4 | RICE engine-generator 4 | JB-RICE-4-DI02 | RICE engine-generator 4 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0315 | I | Modular / portable power | Home run JB-RICE-4-DI02 to the control / marshalling room |  | PCM: power control module | JB-RICE-4-DI02 | RICE engine-generator 4 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 53
I-I-0316 | I | Modular / portable power | Discrete device to JB JB-RICE-4-DI03: 20 x 1 pr (field cables) | RICE-4 | RICE engine-generator 4 | JB-RICE-4-DI03 | RICE engine-generator 4 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0317 | I | Modular / portable power | Home run JB-RICE-4-DI03 to the control / marshalling room |  | PCM: power control module | JB-RICE-4-DI03 | RICE engine-generator 4 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 53
I-I-0318 | I | Modular / portable power | Thermocouple to TC JB JB-RICE-4-TC01: 20 x 1 pr (field cables) | RICE-4 | RICE engine-generator 4 | JB-RICE-4-TC01 | RICE engine-generator 4 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0319 | I | Modular / portable power | Home run JB-RICE-4-TC01 to the control / marshalling room |  | PCM: power control module | JB-RICE-4-TC01 | RICE engine-generator 4 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Duct bank | 550 | 53
I-I-0320 | I | Modular / portable power | Thermocouple to TC JB JB-RICE-4-TC02: 10 x 1 pr (field cables) | RICE-4 | RICE engine-generator 4 | JB-RICE-4-TC02 | RICE engine-generator 4 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0321 | I | Modular / portable power | Home run JB-RICE-4-TC02 to the control / marshalling room |  | PCM: power control module | JB-RICE-4-TC02 | RICE engine-generator 4 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Duct bank | 550 | 53
I-I-0322 | I | Modular / portable power | RTD to JB JB-RICE-4-RTD01: 10 x 1 tri (field cables) | RICE-4 | RICE engine-generator 4 | JB-RICE-4-RTD01 | RICE engine-generator 4 | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0323 | I | Modular / portable power | Home run JB-RICE-4-RTD01 to the control / marshalling room |  | PCM: power control module | JB-RICE-4-RTD01 | RICE engine-generator 4 | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 53
I-I-0324 | I | Modular / portable power | RTD to JB JB-RICE-4-RTD02: 2 x 1 tri (field cables) | RICE-4 | RICE engine-generator 4 | JB-RICE-4-RTD02 | RICE engine-generator 4 | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 2 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0325 | I | Modular / portable power | Home run JB-RICE-4-RTD02 to the control / marshalling room |  | PCM: power control module | JB-RICE-4-RTD02 | RICE engine-generator 4 | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 550 | 53
I-I-0326 | I | Modular / portable power | Analog instrument to JB JB-RICE-5-AI01: 20 x 1 pr (field cables) | RICE-5 | RICE engine-generator 5 | JB-RICE-5-AI01 | RICE engine-generator 5 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0327 | I | Modular / portable power | Home run JB-RICE-5-AI01 to the control / marshalling room |  | PCM: power control module | JB-RICE-5-AI01 | RICE engine-generator 5 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 367 | 208
I-I-0328 | I | Modular / portable power | Analog instrument to JB JB-RICE-5-AI02: 20 x 1 pr (field cables) | RICE-5 | RICE engine-generator 5 | JB-RICE-5-AI02 | RICE engine-generator 5 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0329 | I | Modular / portable power | Home run JB-RICE-5-AI02 to the control / marshalling room |  | PCM: power control module | JB-RICE-5-AI02 | RICE engine-generator 5 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 367 | 208
I-I-0330 | I | Modular / portable power | Analog instrument to JB JB-RICE-5-AI03: 20 x 1 pr (field cables) | RICE-5 | RICE engine-generator 5 | JB-RICE-5-AI03 | RICE engine-generator 5 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0331 | I | Modular / portable power | Home run JB-RICE-5-AI03 to the control / marshalling room |  | PCM: power control module | JB-RICE-5-AI03 | RICE engine-generator 5 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 367 | 208
I-I-0332 | I | Modular / portable power | Analog instrument to JB JB-RICE-5-AI04: 20 x 1 pr (field cables) | RICE-5 | RICE engine-generator 5 | JB-RICE-5-AI04 | RICE engine-generator 5 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0333 | I | Modular / portable power | Home run JB-RICE-5-AI04 to the control / marshalling room |  | PCM: power control module | JB-RICE-5-AI04 | RICE engine-generator 5 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 367 | 208
I-I-0334 | I | Modular / portable power | Discrete device to JB JB-RICE-5-DI01: 20 x 1 pr (field cables) | RICE-5 | RICE engine-generator 5 | JB-RICE-5-DI01 | RICE engine-generator 5 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0335 | I | Modular / portable power | Home run JB-RICE-5-DI01 to the control / marshalling room |  | PCM: power control module | JB-RICE-5-DI01 | RICE engine-generator 5 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 367 | 208
I-I-0336 | I | Modular / portable power | Discrete device to JB JB-RICE-5-DI02: 20 x 1 pr (field cables) | RICE-5 | RICE engine-generator 5 | JB-RICE-5-DI02 | RICE engine-generator 5 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0337 | I | Modular / portable power | Home run JB-RICE-5-DI02 to the control / marshalling room |  | PCM: power control module | JB-RICE-5-DI02 | RICE engine-generator 5 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 367 | 208
I-I-0338 | I | Modular / portable power | Discrete device to JB JB-RICE-5-DI03: 20 x 1 pr (field cables) | RICE-5 | RICE engine-generator 5 | JB-RICE-5-DI03 | RICE engine-generator 5 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0339 | I | Modular / portable power | Home run JB-RICE-5-DI03 to the control / marshalling room |  | PCM: power control module | JB-RICE-5-DI03 | RICE engine-generator 5 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 367 | 208
I-I-0340 | I | Modular / portable power | Thermocouple to TC JB JB-RICE-5-TC01: 20 x 1 pr (field cables) | RICE-5 | RICE engine-generator 5 | JB-RICE-5-TC01 | RICE engine-generator 5 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0341 | I | Modular / portable power | Home run JB-RICE-5-TC01 to the control / marshalling room |  | PCM: power control module | JB-RICE-5-TC01 | RICE engine-generator 5 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Duct bank | 367 | 208
I-I-0342 | I | Modular / portable power | Thermocouple to TC JB JB-RICE-5-TC02: 10 x 1 pr (field cables) | RICE-5 | RICE engine-generator 5 | JB-RICE-5-TC02 | RICE engine-generator 5 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0343 | I | Modular / portable power | Home run JB-RICE-5-TC02 to the control / marshalling room |  | PCM: power control module | JB-RICE-5-TC02 | RICE engine-generator 5 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Duct bank | 367 | 208
I-I-0344 | I | Modular / portable power | RTD to JB JB-RICE-5-RTD01: 10 x 1 tri (field cables) | RICE-5 | RICE engine-generator 5 | JB-RICE-5-RTD01 | RICE engine-generator 5 | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0345 | I | Modular / portable power | Home run JB-RICE-5-RTD01 to the control / marshalling room |  | PCM: power control module | JB-RICE-5-RTD01 | RICE engine-generator 5 | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 367 | 208
I-I-0346 | I | Modular / portable power | RTD to JB JB-RICE-5-RTD02: 2 x 1 tri (field cables) | RICE-5 | RICE engine-generator 5 | JB-RICE-5-RTD02 | RICE engine-generator 5 | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 2 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0347 | I | Modular / portable power | Home run JB-RICE-5-RTD02 to the control / marshalling room |  | PCM: power control module | JB-RICE-5-RTD02 | RICE engine-generator 5 | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 367 | 208
I-I-0348 | I | Modular / portable power | Analog instrument to JB JB-RICE-6-AI01: 20 x 1 pr (field cables) | RICE-6 | RICE engine-generator 6 | JB-RICE-6-AI01 | RICE engine-generator 6 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0349 | I | Modular / portable power | Home run JB-RICE-6-AI01 to the control / marshalling room |  | PCM: power control module | JB-RICE-6-AI01 | RICE engine-generator 6 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 367 | 180
I-I-0350 | I | Modular / portable power | Analog instrument to JB JB-RICE-6-AI02: 20 x 1 pr (field cables) | RICE-6 | RICE engine-generator 6 | JB-RICE-6-AI02 | RICE engine-generator 6 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0351 | I | Modular / portable power | Home run JB-RICE-6-AI02 to the control / marshalling room |  | PCM: power control module | JB-RICE-6-AI02 | RICE engine-generator 6 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 367 | 180
I-I-0352 | I | Modular / portable power | Analog instrument to JB JB-RICE-6-AI03: 20 x 1 pr (field cables) | RICE-6 | RICE engine-generator 6 | JB-RICE-6-AI03 | RICE engine-generator 6 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0353 | I | Modular / portable power | Home run JB-RICE-6-AI03 to the control / marshalling room |  | PCM: power control module | JB-RICE-6-AI03 | RICE engine-generator 6 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 367 | 180
I-I-0354 | I | Modular / portable power | Analog instrument to JB JB-RICE-6-AI04: 20 x 1 pr (field cables) | RICE-6 | RICE engine-generator 6 | JB-RICE-6-AI04 | RICE engine-generator 6 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0355 | I | Modular / portable power | Home run JB-RICE-6-AI04 to the control / marshalling room |  | PCM: power control module | JB-RICE-6-AI04 | RICE engine-generator 6 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 367 | 180
I-I-0356 | I | Modular / portable power | Discrete device to JB JB-RICE-6-DI01: 20 x 1 pr (field cables) | RICE-6 | RICE engine-generator 6 | JB-RICE-6-DI01 | RICE engine-generator 6 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0357 | I | Modular / portable power | Home run JB-RICE-6-DI01 to the control / marshalling room |  | PCM: power control module | JB-RICE-6-DI01 | RICE engine-generator 6 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 367 | 180
I-I-0358 | I | Modular / portable power | Discrete device to JB JB-RICE-6-DI02: 20 x 1 pr (field cables) | RICE-6 | RICE engine-generator 6 | JB-RICE-6-DI02 | RICE engine-generator 6 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0359 | I | Modular / portable power | Home run JB-RICE-6-DI02 to the control / marshalling room |  | PCM: power control module | JB-RICE-6-DI02 | RICE engine-generator 6 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 367 | 180
I-I-0360 | I | Modular / portable power | Discrete device to JB JB-RICE-6-DI03: 20 x 1 pr (field cables) | RICE-6 | RICE engine-generator 6 | JB-RICE-6-DI03 | RICE engine-generator 6 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0361 | I | Modular / portable power | Home run JB-RICE-6-DI03 to the control / marshalling room |  | PCM: power control module | JB-RICE-6-DI03 | RICE engine-generator 6 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 367 | 180
I-I-0362 | I | Modular / portable power | Thermocouple to TC JB JB-RICE-6-TC01: 20 x 1 pr (field cables) | RICE-6 | RICE engine-generator 6 | JB-RICE-6-TC01 | RICE engine-generator 6 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0363 | I | Modular / portable power | Home run JB-RICE-6-TC01 to the control / marshalling room |  | PCM: power control module | JB-RICE-6-TC01 | RICE engine-generator 6 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Duct bank | 367 | 180
I-I-0364 | I | Modular / portable power | Thermocouple to TC JB JB-RICE-6-TC02: 10 x 1 pr (field cables) | RICE-6 | RICE engine-generator 6 | JB-RICE-6-TC02 | RICE engine-generator 6 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0365 | I | Modular / portable power | Home run JB-RICE-6-TC02 to the control / marshalling room |  | PCM: power control module | JB-RICE-6-TC02 | RICE engine-generator 6 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Duct bank | 367 | 180
I-I-0366 | I | Modular / portable power | RTD to JB JB-RICE-6-RTD01: 10 x 1 tri (field cables) | RICE-6 | RICE engine-generator 6 | JB-RICE-6-RTD01 | RICE engine-generator 6 | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0367 | I | Modular / portable power | Home run JB-RICE-6-RTD01 to the control / marshalling room |  | PCM: power control module | JB-RICE-6-RTD01 | RICE engine-generator 6 | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 367 | 180
I-I-0368 | I | Modular / portable power | RTD to JB JB-RICE-6-RTD02: 2 x 1 tri (field cables) | RICE-6 | RICE engine-generator 6 | JB-RICE-6-RTD02 | RICE engine-generator 6 | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 2 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0369 | I | Modular / portable power | Home run JB-RICE-6-RTD02 to the control / marshalling room |  | PCM: power control module | JB-RICE-6-RTD02 | RICE engine-generator 6 | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Duct bank | 367 | 180
I-I-0370 | I | Modular / portable power | Analog instrument to JB JB-RICE-7-AI01: 20 x 1 pr (field cables) | RICE-7 | RICE engine-generator 7 | JB-RICE-7-AI01 | RICE engine-generator 7 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0371 | I | Modular / portable power | Home run JB-RICE-7-AI01 to the control / marshalling room |  | PCM: power control module | JB-RICE-7-AI01 | RICE engine-generator 7 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 189
I-I-0372 | I | Modular / portable power | Analog instrument to JB JB-RICE-7-AI02: 20 x 1 pr (field cables) | RICE-7 | RICE engine-generator 7 | JB-RICE-7-AI02 | RICE engine-generator 7 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0373 | I | Modular / portable power | Home run JB-RICE-7-AI02 to the control / marshalling room |  | PCM: power control module | JB-RICE-7-AI02 | RICE engine-generator 7 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 189
I-I-0374 | I | Modular / portable power | Analog instrument to JB JB-RICE-7-AI03: 20 x 1 pr (field cables) | RICE-7 | RICE engine-generator 7 | JB-RICE-7-AI03 | RICE engine-generator 7 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0375 | I | Modular / portable power | Home run JB-RICE-7-AI03 to the control / marshalling room |  | PCM: power control module | JB-RICE-7-AI03 | RICE engine-generator 7 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 189
I-I-0376 | I | Modular / portable power | Analog instrument to JB JB-RICE-7-AI04: 20 x 1 pr (field cables) | RICE-7 | RICE engine-generator 7 | JB-RICE-7-AI04 | RICE engine-generator 7 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0377 | I | Modular / portable power | Home run JB-RICE-7-AI04 to the control / marshalling room |  | PCM: power control module | JB-RICE-7-AI04 | RICE engine-generator 7 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 189
I-I-0378 | I | Modular / portable power | Discrete device to JB JB-RICE-7-DI01: 20 x 1 pr (field cables) | RICE-7 | RICE engine-generator 7 | JB-RICE-7-DI01 | RICE engine-generator 7 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0379 | I | Modular / portable power | Home run JB-RICE-7-DI01 to the control / marshalling room |  | PCM: power control module | JB-RICE-7-DI01 | RICE engine-generator 7 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 189
I-I-0380 | I | Modular / portable power | Discrete device to JB JB-RICE-7-DI02: 20 x 1 pr (field cables) | RICE-7 | RICE engine-generator 7 | JB-RICE-7-DI02 | RICE engine-generator 7 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0381 | I | Modular / portable power | Home run JB-RICE-7-DI02 to the control / marshalling room |  | PCM: power control module | JB-RICE-7-DI02 | RICE engine-generator 7 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 189
I-I-0382 | I | Modular / portable power | Discrete device to JB JB-RICE-7-DI03: 20 x 1 pr (field cables) | RICE-7 | RICE engine-generator 7 | JB-RICE-7-DI03 | RICE engine-generator 7 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0383 | I | Modular / portable power | Home run JB-RICE-7-DI03 to the control / marshalling room |  | PCM: power control module | JB-RICE-7-DI03 | RICE engine-generator 7 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 189
I-I-0384 | I | Modular / portable power | Thermocouple to TC JB JB-RICE-7-TC01: 20 x 1 pr (field cables) | RICE-7 | RICE engine-generator 7 | JB-RICE-7-TC01 | RICE engine-generator 7 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0385 | I | Modular / portable power | Home run JB-RICE-7-TC01 to the control / marshalling room |  | PCM: power control module | JB-RICE-7-TC01 | RICE engine-generator 7 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Tray | 0 | 189
I-I-0386 | I | Modular / portable power | Thermocouple to TC JB JB-RICE-7-TC02: 10 x 1 pr (field cables) | RICE-7 | RICE engine-generator 7 | JB-RICE-7-TC02 | RICE engine-generator 7 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0387 | I | Modular / portable power | Home run JB-RICE-7-TC02 to the control / marshalling room |  | PCM: power control module | JB-RICE-7-TC02 | RICE engine-generator 7 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Tray | 0 | 189
I-I-0388 | I | Modular / portable power | RTD to JB JB-RICE-7-RTD01: 10 x 1 tri (field cables) | RICE-7 | RICE engine-generator 7 | JB-RICE-7-RTD01 | RICE engine-generator 7 | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0389 | I | Modular / portable power | Home run JB-RICE-7-RTD01 to the control / marshalling room |  | PCM: power control module | JB-RICE-7-RTD01 | RICE engine-generator 7 | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Tray | 0 | 189
I-I-0390 | I | Modular / portable power | RTD to JB JB-RICE-7-RTD02: 2 x 1 tri (field cables) | RICE-7 | RICE engine-generator 7 | JB-RICE-7-RTD02 | RICE engine-generator 7 | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 2 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0391 | I | Modular / portable power | Home run JB-RICE-7-RTD02 to the control / marshalling room |  | PCM: power control module | JB-RICE-7-RTD02 | RICE engine-generator 7 | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Tray | 0 | 189
I-I-0392 | I | Modular / portable power | Analog instrument to JB JB-RICE-8-AI01: 20 x 1 pr (field cables) | RICE-8 | RICE engine-generator 8 | JB-RICE-8-AI01 | RICE engine-generator 8 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0393 | I | Modular / portable power | Home run JB-RICE-8-AI01 to the control / marshalling room |  | PCM: power control module | JB-RICE-8-AI01 | RICE engine-generator 8 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 161
I-I-0394 | I | Modular / portable power | Analog instrument to JB JB-RICE-8-AI02: 20 x 1 pr (field cables) | RICE-8 | RICE engine-generator 8 | JB-RICE-8-AI02 | RICE engine-generator 8 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0395 | I | Modular / portable power | Home run JB-RICE-8-AI02 to the control / marshalling room |  | PCM: power control module | JB-RICE-8-AI02 | RICE engine-generator 8 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 161
I-I-0396 | I | Modular / portable power | Analog instrument to JB JB-RICE-8-AI03: 20 x 1 pr (field cables) | RICE-8 | RICE engine-generator 8 | JB-RICE-8-AI03 | RICE engine-generator 8 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0397 | I | Modular / portable power | Home run JB-RICE-8-AI03 to the control / marshalling room |  | PCM: power control module | JB-RICE-8-AI03 | RICE engine-generator 8 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 161
I-I-0398 | I | Modular / portable power | Analog instrument to JB JB-RICE-8-AI04: 20 x 1 pr (field cables) | RICE-8 | RICE engine-generator 8 | JB-RICE-8-AI04 | RICE engine-generator 8 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0399 | I | Modular / portable power | Home run JB-RICE-8-AI04 to the control / marshalling room |  | PCM: power control module | JB-RICE-8-AI04 | RICE engine-generator 8 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 161
I-I-0400 | I | Modular / portable power | Discrete device to JB JB-RICE-8-DI01: 20 x 1 pr (field cables) | RICE-8 | RICE engine-generator 8 | JB-RICE-8-DI01 | RICE engine-generator 8 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0401 | I | Modular / portable power | Home run JB-RICE-8-DI01 to the control / marshalling room |  | PCM: power control module | JB-RICE-8-DI01 | RICE engine-generator 8 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 161
I-I-0402 | I | Modular / portable power | Discrete device to JB JB-RICE-8-DI02: 20 x 1 pr (field cables) | RICE-8 | RICE engine-generator 8 | JB-RICE-8-DI02 | RICE engine-generator 8 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0403 | I | Modular / portable power | Home run JB-RICE-8-DI02 to the control / marshalling room |  | PCM: power control module | JB-RICE-8-DI02 | RICE engine-generator 8 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 161
I-I-0404 | I | Modular / portable power | Discrete device to JB JB-RICE-8-DI03: 20 x 1 pr (field cables) | RICE-8 | RICE engine-generator 8 | JB-RICE-8-DI03 | RICE engine-generator 8 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0405 | I | Modular / portable power | Home run JB-RICE-8-DI03 to the control / marshalling room |  | PCM: power control module | JB-RICE-8-DI03 | RICE engine-generator 8 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 161
I-I-0406 | I | Modular / portable power | Thermocouple to TC JB JB-RICE-8-TC01: 20 x 1 pr (field cables) | RICE-8 | RICE engine-generator 8 | JB-RICE-8-TC01 | RICE engine-generator 8 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0407 | I | Modular / portable power | Home run JB-RICE-8-TC01 to the control / marshalling room |  | PCM: power control module | JB-RICE-8-TC01 | RICE engine-generator 8 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Tray | 0 | 161
I-I-0408 | I | Modular / portable power | Thermocouple to TC JB JB-RICE-8-TC02: 10 x 1 pr (field cables) | RICE-8 | RICE engine-generator 8 | JB-RICE-8-TC02 | RICE engine-generator 8 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0409 | I | Modular / portable power | Home run JB-RICE-8-TC02 to the control / marshalling room |  | PCM: power control module | JB-RICE-8-TC02 | RICE engine-generator 8 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Tray | 0 | 161
I-I-0410 | I | Modular / portable power | RTD to JB JB-RICE-8-RTD01: 10 x 1 tri (field cables) | RICE-8 | RICE engine-generator 8 | JB-RICE-8-RTD01 | RICE engine-generator 8 | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 10 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0411 | I | Modular / portable power | Home run JB-RICE-8-RTD01 to the control / marshalling room |  | PCM: power control module | JB-RICE-8-RTD01 | RICE engine-generator 8 | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Tray | 0 | 161
I-I-0412 | I | Modular / portable power | RTD to JB JB-RICE-8-RTD02: 2 x 1 tri (field cables) | RICE-8 | RICE engine-generator 8 | JB-RICE-8-RTD02 | RICE engine-generator 8 | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦1 tri¦18 | 1 tri | 18 | 2 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0413 | I | Modular / portable power | Home run JB-RICE-8-RTD02 to the control / marshalling room |  | PCM: power control module | JB-RICE-8-RTD02 | RICE engine-generator 8 | Instrumentation | RTD cable, #18 shielded triads, PLTC | RTD¦12 tri¦18 | 12 tri | 18 | 1 | 1 |  |  |  | Tray | 0 | 161
I-I-0414 | I | Modular / portable power | Instrumentation |  | PCM: power control module |  | Reagent storage | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 32 | 32
I-I-0415 | I | Modular / portable power | Analog instrument to JB JB-SC-1 SCR / CO cata-AI01: 12 x 1 pr (field cables) |  | SC-1 SCR / CO catalyst | JB-SC-1 SCR / CO cata-AI01 | SC-1 SCR / CO catalyst | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 74 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0416 | I | Modular / portable power | Home run JB-SC-1 SCR / CO cata-AI01 to the control / marshalling room |  | PCM: power control module | JB-SC-1 SCR / CO cata-AI01 | SC-1 SCR / CO catalyst | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 40 | 142
I-I-0417 | I | Modular / portable power | Discrete device to JB JB-SC-1 SCR / CO cata-DI01: 8 x 1 pr (field cables) |  | SC-1 SCR / CO catalyst | JB-SC-1 SCR / CO cata-DI01 | SC-1 SCR / CO catalyst | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 74 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0418 | I | Modular / portable power | Home run JB-SC-1 SCR / CO cata-DI01 to the control / marshalling room |  | PCM: power control module | JB-SC-1 SCR / CO cata-DI01 | SC-1 SCR / CO catalyst | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 40 | 142
I-I-0419 | I | Modular / portable power | Analog instrument to JB JB-SC-1 lube-oil fin--AI01: 4 x 1 pr (field cables) |  | SC-1 lube-oil fin-fan cooler | JB-SC-1 lube-oil fin--AI01 | SC-1 lube-oil fin-fan cooler | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 46 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0420 | I | Modular / portable power | Home run JB-SC-1 lube-oil fin--AI01 to the control / marshalling room |  | PCM: power control module | JB-SC-1 lube-oil fin--AI01 | SC-1 lube-oil fin-fan cooler | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 82 | 82
I-I-0421 | I | Modular / portable power | Discrete device to JB JB-SC-1 lube-oil fin--DI01: 8 x 1 pr (field cables) |  | SC-1 lube-oil fin-fan cooler | JB-SC-1 lube-oil fin--DI01 | SC-1 lube-oil fin-fan cooler | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 46 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0422 | I | Modular / portable power | Home run JB-SC-1 lube-oil fin--DI01 to the control / marshalling room |  | PCM: power control module | JB-SC-1 lube-oil fin--DI01 | SC-1 lube-oil fin-fan cooler | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 82 | 82
I-I-0423 | I | Modular / portable power | Analog instrument to JB JB-SC-1-AI01: 20 x 1 pr (field cables) | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | JB-SC-1-AI01 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 99 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0424 | I | Modular / portable power | Home run JB-SC-1-AI01 to the control / marshalling room |  | PCM: power control module | JB-SC-1-AI01 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 40 | 52
I-I-0425 | I | Modular / portable power | Analog instrument to JB JB-SC-1-AI02: 20 x 1 pr (field cables) | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | JB-SC-1-AI02 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 99 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0426 | I | Modular / portable power | Home run JB-SC-1-AI02 to the control / marshalling room |  | PCM: power control module | JB-SC-1-AI02 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 40 | 52
I-I-0427 | I | Modular / portable power | Analog instrument to JB JB-SC-1-AI03: 20 x 1 pr (field cables) | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | JB-SC-1-AI03 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 99 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0428 | I | Modular / portable power | Home run JB-SC-1-AI03 to the control / marshalling room |  | PCM: power control module | JB-SC-1-AI03 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 40 | 52
I-I-0429 | I | Modular / portable power | Analog instrument to JB JB-SC-1-AI04: 20 x 1 pr (field cables) | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | JB-SC-1-AI04 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 99 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0430 | I | Modular / portable power | Home run JB-SC-1-AI04 to the control / marshalling room |  | PCM: power control module | JB-SC-1-AI04 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 40 | 52
I-I-0431 | I | Modular / portable power | Analog instrument to JB JB-SC-1-AI05: 20 x 1 pr (field cables) | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | JB-SC-1-AI05 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 99 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0432 | I | Modular / portable power | Home run JB-SC-1-AI05 to the control / marshalling room |  | PCM: power control module | JB-SC-1-AI05 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 40 | 52
I-I-0433 | I | Modular / portable power | Analog instrument to JB JB-SC-1-AI06: 20 x 1 pr (field cables) | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | JB-SC-1-AI06 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 99 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0434 | I | Modular / portable power | Home run JB-SC-1-AI06 to the control / marshalling room |  | PCM: power control module | JB-SC-1-AI06 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 40 | 52
I-I-0435 | I | Modular / portable power | Analog instrument to JB JB-SC-1-AI07: 20 x 1 pr (field cables) | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | JB-SC-1-AI07 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 99 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0436 | I | Modular / portable power | Home run JB-SC-1-AI07 to the control / marshalling room |  | PCM: power control module | JB-SC-1-AI07 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 40 | 52
I-I-0437 | I | Modular / portable power | Analog instrument to JB JB-SC-1-AI08: 10 x 1 pr (field cables) | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | JB-SC-1-AI08 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 99 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0438 | I | Modular / portable power | Home run JB-SC-1-AI08 to the control / marshalling room |  | PCM: power control module | JB-SC-1-AI08 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 40 | 52
I-I-0439 | I | Modular / portable power | Discrete device to JB JB-SC-1-DI01: 20 x 1 pr (field cables) | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | JB-SC-1-DI01 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 99 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0440 | I | Modular / portable power | Home run JB-SC-1-DI01 to the control / marshalling room |  | PCM: power control module | JB-SC-1-DI01 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 40 | 52
I-I-0441 | I | Modular / portable power | Discrete device to JB JB-SC-1-DI02: 20 x 1 pr (field cables) | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | JB-SC-1-DI02 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 99 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0442 | I | Modular / portable power | Home run JB-SC-1-DI02 to the control / marshalling room |  | PCM: power control module | JB-SC-1-DI02 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 40 | 52
I-I-0443 | I | Modular / portable power | Discrete device to JB JB-SC-1-DI03: 20 x 1 pr (field cables) | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | JB-SC-1-DI03 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 99 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0444 | I | Modular / portable power | Home run JB-SC-1-DI03 to the control / marshalling room |  | PCM: power control module | JB-SC-1-DI03 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 40 | 52
I-I-0445 | I | Modular / portable power | Discrete device to JB JB-SC-1-DI04: 20 x 1 pr (field cables) | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | JB-SC-1-DI04 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 99 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0446 | I | Modular / portable power | Home run JB-SC-1-DI04 to the control / marshalling room |  | PCM: power control module | JB-SC-1-DI04 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 40 | 52
I-I-0447 | I | Modular / portable power | Discrete device to JB JB-SC-1-DI05: 20 x 1 pr (field cables) | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | JB-SC-1-DI05 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 99 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0448 | I | Modular / portable power | Home run JB-SC-1-DI05 to the control / marshalling room |  | PCM: power control module | JB-SC-1-DI05 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 40 | 52
I-I-0449 | I | Modular / portable power | Thermocouple to TC JB JB-SC-1-TC01: 20 x 1 pr (field cables) | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | JB-SC-1-TC01 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 99 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0450 | I | Modular / portable power | Home run JB-SC-1-TC01 to the control / marshalling room |  | PCM: power control module | JB-SC-1-TC01 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Duct bank | 40 | 52
I-I-0451 | I | Modular / portable power | Thermocouple to TC JB JB-SC-1-TC02: 20 x 1 pr (field cables) | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | JB-SC-1-TC02 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 99 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0452 | I | Modular / portable power | Home run JB-SC-1-TC02 to the control / marshalling room |  | PCM: power control module | JB-SC-1-TC02 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Duct bank | 40 | 52
I-I-0453 | I | Modular / portable power | Analog instrument to JB JB-SC-2 SCR / CO cata-AI01: 12 x 1 pr (field cables) |  | SC-2 SCR / CO catalyst | JB-SC-2 SCR / CO cata-AI01 | SC-2 SCR / CO catalyst | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 74 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0454 | I | Modular / portable power | Home run JB-SC-2 SCR / CO cata-AI01 to the control / marshalling room |  | PCM: power control module | JB-SC-2 SCR / CO cata-AI01 | SC-2 SCR / CO catalyst | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | HV duct bank | 4378 | 58
I-I-0455 | I | Modular / portable power | Discrete device to JB JB-SC-2 SCR / CO cata-DI01: 8 x 1 pr (field cables) |  | SC-2 SCR / CO catalyst | JB-SC-2 SCR / CO cata-DI01 | SC-2 SCR / CO catalyst | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 74 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0456 | I | Modular / portable power | Home run JB-SC-2 SCR / CO cata-DI01 to the control / marshalling room |  | PCM: power control module | JB-SC-2 SCR / CO cata-DI01 | SC-2 SCR / CO catalyst | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | HV duct bank | 4378 | 58
I-I-0457 | I | Modular / portable power | Analog instrument to JB JB-SC-2 lube-oil fin--AI01: 4 x 1 pr (field cables) |  | SC-2 lube-oil fin-fan cooler | JB-SC-2 lube-oil fin--AI01 | SC-2 lube-oil fin-fan cooler | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 46 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0458 | I | Modular / portable power | Home run JB-SC-2 lube-oil fin--AI01 to the control / marshalling room |  | PCM: power control module | JB-SC-2 lube-oil fin--AI01 | SC-2 lube-oil fin-fan cooler | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | HV duct bank | 4366 | 93
I-I-0459 | I | Modular / portable power | Discrete device to JB JB-SC-2 lube-oil fin--DI01: 8 x 1 pr (field cables) |  | SC-2 lube-oil fin-fan cooler | JB-SC-2 lube-oil fin--DI01 | SC-2 lube-oil fin-fan cooler | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 46 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0460 | I | Modular / portable power | Home run JB-SC-2 lube-oil fin--DI01 to the control / marshalling room |  | PCM: power control module | JB-SC-2 lube-oil fin--DI01 | SC-2 lube-oil fin-fan cooler | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | HV duct bank | 4366 | 93
I-I-0461 | I | Modular / portable power | Analog instrument to JB JB-SC-2-AI01: 20 x 1 pr (field cables) | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | JB-SC-2-AI01 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 99 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0462 | I | Modular / portable power | Home run JB-SC-2-AI01 to the control / marshalling room |  | PCM: power control module | JB-SC-2-AI01 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | HV duct bank | 4478 | 38
I-I-0463 | I | Modular / portable power | Analog instrument to JB JB-SC-2-AI02: 20 x 1 pr (field cables) | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | JB-SC-2-AI02 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 99 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0464 | I | Modular / portable power | Home run JB-SC-2-AI02 to the control / marshalling room |  | PCM: power control module | JB-SC-2-AI02 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | HV duct bank | 4478 | 38
I-I-0465 | I | Modular / portable power | Analog instrument to JB JB-SC-2-AI03: 20 x 1 pr (field cables) | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | JB-SC-2-AI03 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 99 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0466 | I | Modular / portable power | Home run JB-SC-2-AI03 to the control / marshalling room |  | PCM: power control module | JB-SC-2-AI03 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | HV duct bank | 4478 | 38
I-I-0467 | I | Modular / portable power | Analog instrument to JB JB-SC-2-AI04: 20 x 1 pr (field cables) | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | JB-SC-2-AI04 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 99 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0468 | I | Modular / portable power | Home run JB-SC-2-AI04 to the control / marshalling room |  | PCM: power control module | JB-SC-2-AI04 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | HV duct bank | 4478 | 38
I-I-0469 | I | Modular / portable power | Analog instrument to JB JB-SC-2-AI05: 20 x 1 pr (field cables) | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | JB-SC-2-AI05 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 99 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0470 | I | Modular / portable power | Home run JB-SC-2-AI05 to the control / marshalling room |  | PCM: power control module | JB-SC-2-AI05 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | HV duct bank | 4478 | 38
I-I-0471 | I | Modular / portable power | Analog instrument to JB JB-SC-2-AI06: 20 x 1 pr (field cables) | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | JB-SC-2-AI06 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 99 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0472 | I | Modular / portable power | Home run JB-SC-2-AI06 to the control / marshalling room |  | PCM: power control module | JB-SC-2-AI06 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | HV duct bank | 4478 | 38
I-I-0473 | I | Modular / portable power | Analog instrument to JB JB-SC-2-AI07: 20 x 1 pr (field cables) | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | JB-SC-2-AI07 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 99 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0474 | I | Modular / portable power | Home run JB-SC-2-AI07 to the control / marshalling room |  | PCM: power control module | JB-SC-2-AI07 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | HV duct bank | 4478 | 38
I-I-0475 | I | Modular / portable power | Analog instrument to JB JB-SC-2-AI08: 10 x 1 pr (field cables) | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | JB-SC-2-AI08 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 99 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0476 | I | Modular / portable power | Home run JB-SC-2-AI08 to the control / marshalling room |  | PCM: power control module | JB-SC-2-AI08 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | HV duct bank | 4478 | 38
I-I-0477 | I | Modular / portable power | Discrete device to JB JB-SC-2-DI01: 20 x 1 pr (field cables) | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | JB-SC-2-DI01 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 99 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0478 | I | Modular / portable power | Home run JB-SC-2-DI01 to the control / marshalling room |  | PCM: power control module | JB-SC-2-DI01 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | HV duct bank | 4478 | 38
I-I-0479 | I | Modular / portable power | Discrete device to JB JB-SC-2-DI02: 20 x 1 pr (field cables) | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | JB-SC-2-DI02 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 99 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0480 | I | Modular / portable power | Home run JB-SC-2-DI02 to the control / marshalling room |  | PCM: power control module | JB-SC-2-DI02 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | HV duct bank | 4478 | 38
I-I-0481 | I | Modular / portable power | Discrete device to JB JB-SC-2-DI03: 20 x 1 pr (field cables) | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | JB-SC-2-DI03 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 99 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0482 | I | Modular / portable power | Home run JB-SC-2-DI03 to the control / marshalling room |  | PCM: power control module | JB-SC-2-DI03 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | HV duct bank | 4478 | 38
I-I-0483 | I | Modular / portable power | Discrete device to JB JB-SC-2-DI04: 20 x 1 pr (field cables) | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | JB-SC-2-DI04 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 99 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0484 | I | Modular / portable power | Home run JB-SC-2-DI04 to the control / marshalling room |  | PCM: power control module | JB-SC-2-DI04 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | HV duct bank | 4478 | 38
I-I-0485 | I | Modular / portable power | Discrete device to JB JB-SC-2-DI05: 20 x 1 pr (field cables) | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | JB-SC-2-DI05 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 99 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0486 | I | Modular / portable power | Home run JB-SC-2-DI05 to the control / marshalling room |  | PCM: power control module | JB-SC-2-DI05 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | HV duct bank | 4478 | 38
I-I-0487 | I | Modular / portable power | Thermocouple to TC JB JB-SC-2-TC01: 20 x 1 pr (field cables) | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | JB-SC-2-TC01 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 99 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0488 | I | Modular / portable power | Home run JB-SC-2-TC01 to the control / marshalling room |  | PCM: power control module | JB-SC-2-TC01 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | HV duct bank | 4478 | 38
I-I-0489 | I | Modular / portable power | Thermocouple to TC JB JB-SC-2-TC02: 20 x 1 pr (field cables) | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | JB-SC-2-TC02 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 99 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0490 | I | Modular / portable power | Home run JB-SC-2-TC02 to the control / marshalling room |  | PCM: power control module | JB-SC-2-TC02 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | HV duct bank | 4478 | 38
I-I-0491 | I | Modular / portable power | Analog instrument to JB JB-T-MOD 230 kV take--AI01: 8 x 1 pr (field cables) |  | T-MOD 230 kV take-off gantry with arresters | JB-T-MOD 230 kV take--AI01 | T-MOD 230 kV take-off gantry with arresters | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 88 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0492 | I | Modular / portable power | Home run JB-T-MOD 230 kV take--AI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-T-MOD 230 kV take--AI01 | T-MOD 230 kV take-off gantry with arresters | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | HV duct bank | 2426 | 141
I-I-0493 | I | Modular / portable power | Discrete device to JB JB-T-MOD 230 kV take--DI01: 16 x 1 pr (field cables) |  | T-MOD 230 kV take-off gantry with arresters | JB-T-MOD 230 kV take--DI01 | T-MOD 230 kV take-off gantry with arresters | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 88 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0494 | I | Modular / portable power | Home run JB-T-MOD 230 kV take--DI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-T-MOD 230 kV take--DI01 | T-MOD 230 kV take-off gantry with arresters | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | HV duct bank | 2426 | 141
I-I-0495 | I | Modular / portable power | Analog instrument to JB JB-T-MOD-1 / T-MOD-2 -AI01: 8 x 1 pr (field cables) |  | T-MOD-1 / T-MOD-2 firewall | JB-T-MOD-1 / T-MOD-2 -AI01 | T-MOD-1 / T-MOD-2 firewall | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 64 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0496 | I | Modular / portable power | Home run JB-T-MOD-1 / T-MOD-2 -AI01 to the control / marshalling room |  | PCM: power control module | JB-T-MOD-1 / T-MOD-2 -AI01 | T-MOD-1 / T-MOD-2 firewall | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 415 | 130
I-I-0497 | I | Modular / portable power | Discrete device to JB JB-T-MOD-1 / T-MOD-2 -DI01: 16 x 1 pr (field cables) |  | T-MOD-1 / T-MOD-2 firewall | JB-T-MOD-1 / T-MOD-2 -DI01 | T-MOD-1 / T-MOD-2 firewall | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 64 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0498 | I | Modular / portable power | Home run JB-T-MOD-1 / T-MOD-2 -DI01 to the control / marshalling room |  | PCM: power control module | JB-T-MOD-1 / T-MOD-2 -DI01 | T-MOD-1 / T-MOD-2 firewall | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 415 | 130
I-I-0499 | I | Modular / portable power | Analog instrument to JB JB-T-MOD-1-AI01: 8 x 1 pr (field cables) | T-MOD-1 | T-MOD-1: 13.8/230 kV | JB-T-MOD-1-AI01 | T-MOD-1: 13.8/230 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 77 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0500 | I | Modular / portable power | Home run JB-T-MOD-1-AI01 to the control / marshalling room |  | PCM: power control module | JB-T-MOD-1-AI01 | T-MOD-1: 13.8/230 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 415 | 82
I-I-0501 | I | Modular / portable power | Discrete device to JB JB-T-MOD-1-DI01: 16 x 1 pr (field cables) | T-MOD-1 | T-MOD-1: 13.8/230 kV | JB-T-MOD-1-DI01 | T-MOD-1: 13.8/230 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 77 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0502 | I | Modular / portable power | Home run JB-T-MOD-1-DI01 to the control / marshalling room |  | PCM: power control module | JB-T-MOD-1-DI01 | T-MOD-1: 13.8/230 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 415 | 82
I-I-0503 | I | Modular / portable power | Analog instrument to JB JB-T-MOD-2-AI01: 8 x 1 pr (field cables) | T-MOD-2 | T-MOD-2: 13.8/230 kV | JB-T-MOD-2-AI01 | T-MOD-2: 13.8/230 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 77 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0504 | I | Modular / portable power | Home run JB-T-MOD-2-AI01 to the control / marshalling room |  | PCM: power control module | JB-T-MOD-2-AI01 | T-MOD-2: 13.8/230 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 799 | 191
I-I-0505 | I | Modular / portable power | Discrete device to JB JB-T-MOD-2-DI01: 16 x 1 pr (field cables) | T-MOD-2 | T-MOD-2: 13.8/230 kV | JB-T-MOD-2-DI01 | T-MOD-2: 13.8/230 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 16 | 1 |  |  |  | Tray / conduit | 77 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0506 | I | Modular / portable power | Home run JB-T-MOD-2-DI01 to the control / marshalling room |  | PCM: power control module | JB-T-MOD-2-DI01 | T-MOD-2: 13.8/230 kV | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 799 | 191
I-I-0507 | I | Modular / portable power | Analog instrument to JB JB-TM-1-AI01: 20 x 1 pr (field cables) | TM-1 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | JB-TM-1-AI01 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 108 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0508 | I | Modular / portable power | Home run JB-TM-1-AI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-TM-1-AI01 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 382 | 50
I-I-0509 | I | Modular / portable power | Analog instrument to JB JB-TM-1-AI02: 20 x 1 pr (field cables) | TM-1 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | JB-TM-1-AI02 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 108 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0510 | I | Modular / portable power | Home run JB-TM-1-AI02 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-TM-1-AI02 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 382 | 50
I-I-0511 | I | Modular / portable power | Analog instrument to JB JB-TM-1-AI03: 20 x 1 pr (field cables) | TM-1 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | JB-TM-1-AI03 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 108 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0512 | I | Modular / portable power | Home run JB-TM-1-AI03 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-TM-1-AI03 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 382 | 50
I-I-0513 | I | Modular / portable power | Analog instrument to JB JB-TM-1-AI04: 20 x 1 pr (field cables) | TM-1 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | JB-TM-1-AI04 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 108 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0514 | I | Modular / portable power | Home run JB-TM-1-AI04 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-TM-1-AI04 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 382 | 50
I-I-0515 | I | Modular / portable power | Analog instrument to JB JB-TM-1-AI05: 20 x 1 pr (field cables) | TM-1 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | JB-TM-1-AI05 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 108 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0516 | I | Modular / portable power | Home run JB-TM-1-AI05 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-TM-1-AI05 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 382 | 50
I-I-0517 | I | Modular / portable power | Discrete device to JB JB-TM-1-DI01: 20 x 1 pr (field cables) | TM-1 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | JB-TM-1-DI01 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 108 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0518 | I | Modular / portable power | Home run JB-TM-1-DI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-TM-1-DI01 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 382 | 50
I-I-0519 | I | Modular / portable power | Discrete device to JB JB-TM-1-DI02: 20 x 1 pr (field cables) | TM-1 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | JB-TM-1-DI02 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 108 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0520 | I | Modular / portable power | Home run JB-TM-1-DI02 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-TM-1-DI02 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 382 | 50
I-I-0521 | I | Modular / portable power | Discrete device to JB JB-TM-1-DI03: 20 x 1 pr (field cables) | TM-1 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | JB-TM-1-DI03 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 108 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0522 | I | Modular / portable power | Home run JB-TM-1-DI03 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-TM-1-DI03 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 382 | 50
I-I-0523 | I | Modular / portable power | Thermocouple to TC JB JB-TM-1-TC01: 20 x 1 pr (field cables) | TM-1 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | JB-TM-1-TC01 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 108 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0524 | I | Modular / portable power | Home run JB-TM-1-TC01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-TM-1-TC01 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Surface | 382 | 50
I-I-0525 | I | Modular / portable power | Analog instrument to JB JB-TM-2-AI01: 20 x 1 pr (field cables) | TM-2 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | JB-TM-2-AI01 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 108 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0526 | I | Modular / portable power | Home run JB-TM-2-AI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-TM-2-AI01 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 386 | 52
I-I-0527 | I | Modular / portable power | Analog instrument to JB JB-TM-2-AI02: 20 x 1 pr (field cables) | TM-2 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | JB-TM-2-AI02 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 108 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0528 | I | Modular / portable power | Home run JB-TM-2-AI02 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-TM-2-AI02 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 386 | 52
I-I-0529 | I | Modular / portable power | Analog instrument to JB JB-TM-2-AI03: 20 x 1 pr (field cables) | TM-2 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | JB-TM-2-AI03 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 108 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0530 | I | Modular / portable power | Home run JB-TM-2-AI03 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-TM-2-AI03 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 386 | 52
I-I-0531 | I | Modular / portable power | Analog instrument to JB JB-TM-2-AI04: 20 x 1 pr (field cables) | TM-2 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | JB-TM-2-AI04 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 108 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0532 | I | Modular / portable power | Home run JB-TM-2-AI04 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-TM-2-AI04 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 386 | 52
I-I-0533 | I | Modular / portable power | Analog instrument to JB JB-TM-2-AI05: 20 x 1 pr (field cables) | TM-2 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | JB-TM-2-AI05 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 108 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0534 | I | Modular / portable power | Home run JB-TM-2-AI05 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-TM-2-AI05 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 386 | 52
I-I-0535 | I | Modular / portable power | Discrete device to JB JB-TM-2-DI01: 20 x 1 pr (field cables) | TM-2 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | JB-TM-2-DI01 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 108 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0536 | I | Modular / portable power | Home run JB-TM-2-DI01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-TM-2-DI01 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 386 | 52
I-I-0537 | I | Modular / portable power | Discrete device to JB JB-TM-2-DI02: 20 x 1 pr (field cables) | TM-2 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | JB-TM-2-DI02 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 108 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0538 | I | Modular / portable power | Home run JB-TM-2-DI02 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-TM-2-DI02 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 386 | 52
I-I-0539 | I | Modular / portable power | Discrete device to JB JB-TM-2-DI03: 20 x 1 pr (field cables) | TM-2 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | JB-TM-2-DI03 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 108 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0540 | I | Modular / portable power | Home run JB-TM-2-DI03 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-TM-2-DI03 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Surface | 386 | 52
I-I-0541 | I | Modular / portable power | Thermocouple to TC JB JB-TM-2-TC01: 20 x 1 pr (field cables) | TM-2 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | JB-TM-2-TC01 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 108 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
I-I-0542 | I | Modular / portable power | Home run JB-TM-2-TC01 to the control / marshalling room | PAD-EH | PAD-EH 13.8 kV switchgear e-house | JB-TM-2-TC01 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | TCX¦24 pr¦16 | 24 pr | 16 | 1 | 1 |  |  |  | Surface | 386 | 52
I-I-0543 | I | Modular / portable power | Instrumentation |  | PCM: power control module |  | Water-injection skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | HV duct bank | 4299 | 87
I-I-0544 | I | Modular / portable power | Instrumentation |  | PCM: power control module |  | Water-injection skid | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | HV duct bank | 4299 | 87
I-P-0001 | I | Modular / portable power | LV power feeder |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | Aqueous ammonia (SC units) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 10 | 14.2 | HV duct bank | 4262 | 40 |  |  |  |  | VD 2.9 %
I-P-0002 | I | Modular / portable power | Black-start genset output |  | Black-start genset (proposed; requires study) |  | BS black-start switchgear | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦500 | 3/C+G | 500 kcmil | 10 | 1 | 480 | 2000 | 2532.3 | Tray | 0 | 41 |  |  |  |  | VD 0.1 %
I-P-0003 | I | Modular / portable power | Black-start genset output |  | Black-start genset (proposed; requires study) |  | BS black-start switchgear | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦500 | 3/C+G | 500 kcmil | 10 | 1 | 480 | 2000 | 2532.3 | Tray | 0 | 49 |  |  |  |  | VD 0.1 %
I-P-0004 | I | Modular / portable power | LV power feeder |  | PCM: power control module |  | BS black-start switchgear | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 562 | 64 |  |  |  |  | VD 2.6 %
I-P-0005 | I | Modular / portable power | LV power feeder |  | PCM: power control module |  | CONDITIONAL: BESS black-start alternative | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 550 | 32 |  |  |  |  | VD 2.4 %
I-P-0006 | I | Modular / portable power | LV power feeder |  | PCM: power control module |  | CONDITIONAL: SC-1 inlet chiller / evaporative cooler | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 3 | 1 | 480 | 500 | 707.6 | Duct bank | 40 | 52 |  |  |  |  | VD 0.3 %
I-P-0007 | I | Modular / portable power | LV power feeder |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | CONDITIONAL: SC-2 inlet chiller / evaporative cooler | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦500 | 3/C+G | 500 kcmil | 12 | 1 | 480 | 500 | 707.6 | HV duct bank | 4491 | 40 |  |  |  |  | VD 2.7 %
I-P-0008 | I | Modular / portable power | FC-5 SOFC output to inverter / AC cabinet | FC-5 | FC-5: SOFC module (Bloom ES5 class, 200-300 kW) |  | FC-5..12 inverter / AC cabinet / desulfurizer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦3/0 | 3/C+G | 3/0 | 2 | 1 | 480 | 250 | 316.5 | Duct bank | 139 | 32 |  |  |  |  | VD 0.8 %
I-P-0009 | I | Modular / portable power | FC-6 SOFC output to inverter / AC cabinet | FC-6 | FC-6: SOFC module (Bloom ES5 class, 200-300 kW) |  | FC-5..12 inverter / AC cabinet / desulfurizer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦3/0 | 3/C+G | 3/0 | 2 | 1 | 480 | 250 | 316.5 | Duct bank | 125 | 32 |  |  |  |  | VD 0.8 %
I-P-0010 | I | Modular / portable power | FC-7 SOFC output to inverter / AC cabinet | FC-7 | FC-7: SOFC module (Bloom ES5 class, 200-300 kW) |  | FC-5..12 inverter / AC cabinet / desulfurizer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦3/0 | 3/C+G | 3/0 | 2 | 1 | 480 | 250 | 316.5 | Duct bank | 111 | 32 |  |  |  |  | VD 0.7 %
I-P-0011 | I | Modular / portable power | FC-8 SOFC output to inverter / AC cabinet | FC-8 | FC-8: SOFC module (Bloom ES5 class, 200-300 kW) |  | FC-5..12 inverter / AC cabinet / desulfurizer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦3/0 | 3/C+G | 3/0 | 2 | 1 | 480 | 250 | 316.5 | Duct bank | 97 | 32 |  |  |  |  | VD 0.6 %
I-P-0012 | I | Modular / portable power | FC-9 SOFC output to inverter / AC cabinet | FC-9 | FC-9: SOFC module (Bloom ES5 class, 200-300 kW) |  | FC-5..12 inverter / AC cabinet / desulfurizer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦3/0 | 3/C+G | 3/0 | 2 | 1 | 480 | 250 | 316.5 | Duct bank | 83 | 32 |  |  |  |  | VD 0.6 %
I-P-0013 | I | Modular / portable power | FC-10 SOFC output to inverter / AC cabinet | FC-10 | FC-10: SOFC module (Bloom ES5 class, 200-300 kW) |  | FC-5..12 inverter / AC cabinet / desulfurizer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦3/0 | 3/C+G | 3/0 | 2 | 1 | 480 | 250 | 316.5 | Duct bank | 69 | 32 |  |  |  |  | VD 0.5 %
I-P-0014 | I | Modular / portable power | FC-11 SOFC output to inverter / AC cabinet | FC-11 | FC-11: SOFC module (Bloom ES5 class, 200-300 kW) |  | FC-5..12 inverter / AC cabinet / desulfurizer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦3/0 | 3/C+G | 3/0 | 2 | 1 | 480 | 250 | 316.5 | Duct bank | 55 | 32 |  |  |  |  | VD 0.4 %
I-P-0015 | I | Modular / portable power | FC-12 SOFC output to inverter / AC cabinet | FC-12 | FC-12: SOFC module (Bloom ES5 class, 200-300 kW) |  | FC-5..12 inverter / AC cabinet / desulfurizer | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦3/0 | 3/C+G | 3/0 | 2 | 1 | 480 | 250 | 316.5 | Duct bank | 46 | 32 |  |  |  |  | VD 0.4 %
I-P-0016 | I | Modular / portable power | FC-1 SOFC output to inverter / AC cabinet |  | FC-1: SOFC module (Bloom ES5 class, 200-300 kW) |  | Fuel-cell inverter / AC cabinet / desulfurizer | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦3/0 | 3/C+G | 3/0 | 2 | 1 | 480 | 250 | 316.5 | Tray | 62 | 32 |  |  |  |  | VD 0.5 %
I-P-0017 | I | Modular / portable power | FC-2 SOFC output to inverter / AC cabinet |  | FC-2: SOFC module (Bloom ES5 class, 200-300 kW) |  | Fuel-cell inverter / AC cabinet / desulfurizer | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦3/0 | 3/C+G | 3/0 | 2 | 1 | 480 | 250 | 316.5 | Tray | 39 | 41 |  |  |  |  | VD 0.4 %
I-P-0018 | I | Modular / portable power | FC-3 SOFC output to inverter / AC cabinet |  | FC-3: SOFC module (Bloom ES5 class, 200-300 kW) |  | Fuel-cell inverter / AC cabinet / desulfurizer | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦3/0 | 3/C+G | 3/0 | 2 | 1 | 480 | 250 | 316.5 | Tray | 11 | 55 |  |  |  |  | VD 0.3 %
I-P-0019 | I | Modular / portable power | FC-4 SOFC output to inverter / AC cabinet |  | FC-4: SOFC module (Bloom ES5 class, 200-300 kW) |  | Fuel-cell inverter / AC cabinet / desulfurizer | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦3/0 | 3/C+G | 3/0 | 2 | 1 | 480 | 250 | 316.5 | Tray | 0 | 52 |  |  |  |  | VD 0.3 %
I-P-0020 | I | Modular / portable power | Motor 1 of 6, 15 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | Fuel-gas compressors 3 x 100% electric | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦3/0 | 3/C+G | 3/0 | 1 | 1 | 480 | 15 | 21.2 | HV duct bank | 4396 | 40 |  |  |  |  | VD 2.9 %
I-P-0021 | I | Modular / portable power | Motor 2 of 6, 15 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | Fuel-gas compressors 3 x 100% electric | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦3/0 | 3/C+G | 3/0 | 1 | 1 | 480 | 15 | 21.2 | HV duct bank | 4396 | 40 |  |  |  |  | VD 2.9 %
I-P-0022 | I | Modular / portable power | Motor 3 of 6, 15 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | Fuel-gas compressors 3 x 100% electric | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦3/0 | 3/C+G | 3/0 | 1 | 1 | 480 | 15 | 21.2 | HV duct bank | 4396 | 40 |  |  |  |  | VD 2.9 %
I-P-0023 | I | Modular / portable power | Motor 4 of 6, 15 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | Fuel-gas compressors 3 x 100% electric | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦3/0 | 3/C+G | 3/0 | 1 | 1 | 480 | 15 | 21.2 | HV duct bank | 4396 | 40 |  |  |  |  | VD 2.9 %
I-P-0024 | I | Modular / portable power | Motor 5 of 6, 15 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | Fuel-gas compressors 3 x 100% electric | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦3/0 | 3/C+G | 3/0 | 1 | 1 | 480 | 15 | 21.2 | HV duct bank | 4396 | 40 |  |  |  |  | VD 2.9 %
I-P-0025 | I | Modular / portable power | Motor 6 of 6, 15 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | Fuel-gas compressors 3 x 100% electric | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦3/0 | 3/C+G | 3/0 | 1 | 1 | 480 | 15 | 21.2 | HV duct bank | 4396 | 40 |  |  |  |  | VD 2.9 %
I-P-0026 | I | Modular / portable power | LV power feeder |  | PCM: power control module |  | Gas conditioning skid | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Tray | 32 | 94 |  |  |  |  | VD 1.0 %
I-P-0027 | I | Modular / portable power | LV panel / distribution feeder |  | PCM: power control module |  | Lube oil / starting air / oily water building | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 79 | 111.8 | Tray | 32 | 164 |  |  |  |  | VD 1.1 %
I-P-0028 | I | Modular / portable power | LV panel / distribution feeder |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | MOD-EH | MOD-EH: 13.8 kV modular collector e-house | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 368 | 34 |  |  |  |  | VD 2.1 %
I-P-0029 | I | Modular / portable power | Fuel-cell AC cabinet to MOD-LV |  | Fuel-cell inverter / AC cabinet / desulfurizer |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 6 | 1 | 480 | 1000 | 1266.2 | Duct bank | 233 | 32 |  |  |  |  | VD 0.8 %
I-P-0030 | I | Modular / portable power | Fuel-cell AC cabinet to MOD-LV |  | FC-5..12 inverter / AC cabinet / desulfurizer |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦500 | 3/C+G | 500 kcmil | 12 | 1 | 480 | 2000 | 2532.3 | Duct bank | 2588 | 36
I-P-0031 | I | Modular / portable power | MT-1 microturbine output |  | MT-1: microturbine 1 MW (Capstone C1000 class) |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 6 | 1 | 480 | 1000 | 1266.2 | Duct bank | 106 | 32 |  |  |  |  | VD 0.4 %
I-P-0032 | I | Modular / portable power | MT-2 microturbine output |  | MT-2: microturbine 1 MW (Capstone C1000 class) |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 6 | 1 | 480 | 1000 | 1266.2 | Duct bank | 114 | 38 |  |  |  |  | VD 0.5 %
I-P-0033 | I | Modular / portable power | MT-3 microturbine output |  | MT-3: microturbine 1 MW (Capstone C1000 class) |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 6 | 1 | 480 | 1000 | 1266.2 | Duct bank | 121 | 45 |  |  |  |  | VD 0.5 %
I-P-0034 | I | Modular / portable power | MT-4 microturbine output | MT-4 | MT-4: microturbine 1 MW (Capstone C1000 class) |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦500 | 3/C+G | 500 kcmil | 12 | 1 | 480 | 1000 | 1266.2 | Duct bank | 2612 | 46 |  |  |  |  | VD 2.9 %
I-P-0035 | I | Modular / portable power | MT-5 microturbine output | MT-5 | MT-5: microturbine 1 MW (Capstone C1000 class) |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦500 | 3/C+G | 500 kcmil | 12 | 1 | 480 | 1000 | 1266.2 | Duct bank | 2636 | 36 |  |  |  |  | VD 2.9 %
I-P-0036 | I | Modular / portable power | MT-6 microturbine output | MT-6 | MT-6: microturbine 1 MW (Capstone C1000 class) |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦500 | 3/C+G | 500 kcmil | 12 | 1 | 480 | 1000 | 1266.2 | Duct bank | 2769 | 53
I-P-0037 | I | Modular / portable power | PAD-LV to PAD-TX | PAD-LV | PAD-LV 480 V paralleling switchboard | PAD-TX | PAD-TX 480 V : 13.8 kV | LV 600 V | XHHW-2 600 V 1/C Cu (feeder sets in tray / duct) | LV1C¦1/C¦500 | 1/C | 500 kcmil | 12 | 4 | 480 | 3000 | 3600 | Duct bank | 55 | 32 |  |  |  |  | 12 sets of 4 x 1/C (or bus duct)
I-P-0038 | I | Modular / portable power | LV panel / distribution feeder |  | PCM: power control module |  | PCM: power control module | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 38 | 53.8 | Tray | 0 | 32 |  |  |  |  | VD 0.2 %
I-P-0039 | I | Modular / portable power | Motor 1 of 1, 15 kW |  | PCM: power control module |  | RICE 1 SCR + oxidation catalyst and stack | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 470 | 160 |  |  |  |  | VD 2.6 %
I-P-0040 | I | Modular / portable power | Area / platform lighting circuit 1 (6 fixtures) |  | PCM: power control module |  | RICE 1 SCR + oxidation catalyst and stack | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Duct bank | 770 | 160 |  |  |  |  | fixture-to-fixture run included
I-P-0041 | I | Modular / portable power | Motor 1 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 1 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦1 | 3/C+3G | 1 | 1 | 1 | 480 | 30 | 42 | Duct bank | 825 | 139 |  |  |  |  | VD 2.5 %
I-P-0042 | I | Modular / portable power | Motor 2 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 1 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦1 | 3/C+3G | 1 | 1 | 1 | 480 | 30 | 42 | Duct bank | 825 | 139 |  |  |  |  | VD 2.5 %
I-P-0043 | I | Modular / portable power | Motor 3 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 1 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦1 | 3/C+3G | 1 | 1 | 1 | 480 | 30 | 42 | Duct bank | 825 | 139 |  |  |  |  | VD 2.5 %
I-P-0044 | I | Modular / portable power | Motor 4 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 1 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦1 | 3/C+3G | 1 | 1 | 1 | 480 | 30 | 42 | Duct bank | 825 | 139 |  |  |  |  | VD 2.5 %
I-P-0045 | I | Modular / portable power | Motor 5 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 1 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦1 | 3/C+3G | 1 | 1 | 1 | 480 | 30 | 42 | Duct bank | 825 | 139 |  |  |  |  | VD 2.5 %
I-P-0046 | I | Modular / portable power | Motor 1 of 1, 15 kW |  | PCM: power control module |  | RICE 2 SCR + oxidation catalyst and stack | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 470 | 132 |  |  |  |  | VD 2.5 %
I-P-0047 | I | Modular / portable power | Area / platform lighting circuit 1 (6 fixtures) |  | PCM: power control module |  | RICE 2 SCR + oxidation catalyst and stack | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Duct bank | 770 | 132 |  |  |  |  | fixture-to-fixture run included
I-P-0048 | I | Modular / portable power | Motor 1 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 2 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦2 | 3/C+3G | 2 | 1 | 1 | 480 | 30 | 42 | Duct bank | 630 | 192 |  |  |  |  | VD 2.7 %
I-P-0049 | I | Modular / portable power | Motor 2 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 2 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦2 | 3/C+3G | 2 | 1 | 1 | 480 | 30 | 42 | Duct bank | 630 | 192 |  |  |  |  | VD 2.7 %
I-P-0050 | I | Modular / portable power | Motor 3 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 2 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦2 | 3/C+3G | 2 | 1 | 1 | 480 | 30 | 42 | Duct bank | 630 | 192 |  |  |  |  | VD 2.7 %
I-P-0051 | I | Modular / portable power | Motor 4 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 2 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦2 | 3/C+3G | 2 | 1 | 1 | 480 | 30 | 42 | Duct bank | 630 | 192 |  |  |  |  | VD 2.7 %
I-P-0052 | I | Modular / portable power | Motor 5 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 2 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦2 | 3/C+3G | 2 | 1 | 1 | 480 | 30 | 42 | Duct bank | 630 | 192 |  |  |  |  | VD 2.7 %
I-P-0053 | I | Modular / portable power | Motor 1 of 1, 15 kW |  | PCM: power control module |  | RICE 3 SCR + oxidation catalyst and stack | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 470 | 104 |  |  |  |  | VD 2.4 %
I-P-0054 | I | Modular / portable power | Area / platform lighting circuit 1 (6 fixtures) |  | PCM: power control module |  | RICE 3 SCR + oxidation catalyst and stack | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Duct bank | 770 | 104 |  |  |  |  | fixture-to-fixture run included
I-P-0055 | I | Modular / portable power | Motor 1 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 3 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦6 | 3/C+3G | 6 | 1 | 1 | 480 | 30 | 42 | Tray | 112 | 232 |  |  |  |  | VD 2.8 %
I-P-0056 | I | Modular / portable power | Motor 2 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 3 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦6 | 3/C+3G | 6 | 1 | 1 | 480 | 30 | 42 | Tray | 112 | 232 |  |  |  |  | VD 2.8 %
I-P-0057 | I | Modular / portable power | Motor 3 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 3 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦6 | 3/C+3G | 6 | 1 | 1 | 480 | 30 | 42 | Tray | 112 | 232 |  |  |  |  | VD 2.8 %
I-P-0058 | I | Modular / portable power | Motor 4 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 3 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦6 | 3/C+3G | 6 | 1 | 1 | 480 | 30 | 42 | Tray | 112 | 232 |  |  |  |  | VD 2.8 %
I-P-0059 | I | Modular / portable power | Motor 5 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 3 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦6 | 3/C+3G | 6 | 1 | 1 | 480 | 30 | 42 | Tray | 112 | 232 |  |  |  |  | VD 2.8 %
I-P-0060 | I | Modular / portable power | Motor 1 of 1, 15 kW |  | PCM: power control module |  | RICE 4 SCR + oxidation catalyst and stack | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 470 | 76 |  |  |  |  | VD 2.3 %
I-P-0061 | I | Modular / portable power | Area / platform lighting circuit 1 (6 fixtures) |  | PCM: power control module |  | RICE 4 SCR + oxidation catalyst and stack | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Duct bank | 770 | 76 |  |  |  |  | fixture-to-fixture run included
I-P-0062 | I | Modular / portable power | Motor 1 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 4 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦6 | 3/C+3G | 6 | 1 | 1 | 480 | 30 | 42 | Tray | 80 | 206 |  |  |  |  | VD 2.4 %
I-P-0063 | I | Modular / portable power | Motor 2 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 4 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦6 | 3/C+3G | 6 | 1 | 1 | 480 | 30 | 42 | Tray | 80 | 206 |  |  |  |  | VD 2.4 %
I-P-0064 | I | Modular / portable power | Motor 3 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 4 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦6 | 3/C+3G | 6 | 1 | 1 | 480 | 30 | 42 | Tray | 80 | 206 |  |  |  |  | VD 2.4 %
I-P-0065 | I | Modular / portable power | Motor 4 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 4 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦6 | 3/C+3G | 6 | 1 | 1 | 480 | 30 | 42 | Tray | 80 | 206 |  |  |  |  | VD 2.4 %
I-P-0066 | I | Modular / portable power | Motor 5 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 4 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦6 | 3/C+3G | 6 | 1 | 1 | 480 | 30 | 42 | Tray | 80 | 206 |  |  |  |  | VD 2.4 %
I-P-0067 | I | Modular / portable power | Motor 1 of 1, 15 kW |  | PCM: power control module |  | RICE 5 SCR + oxidation catalyst and stack | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 322 | 196 |  |  |  |  | VD 2.1 %
I-P-0068 | I | Modular / portable power | Area / platform lighting circuit 1 (6 fixtures) |  | PCM: power control module |  | RICE 5 SCR + oxidation catalyst and stack | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Duct bank | 622 | 196 |  |  |  |  | fixture-to-fixture run included
I-P-0069 | I | Modular / portable power | Motor 1 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 5 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦6 | 3/C+3G | 6 | 1 | 1 | 480 | 30 | 42 | Tray | 80 | 178 |  |  |  |  | VD 2.1 %
I-P-0070 | I | Modular / portable power | Motor 2 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 5 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦6 | 3/C+3G | 6 | 1 | 1 | 480 | 30 | 42 | Tray | 80 | 178 |  |  |  |  | VD 2.1 %
I-P-0071 | I | Modular / portable power | Motor 3 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 5 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦6 | 3/C+3G | 6 | 1 | 1 | 480 | 30 | 42 | Tray | 80 | 178 |  |  |  |  | VD 2.1 %
I-P-0072 | I | Modular / portable power | Motor 4 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 5 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦6 | 3/C+3G | 6 | 1 | 1 | 480 | 30 | 42 | Tray | 80 | 178 |  |  |  |  | VD 2.1 %
I-P-0073 | I | Modular / portable power | Motor 5 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 5 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦6 | 3/C+3G | 6 | 1 | 1 | 480 | 30 | 42 | Tray | 80 | 178 |  |  |  |  | VD 2.1 %
I-P-0074 | I | Modular / portable power | Motor 1 of 1, 15 kW |  | PCM: power control module |  | RICE 6 SCR + oxidation catalyst and stack | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 322 | 168 |  |  |  |  | VD 2.0 %
I-P-0075 | I | Modular / portable power | Area / platform lighting circuit 1 (6 fixtures) |  | PCM: power control module |  | RICE 6 SCR + oxidation catalyst and stack | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Duct bank | 622 | 168 |  |  |  |  | fixture-to-fixture run included
I-P-0076 | I | Modular / portable power | Motor 1 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 6 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦6 | 3/C+3G | 6 | 1 | 1 | 480 | 30 | 42 | Tray | 80 | 150 |  |  |  |  | VD 1.9 %
I-P-0077 | I | Modular / portable power | Motor 2 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 6 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦6 | 3/C+3G | 6 | 1 | 1 | 480 | 30 | 42 | Tray | 80 | 150 |  |  |  |  | VD 1.9 %
I-P-0078 | I | Modular / portable power | Motor 3 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 6 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦6 | 3/C+3G | 6 | 1 | 1 | 480 | 30 | 42 | Tray | 80 | 150 |  |  |  |  | VD 1.9 %
I-P-0079 | I | Modular / portable power | Motor 4 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 6 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦6 | 3/C+3G | 6 | 1 | 1 | 480 | 30 | 42 | Tray | 80 | 150 |  |  |  |  | VD 1.9 %
I-P-0080 | I | Modular / portable power | Motor 5 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 6 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦6 | 3/C+3G | 6 | 1 | 1 | 480 | 30 | 42 | Tray | 80 | 150 |  |  |  |  | VD 1.9 %
I-P-0081 | I | Modular / portable power | Motor 1 of 1, 15 kW |  | PCM: power control module |  | RICE 7 SCR + oxidation catalyst and stack | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 322 | 140 |  |  |  |  | VD 3.0 %
I-P-0082 | I | Modular / portable power | Area / platform lighting circuit 1 (6 fixtures) |  | PCM: power control module |  | RICE 7 SCR + oxidation catalyst and stack | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Duct bank | 622 | 140 |  |  |  |  | fixture-to-fixture run included
I-P-0083 | I | Modular / portable power | Motor 1 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 7 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦6 | 3/C+3G | 6 | 1 | 1 | 480 | 30 | 42 | Tray | 80 | 122 |  |  |  |  | VD 1.7 %
I-P-0084 | I | Modular / portable power | Motor 2 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 7 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦6 | 3/C+3G | 6 | 1 | 1 | 480 | 30 | 42 | Tray | 80 | 122 |  |  |  |  | VD 1.7 %
I-P-0085 | I | Modular / portable power | Motor 3 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 7 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦6 | 3/C+3G | 6 | 1 | 1 | 480 | 30 | 42 | Tray | 80 | 122 |  |  |  |  | VD 1.7 %
I-P-0086 | I | Modular / portable power | Motor 4 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 7 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦6 | 3/C+3G | 6 | 1 | 1 | 480 | 30 | 42 | Tray | 80 | 122 |  |  |  |  | VD 1.7 %
I-P-0087 | I | Modular / portable power | Motor 5 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 7 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦6 | 3/C+3G | 6 | 1 | 1 | 480 | 30 | 42 | Tray | 80 | 122 |  |  |  |  | VD 1.7 %
I-P-0088 | I | Modular / portable power | Motor 1 of 1, 15 kW |  | PCM: power control module |  | RICE 8 SCR + oxidation catalyst and stack | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 322 | 112 |  |  |  |  | VD 2.8 %
I-P-0089 | I | Modular / portable power | Area / platform lighting circuit 1 (6 fixtures) |  | PCM: power control module |  | RICE 8 SCR + oxidation catalyst and stack | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Duct bank | 622 | 112 |  |  |  |  | fixture-to-fixture run included
I-P-0090 | I | Modular / portable power | Motor 1 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 8 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦6 | 3/C+3G | 6 | 1 | 1 | 480 | 30 | 42 | Tray | 80 | 94 |  |  |  |  | VD 1.4 %
I-P-0091 | I | Modular / portable power | Motor 2 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 8 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦6 | 3/C+3G | 6 | 1 | 1 | 480 | 30 | 42 | Tray | 80 | 94 |  |  |  |  | VD 1.4 %
I-P-0092 | I | Modular / portable power | Motor 3 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 8 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦6 | 3/C+3G | 6 | 1 | 1 | 480 | 30 | 42 | Tray | 80 | 94 |  |  |  |  | VD 1.4 %
I-P-0093 | I | Modular / portable power | Motor 4 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 8 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦6 | 3/C+3G | 6 | 1 | 1 | 480 | 30 | 42 | Tray | 80 | 94 |  |  |  |  | VD 1.4 %
I-P-0094 | I | Modular / portable power | Motor 5 of 5, 30 kW (VFD output) |  | PCM: power control module |  | RICE 8 radiators (5) | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦6 | 3/C+3G | 6 | 1 | 1 | 480 | 30 | 42 | Tray | 80 | 94 |  |  |  |  | VD 1.4 %
I-P-0095 | I | Modular / portable power | LV panel / distribution feeder |  | PCM: power control module |  | RICE CEMS | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 260 | 131 |  |  |  |  | VD 2.0 %
I-P-0096 | I | Modular / portable power | LV power feeder |  | PCM: power control module | RICE | RICE engine hall (8 engines) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 367 | 95 |  |  |  |  | VD 3.0 %
I-P-0097 | I | Modular / portable power | Motor 1 of 6, 22 kW |  | PCM: power control module | RICE-1 | RICE engine-generator 1 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 550 | 137 |  |  |  |  | VD 2.6 %
I-P-0098 | I | Modular / portable power | Motor 2 of 6, 22 kW |  | PCM: power control module | RICE-1 | RICE engine-generator 1 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 550 | 137 |  |  |  |  | VD 2.6 %
I-P-0099 | I | Modular / portable power | Motor 3 of 6, 22 kW |  | PCM: power control module | RICE-1 | RICE engine-generator 1 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 550 | 137 |  |  |  |  | VD 2.6 %
I-P-0100 | I | Modular / portable power | Motor 4 of 6, 22 kW |  | PCM: power control module | RICE-1 | RICE engine-generator 1 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 550 | 137 |  |  |  |  | VD 2.6 %
I-P-0101 | I | Modular / portable power | Motor 5 of 6, 22 kW |  | PCM: power control module | RICE-1 | RICE engine-generator 1 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 550 | 137 |  |  |  |  | VD 2.6 %
I-P-0102 | I | Modular / portable power | Motor 6 of 6, 22 kW |  | PCM: power control module | RICE-1 | RICE engine-generator 1 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 550 | 137 |  |  |  |  | VD 2.6 %
I-P-0103 | I | Modular / portable power | 480 V welding receptacle 1 |  | PCM: power control module | RICE-1 | RICE engine-generator 1 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 60 | 76 | Duct bank | 550 | 137 |  |  |  |  | VD 2.5 %
I-P-0104 | I | Modular / portable power | 480 V welding receptacle 2 |  | PCM: power control module | RICE-1 | RICE engine-generator 1 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 60 | 76 | Duct bank | 550 | 137 |  |  |  |  | VD 2.5 %
I-P-0105 | I | Modular / portable power | 480 V welding receptacle 3 |  | PCM: power control module | RICE-1 | RICE engine-generator 1 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 60 | 76 | Duct bank | 550 | 137 |  |  |  |  | VD 2.5 %
I-P-0106 | I | Modular / portable power | 480 V welding receptacle 4 |  | PCM: power control module | RICE-1 | RICE engine-generator 1 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 60 | 76 | Duct bank | 550 | 137 |  |  |  |  | VD 2.5 %
I-P-0107 | I | Modular / portable power | Motor 1 of 6, 22 kW |  | PCM: power control module | RICE-2 | RICE engine-generator 2 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 550 | 109 |  |  |  |  | VD 2.5 %
I-P-0108 | I | Modular / portable power | Motor 2 of 6, 22 kW |  | PCM: power control module | RICE-2 | RICE engine-generator 2 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 550 | 109 |  |  |  |  | VD 2.5 %
I-P-0109 | I | Modular / portable power | Motor 3 of 6, 22 kW |  | PCM: power control module | RICE-2 | RICE engine-generator 2 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 550 | 109 |  |  |  |  | VD 2.5 %
I-P-0110 | I | Modular / portable power | Motor 4 of 6, 22 kW |  | PCM: power control module | RICE-2 | RICE engine-generator 2 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 550 | 109 |  |  |  |  | VD 2.5 %
I-P-0111 | I | Modular / portable power | Motor 5 of 6, 22 kW |  | PCM: power control module | RICE-2 | RICE engine-generator 2 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 550 | 109 |  |  |  |  | VD 2.5 %
I-P-0112 | I | Modular / portable power | Motor 6 of 6, 22 kW |  | PCM: power control module | RICE-2 | RICE engine-generator 2 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 550 | 109 |  |  |  |  | VD 2.5 %
I-P-0113 | I | Modular / portable power | 480 V welding receptacle 1 |  | PCM: power control module | RICE-2 | RICE engine-generator 2 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 60 | 76 | Duct bank | 550 | 109 |  |  |  |  | VD 2.4 %
I-P-0114 | I | Modular / portable power | 480 V welding receptacle 2 |  | PCM: power control module | RICE-2 | RICE engine-generator 2 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 60 | 76 | Duct bank | 550 | 109 |  |  |  |  | VD 2.4 %
I-P-0115 | I | Modular / portable power | 480 V welding receptacle 3 |  | PCM: power control module | RICE-2 | RICE engine-generator 2 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 60 | 76 | Duct bank | 550 | 109 |  |  |  |  | VD 2.4 %
I-P-0116 | I | Modular / portable power | 480 V welding receptacle 4 |  | PCM: power control module | RICE-2 | RICE engine-generator 2 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1/0 | 3/C+G | 1/0 | 1 | 1 | 480 | 60 | 76 | Duct bank | 550 | 109 |  |  |  |  | VD 2.4 %
I-P-0117 | I | Modular / portable power | Motor 1 of 6, 22 kW |  | PCM: power control module | RICE-3 | RICE engine-generator 3 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 550 | 81 |  |  |  |  | VD 2.4 %
I-P-0118 | I | Modular / portable power | Motor 2 of 6, 22 kW |  | PCM: power control module | RICE-3 | RICE engine-generator 3 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 550 | 81 |  |  |  |  | VD 2.4 %
I-P-0119 | I | Modular / portable power | Motor 3 of 6, 22 kW |  | PCM: power control module | RICE-3 | RICE engine-generator 3 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 550 | 81 |  |  |  |  | VD 2.4 %
I-P-0120 | I | Modular / portable power | Motor 4 of 6, 22 kW |  | PCM: power control module | RICE-3 | RICE engine-generator 3 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 550 | 81 |  |  |  |  | VD 2.4 %
I-P-0121 | I | Modular / portable power | Motor 5 of 6, 22 kW |  | PCM: power control module | RICE-3 | RICE engine-generator 3 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 550 | 81 |  |  |  |  | VD 2.4 %
I-P-0122 | I | Modular / portable power | Motor 6 of 6, 22 kW |  | PCM: power control module | RICE-3 | RICE engine-generator 3 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 550 | 81 |  |  |  |  | VD 2.4 %
I-P-0123 | I | Modular / portable power | 480 V welding receptacle 1 |  | PCM: power control module | RICE-3 | RICE engine-generator 3 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 60 | 76 | Duct bank | 550 | 81 |  |  |  |  | VD 2.9 %
I-P-0124 | I | Modular / portable power | 480 V welding receptacle 2 |  | PCM: power control module | RICE-3 | RICE engine-generator 3 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 60 | 76 | Duct bank | 550 | 81 |  |  |  |  | VD 2.9 %
I-P-0125 | I | Modular / portable power | 480 V welding receptacle 3 |  | PCM: power control module | RICE-3 | RICE engine-generator 3 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 60 | 76 | Duct bank | 550 | 81 |  |  |  |  | VD 2.9 %
I-P-0126 | I | Modular / portable power | 480 V welding receptacle 4 |  | PCM: power control module | RICE-3 | RICE engine-generator 3 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 60 | 76 | Duct bank | 550 | 81 |  |  |  |  | VD 2.9 %
I-P-0127 | I | Modular / portable power | Motor 1 of 6, 22 kW |  | PCM: power control module | RICE-4 | RICE engine-generator 4 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 550 | 53 |  |  |  |  | VD 2.3 %
I-P-0128 | I | Modular / portable power | Motor 2 of 6, 22 kW |  | PCM: power control module | RICE-4 | RICE engine-generator 4 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 550 | 53 |  |  |  |  | VD 2.3 %
I-P-0129 | I | Modular / portable power | Motor 3 of 6, 22 kW |  | PCM: power control module | RICE-4 | RICE engine-generator 4 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 550 | 53 |  |  |  |  | VD 2.3 %
I-P-0130 | I | Modular / portable power | Motor 4 of 6, 22 kW |  | PCM: power control module | RICE-4 | RICE engine-generator 4 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 550 | 53 |  |  |  |  | VD 2.3 %
I-P-0131 | I | Modular / portable power | Motor 5 of 6, 22 kW |  | PCM: power control module | RICE-4 | RICE engine-generator 4 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 550 | 53 |  |  |  |  | VD 2.3 %
I-P-0132 | I | Modular / portable power | Motor 6 of 6, 22 kW |  | PCM: power control module | RICE-4 | RICE engine-generator 4 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 550 | 53 |  |  |  |  | VD 2.3 %
I-P-0133 | I | Modular / portable power | 480 V welding receptacle 1 |  | PCM: power control module | RICE-4 | RICE engine-generator 4 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 60 | 76 | Duct bank | 550 | 53 |  |  |  |  | VD 2.8 %
I-P-0134 | I | Modular / portable power | 480 V welding receptacle 2 |  | PCM: power control module | RICE-4 | RICE engine-generator 4 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 60 | 76 | Duct bank | 550 | 53 |  |  |  |  | VD 2.8 %
I-P-0135 | I | Modular / portable power | 480 V welding receptacle 3 |  | PCM: power control module | RICE-4 | RICE engine-generator 4 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 60 | 76 | Duct bank | 550 | 53 |  |  |  |  | VD 2.8 %
I-P-0136 | I | Modular / portable power | 480 V welding receptacle 4 |  | PCM: power control module | RICE-4 | RICE engine-generator 4 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 60 | 76 | Duct bank | 550 | 53 |  |  |  |  | VD 2.8 %
I-P-0137 | I | Modular / portable power | Motor 1 of 6, 22 kW |  | PCM: power control module | RICE-5 | RICE engine-generator 5 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 367 | 208 |  |  |  |  | VD 2.2 %
I-P-0138 | I | Modular / portable power | Motor 2 of 6, 22 kW |  | PCM: power control module | RICE-5 | RICE engine-generator 5 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 367 | 208 |  |  |  |  | VD 2.2 %
I-P-0139 | I | Modular / portable power | Motor 3 of 6, 22 kW |  | PCM: power control module | RICE-5 | RICE engine-generator 5 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 367 | 208 |  |  |  |  | VD 2.2 %
I-P-0140 | I | Modular / portable power | Motor 4 of 6, 22 kW |  | PCM: power control module | RICE-5 | RICE engine-generator 5 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 367 | 208 |  |  |  |  | VD 2.2 %
I-P-0141 | I | Modular / portable power | Motor 5 of 6, 22 kW |  | PCM: power control module | RICE-5 | RICE engine-generator 5 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 367 | 208 |  |  |  |  | VD 2.2 %
I-P-0142 | I | Modular / portable power | Motor 6 of 6, 22 kW |  | PCM: power control module | RICE-5 | RICE engine-generator 5 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 367 | 208 |  |  |  |  | VD 2.2 %
I-P-0143 | I | Modular / portable power | 480 V welding receptacle 1 |  | PCM: power control module | RICE-5 | RICE engine-generator 5 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 60 | 76 | Duct bank | 367 | 208 |  |  |  |  | VD 2.7 %
I-P-0144 | I | Modular / portable power | 480 V welding receptacle 2 |  | PCM: power control module | RICE-5 | RICE engine-generator 5 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 60 | 76 | Duct bank | 367 | 208 |  |  |  |  | VD 2.7 %
I-P-0145 | I | Modular / portable power | 480 V welding receptacle 3 |  | PCM: power control module | RICE-5 | RICE engine-generator 5 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 60 | 76 | Duct bank | 367 | 208 |  |  |  |  | VD 2.7 %
I-P-0146 | I | Modular / portable power | 480 V welding receptacle 4 |  | PCM: power control module | RICE-5 | RICE engine-generator 5 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 60 | 76 | Duct bank | 367 | 208 |  |  |  |  | VD 2.7 %
I-P-0147 | I | Modular / portable power | Motor 1 of 6, 22 kW |  | PCM: power control module | RICE-6 | RICE engine-generator 6 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 367 | 180 |  |  |  |  | VD 2.1 %
I-P-0148 | I | Modular / portable power | Motor 2 of 6, 22 kW |  | PCM: power control module | RICE-6 | RICE engine-generator 6 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 367 | 180 |  |  |  |  | VD 2.1 %
I-P-0149 | I | Modular / portable power | Motor 3 of 6, 22 kW |  | PCM: power control module | RICE-6 | RICE engine-generator 6 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 367 | 180 |  |  |  |  | VD 2.1 %
I-P-0150 | I | Modular / portable power | Motor 4 of 6, 22 kW |  | PCM: power control module | RICE-6 | RICE engine-generator 6 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 367 | 180 |  |  |  |  | VD 2.1 %
I-P-0151 | I | Modular / portable power | Motor 5 of 6, 22 kW |  | PCM: power control module | RICE-6 | RICE engine-generator 6 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 367 | 180 |  |  |  |  | VD 2.1 %
I-P-0152 | I | Modular / portable power | Motor 6 of 6, 22 kW |  | PCM: power control module | RICE-6 | RICE engine-generator 6 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 367 | 180 |  |  |  |  | VD 2.1 %
I-P-0153 | I | Modular / portable power | 480 V welding receptacle 1 |  | PCM: power control module | RICE-6 | RICE engine-generator 6 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 60 | 76 | Duct bank | 367 | 180 |  |  |  |  | VD 2.5 %
I-P-0154 | I | Modular / portable power | 480 V welding receptacle 2 |  | PCM: power control module | RICE-6 | RICE engine-generator 6 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 60 | 76 | Duct bank | 367 | 180 |  |  |  |  | VD 2.5 %
I-P-0155 | I | Modular / portable power | 480 V welding receptacle 3 |  | PCM: power control module | RICE-6 | RICE engine-generator 6 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 60 | 76 | Duct bank | 367 | 180 |  |  |  |  | VD 2.5 %
I-P-0156 | I | Modular / portable power | 480 V welding receptacle 4 |  | PCM: power control module | RICE-6 | RICE engine-generator 6 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦1 | 3/C+G | 1 | 1 | 1 | 480 | 60 | 76 | Duct bank | 367 | 180 |  |  |  |  | VD 2.5 %
I-P-0157 | I | Modular / portable power | Motor 1 of 6, 22 kW |  | PCM: power control module | RICE-7 | RICE engine-generator 7 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 22 | 31.1 | Tray | 0 | 189 |  |  |  |  | VD 1.8 %
I-P-0158 | I | Modular / portable power | Motor 2 of 6, 22 kW |  | PCM: power control module | RICE-7 | RICE engine-generator 7 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 22 | 31.1 | Tray | 0 | 189 |  |  |  |  | VD 1.8 %
I-P-0159 | I | Modular / portable power | Motor 3 of 6, 22 kW |  | PCM: power control module | RICE-7 | RICE engine-generator 7 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 22 | 31.1 | Tray | 0 | 189 |  |  |  |  | VD 1.8 %
I-P-0160 | I | Modular / portable power | Motor 4 of 6, 22 kW |  | PCM: power control module | RICE-7 | RICE engine-generator 7 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 22 | 31.1 | Tray | 0 | 189 |  |  |  |  | VD 1.8 %
I-P-0161 | I | Modular / portable power | Motor 5 of 6, 22 kW |  | PCM: power control module | RICE-7 | RICE engine-generator 7 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 22 | 31.1 | Tray | 0 | 189 |  |  |  |  | VD 1.8 %
I-P-0162 | I | Modular / portable power | Motor 6 of 6, 22 kW |  | PCM: power control module | RICE-7 | RICE engine-generator 7 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 22 | 31.1 | Tray | 0 | 189 |  |  |  |  | VD 1.8 %
I-P-0163 | I | Modular / portable power | 480 V welding receptacle 1 |  | PCM: power control module | RICE-7 | RICE engine-generator 7 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 0 | 189 |  |  |  |  | VD 1.1 %
I-P-0164 | I | Modular / portable power | 480 V welding receptacle 2 |  | PCM: power control module | RICE-7 | RICE engine-generator 7 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 0 | 189 |  |  |  |  | VD 1.1 %
I-P-0165 | I | Modular / portable power | 480 V welding receptacle 3 |  | PCM: power control module | RICE-7 | RICE engine-generator 7 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 0 | 189 |  |  |  |  | VD 1.1 %
I-P-0166 | I | Modular / portable power | 480 V welding receptacle 4 |  | PCM: power control module | RICE-7 | RICE engine-generator 7 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 0 | 189 |  |  |  |  | VD 1.1 %
I-P-0167 | I | Modular / portable power | Motor 1 of 6, 22 kW |  | PCM: power control module | RICE-8 | RICE engine-generator 8 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 22 | 31.1 | Tray | 0 | 161 |  |  |  |  | VD 1.5 %
I-P-0168 | I | Modular / portable power | Motor 2 of 6, 22 kW |  | PCM: power control module | RICE-8 | RICE engine-generator 8 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 22 | 31.1 | Tray | 0 | 161 |  |  |  |  | VD 1.5 %
I-P-0169 | I | Modular / portable power | Motor 3 of 6, 22 kW |  | PCM: power control module | RICE-8 | RICE engine-generator 8 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 22 | 31.1 | Tray | 0 | 161 |  |  |  |  | VD 1.5 %
I-P-0170 | I | Modular / portable power | Motor 4 of 6, 22 kW |  | PCM: power control module | RICE-8 | RICE engine-generator 8 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 22 | 31.1 | Tray | 0 | 161 |  |  |  |  | VD 1.5 %
I-P-0171 | I | Modular / portable power | Motor 5 of 6, 22 kW |  | PCM: power control module | RICE-8 | RICE engine-generator 8 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 22 | 31.1 | Tray | 0 | 161 |  |  |  |  | VD 1.5 %
I-P-0172 | I | Modular / portable power | Motor 6 of 6, 22 kW |  | PCM: power control module | RICE-8 | RICE engine-generator 8 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 22 | 31.1 | Tray | 0 | 161 |  |  |  |  | VD 1.5 %
I-P-0173 | I | Modular / portable power | 480 V welding receptacle 1 |  | PCM: power control module | RICE-8 | RICE engine-generator 8 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 0 | 161 |  |  |  |  | VD 0.9 %
I-P-0174 | I | Modular / portable power | 480 V welding receptacle 2 |  | PCM: power control module | RICE-8 | RICE engine-generator 8 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 0 | 161 |  |  |  |  | VD 0.9 %
I-P-0175 | I | Modular / portable power | 480 V welding receptacle 3 |  | PCM: power control module | RICE-8 | RICE engine-generator 8 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 0 | 161 |  |  |  |  | VD 0.9 %
I-P-0176 | I | Modular / portable power | 480 V welding receptacle 4 |  | PCM: power control module | RICE-8 | RICE engine-generator 8 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 60 | 76 | Tray | 0 | 161 |  |  |  |  | VD 0.9 %
I-P-0177 | I | Modular / portable power | LV power feeder |  | PCM: power control module |  | Reagent storage | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Tray | 32 | 32 |  |  |  |  | VD 0.7 %
I-P-0178 | I | Modular / portable power | Motor 1 of 2, 30 kW |  | PCM: power control module |  | SC-1 SCR / CO catalyst | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 40 | 142 |  |  |  |  | VD 1.5 %
I-P-0179 | I | Modular / portable power | Motor 2 of 2, 30 kW |  | PCM: power control module |  | SC-1 SCR / CO catalyst | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 40 | 142 |  |  |  |  | VD 1.5 %
I-P-0180 | I | Modular / portable power | Motor 1 of 4, 15 kW |  | PCM: power control module |  | SC-1 lube-oil fin-fan cooler | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 82 | 82 |  |  |  |  | VD 1.7 %
I-P-0181 | I | Modular / portable power | Motor 2 of 4, 15 kW |  | PCM: power control module |  | SC-1 lube-oil fin-fan cooler | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 82 | 82 |  |  |  |  | VD 1.7 %
I-P-0182 | I | Modular / portable power | Motor 3 of 4, 15 kW |  | PCM: power control module |  | SC-1 lube-oil fin-fan cooler | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 82 | 82 |  |  |  |  | VD 1.7 %
I-P-0183 | I | Modular / portable power | Motor 4 of 4, 15 kW |  | PCM: power control module |  | SC-1 lube-oil fin-fan cooler | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 82 | 82 |  |  |  |  | VD 1.7 %
I-P-0184 | I | Modular / portable power | Area / platform lighting circuit 1 (4 fixtures) |  | PCM: power control module |  | SC-1 stack (80 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 3 | 5 | HV duct bank | 4778 | 144 |  |  |  |  | fixture-to-fixture run included
I-P-0185 | I | Modular / portable power | Motor 1 of 10, 30 kW |  | PCM: power control module | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 40 | 52 |  |  |  |  | VD 0.8 %
I-P-0186 | I | Modular / portable power | Motor 2 of 10, 30 kW |  | PCM: power control module | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 40 | 52 |  |  |  |  | VD 0.8 %
I-P-0187 | I | Modular / portable power | Motor 3 of 10, 30 kW |  | PCM: power control module | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 40 | 52 |  |  |  |  | VD 0.8 %
I-P-0188 | I | Modular / portable power | Motor 4 of 10, 30 kW |  | PCM: power control module | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 40 | 52 |  |  |  |  | VD 0.8 %
I-P-0189 | I | Modular / portable power | Motor 5 of 10, 30 kW |  | PCM: power control module | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 40 | 52 |  |  |  |  | VD 0.8 %
I-P-0190 | I | Modular / portable power | Motor 6 of 10, 30 kW |  | PCM: power control module | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 40 | 52 |  |  |  |  | VD 0.8 %
I-P-0191 | I | Modular / portable power | Motor 7 of 10, 30 kW |  | PCM: power control module | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 40 | 52 |  |  |  |  | VD 0.8 %
I-P-0192 | I | Modular / portable power | Motor 8 of 10, 30 kW |  | PCM: power control module | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 40 | 52 |  |  |  |  | VD 0.8 %
I-P-0193 | I | Modular / portable power | Motor 9 of 10, 30 kW |  | PCM: power control module | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 40 | 52 |  |  |  |  | VD 0.8 %
I-P-0194 | I | Modular / portable power | Motor 10 of 10, 30 kW |  | PCM: power control module | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 40 | 52 |  |  |  |  | VD 0.8 %
I-P-0195 | I | Modular / portable power | Motor 1 of 2, 30 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | SC-2 SCR / CO catalyst | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 30 | 42.5 | HV duct bank | 4341 | 60 |  |  |  |  | VD 2.7 %
I-P-0196 | I | Modular / portable power | Motor 2 of 2, 30 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | SC-2 SCR / CO catalyst | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 30 | 42.5 | HV duct bank | 4341 | 60 |  |  |  |  | VD 2.7 %
I-P-0197 | I | Modular / portable power | Motor 1 of 4, 15 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | SC-2 lube-oil fin-fan cooler | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦3/0 | 3/C+G | 3/0 | 1 | 1 | 480 | 15 | 21.2 | HV duct bank | 4329 | 95 |  |  |  |  | VD 2.9 %
I-P-0198 | I | Modular / portable power | Motor 2 of 4, 15 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | SC-2 lube-oil fin-fan cooler | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦3/0 | 3/C+G | 3/0 | 1 | 1 | 480 | 15 | 21.2 | HV duct bank | 4329 | 95 |  |  |  |  | VD 2.9 %
I-P-0199 | I | Modular / portable power | Motor 3 of 4, 15 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | SC-2 lube-oil fin-fan cooler | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦3/0 | 3/C+G | 3/0 | 1 | 1 | 480 | 15 | 21.2 | HV duct bank | 4329 | 95 |  |  |  |  | VD 2.9 %
I-P-0200 | I | Modular / portable power | Motor 4 of 4, 15 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | SC-2 lube-oil fin-fan cooler | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦3/0 | 3/C+G | 3/0 | 1 | 1 | 480 | 15 | 21.2 | HV duct bank | 4329 | 95 |  |  |  |  | VD 2.9 %
I-P-0201 | I | Modular / portable power | Area / platform lighting circuit 1 (4 fixtures) |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | SC-2 stack (80 ft) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 3 | 5 | HV duct bank | 4641 | 80 |  |  |  |  | fixture-to-fixture run included
I-P-0202 | I | Modular / portable power | Motor 1 of 10, 30 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 30 | 42.5 | HV duct bank | 4441 | 40 |  |  |  |  | VD 2.8 %
I-P-0203 | I | Modular / portable power | Motor 2 of 10, 30 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 30 | 42.5 | HV duct bank | 4441 | 40 |  |  |  |  | VD 2.8 %
I-P-0204 | I | Modular / portable power | Motor 3 of 10, 30 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 30 | 42.5 | HV duct bank | 4441 | 40 |  |  |  |  | VD 2.8 %
I-P-0205 | I | Modular / portable power | Motor 4 of 10, 30 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 30 | 42.5 | HV duct bank | 4441 | 40 |  |  |  |  | VD 2.8 %
I-P-0206 | I | Modular / portable power | Motor 5 of 10, 30 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 30 | 42.5 | HV duct bank | 4441 | 40 |  |  |  |  | VD 2.8 %
I-P-0207 | I | Modular / portable power | Motor 6 of 10, 30 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 30 | 42.5 | HV duct bank | 4441 | 40 |  |  |  |  | VD 2.8 %
I-P-0208 | I | Modular / portable power | Motor 7 of 10, 30 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 30 | 42.5 | HV duct bank | 4441 | 40 |  |  |  |  | VD 2.8 %
I-P-0209 | I | Modular / portable power | Motor 8 of 10, 30 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 30 | 42.5 | HV duct bank | 4441 | 40 |  |  |  |  | VD 2.8 %
I-P-0210 | I | Modular / portable power | Motor 9 of 10, 30 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 30 | 42.5 | HV duct bank | 4441 | 40 |  |  |  |  | VD 2.8 %
I-P-0211 | I | Modular / portable power | Motor 10 of 10, 30 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 30 | 42.5 | HV duct bank | 4441 | 40 |  |  |  |  | VD 2.8 %
I-P-0212 | I | Modular / portable power | Motor 1 of 6, 2 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | T-MOD 230 kV take-off gantry with arresters | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 386 | 130 |  |  |  |  | VD 0.7 %
I-P-0213 | I | Modular / portable power | Motor 2 of 6, 2 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | T-MOD 230 kV take-off gantry with arresters | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 386 | 130 |  |  |  |  | VD 0.7 %
I-P-0214 | I | Modular / portable power | Motor 3 of 6, 2 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | T-MOD 230 kV take-off gantry with arresters | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 386 | 130 |  |  |  |  | VD 0.7 %
I-P-0215 | I | Modular / portable power | Motor 4 of 6, 2 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | T-MOD 230 kV take-off gantry with arresters | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 386 | 130 |  |  |  |  | VD 0.7 %
I-P-0216 | I | Modular / portable power | Motor 5 of 6, 2 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | T-MOD 230 kV take-off gantry with arresters | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 386 | 130 |  |  |  |  | VD 0.7 %
I-P-0217 | I | Modular / portable power | Motor 6 of 6, 2 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | T-MOD 230 kV take-off gantry with arresters | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 386 | 130 |  |  |  |  | VD 0.7 %
I-P-0218 | I | Modular / portable power | Motor 1 of 6, 2 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | T-MOD-1 / T-MOD-2 firewall | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 378 | 132 |  |  |  |  | VD 0.7 %
I-P-0219 | I | Modular / portable power | Motor 2 of 6, 2 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | T-MOD-1 / T-MOD-2 firewall | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 378 | 132 |  |  |  |  | VD 0.7 %
I-P-0220 | I | Modular / portable power | Motor 3 of 6, 2 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | T-MOD-1 / T-MOD-2 firewall | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 378 | 132 |  |  |  |  | VD 0.7 %
I-P-0221 | I | Modular / portable power | Motor 4 of 6, 2 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | T-MOD-1 / T-MOD-2 firewall | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 378 | 132 |  |  |  |  | VD 0.7 %
I-P-0222 | I | Modular / portable power | Motor 5 of 6, 2 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | T-MOD-1 / T-MOD-2 firewall | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 378 | 132 |  |  |  |  | VD 0.7 %
I-P-0223 | I | Modular / portable power | Motor 6 of 6, 2 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | T-MOD-1 / T-MOD-2 firewall | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 378 | 132 |  |  |  |  | VD 0.7 %
I-P-0224 | I | Modular / portable power | Motor 1 of 6, 2 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | T-MOD-1 | T-MOD-1: 13.8/230 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 378 | 84 |  |  |  |  | VD 0.6 %
I-P-0225 | I | Modular / portable power | Motor 2 of 6, 2 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | T-MOD-1 | T-MOD-1: 13.8/230 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 378 | 84 |  |  |  |  | VD 0.6 %
I-P-0226 | I | Modular / portable power | Motor 3 of 6, 2 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | T-MOD-1 | T-MOD-1: 13.8/230 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 378 | 84 |  |  |  |  | VD 0.6 %
I-P-0227 | I | Modular / portable power | Motor 4 of 6, 2 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | T-MOD-1 | T-MOD-1: 13.8/230 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 378 | 84 |  |  |  |  | VD 0.6 %
I-P-0228 | I | Modular / portable power | Motor 5 of 6, 2 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | T-MOD-1 | T-MOD-1: 13.8/230 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 378 | 84 |  |  |  |  | VD 0.6 %
I-P-0229 | I | Modular / portable power | Motor 6 of 6, 2 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | T-MOD-1 | T-MOD-1: 13.8/230 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Duct bank | 378 | 84 |  |  |  |  | VD 0.6 %
I-P-0230 | I | Modular / portable power | Motor 1 of 6, 2 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | T-MOD-2 | T-MOD-2: 13.8/230 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 0 | 189 |  |  |  |  | VD 0.3 %
I-P-0231 | I | Modular / portable power | Motor 2 of 6, 2 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | T-MOD-2 | T-MOD-2: 13.8/230 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 0 | 189 |  |  |  |  | VD 0.3 %
I-P-0232 | I | Modular / portable power | Motor 3 of 6, 2 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | T-MOD-2 | T-MOD-2: 13.8/230 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 0 | 189 |  |  |  |  | VD 0.3 %
I-P-0233 | I | Modular / portable power | Motor 4 of 6, 2 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | T-MOD-2 | T-MOD-2: 13.8/230 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 0 | 189 |  |  |  |  | VD 0.3 %
I-P-0234 | I | Modular / portable power | Motor 5 of 6, 2 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | T-MOD-2 | T-MOD-2: 13.8/230 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 0 | 189 |  |  |  |  | VD 0.3 %
I-P-0235 | I | Modular / portable power | Motor 6 of 6, 2 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | T-MOD-2 | T-MOD-2: 13.8/230 kV | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 2 | 2.8 | Tray | 0 | 189 |  |  |  |  | VD 0.3 %
I-P-0236 | I | Modular / portable power | Motor 1 of 6, 22 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | TM-1 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4/0 | 3/C+G | 4/0 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 3194 | 70 |  |  |  |  | VD 2.5 %
I-P-0237 | I | Modular / portable power | Motor 2 of 6, 22 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | TM-1 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4/0 | 3/C+G | 4/0 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 3194 | 70 |  |  |  |  | VD 2.5 %
I-P-0238 | I | Modular / portable power | Motor 3 of 6, 22 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | TM-1 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4/0 | 3/C+G | 4/0 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 3194 | 70 |  |  |  |  | VD 2.5 %
I-P-0239 | I | Modular / portable power | Motor 4 of 6, 22 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | TM-1 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4/0 | 3/C+G | 4/0 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 3194 | 70 |  |  |  |  | VD 2.5 %
I-P-0240 | I | Modular / portable power | Motor 5 of 6, 22 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | TM-1 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4/0 | 3/C+G | 4/0 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 3194 | 70 |  |  |  |  | VD 2.5 %
I-P-0241 | I | Modular / portable power | Motor 6 of 6, 22 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | TM-1 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4/0 | 3/C+G | 4/0 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 3194 | 70 |  |  |  |  | VD 2.5 %
I-P-0242 | I | Modular / portable power | Motor 1 of 6, 22 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | TM-2 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4/0 | 3/C+G | 4/0 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 3194 | 76 |  |  |  |  | VD 2.5 %
I-P-0243 | I | Modular / portable power | Motor 2 of 6, 22 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | TM-2 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4/0 | 3/C+G | 4/0 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 3194 | 76 |  |  |  |  | VD 2.5 %
I-P-0244 | I | Modular / portable power | Motor 3 of 6, 22 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | TM-2 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4/0 | 3/C+G | 4/0 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 3194 | 76 |  |  |  |  | VD 2.5 %
I-P-0245 | I | Modular / portable power | Motor 4 of 6, 22 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | TM-2 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4/0 | 3/C+G | 4/0 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 3194 | 76 |  |  |  |  | VD 2.5 %
I-P-0246 | I | Modular / portable power | Motor 5 of 6, 22 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | TM-2 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4/0 | 3/C+G | 4/0 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 3194 | 76 |  |  |  |  | VD 2.5 %
I-P-0247 | I | Modular / portable power | Motor 6 of 6, 22 kW |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | TM-2 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦4/0 | 3/C+G | 4/0 | 1 | 1 | 480 | 22 | 31.1 | Duct bank | 3194 | 76 |  |  |  |  | VD 2.5 %
I-P-0248 | I | Modular / portable power | LV power feeder |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | Water-injection skid | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦3/0 | 3/C+G | 3/0 | 1 | 1 | 480 | 15 | 21.2 | HV duct bank | 4262 | 89 |  |  |  |  | VD 2.8 %
I-MV-0001 | I | Modular / portable power | Modular-yard fuel-gas compressor | MOD-EH | MOD-EH: 13.8 kV modular collector e-house |  | Fuel-gas compressors 3 x 100% electric | MV 15 kV | ARMOR-X MC-HL / MV-105 15 kV 3/C Cu, EPR 133%, tape shield, gnd, CWA, red PVC | MV15AX¦3/C¦2 | 3/C | 2 | 1 | 1 | 13800 | 1500 | 70 | HV duct bank | 4010 | 38
I-MV-0002 | I | Modular / portable power | Modular-yard fuel-gas compressor | MOD-EH | MOD-EH: 13.8 kV modular collector e-house |  | Fuel-gas compressors 3 x 100% electric | MV 15 kV | ARMOR-X MC-HL / MV-105 15 kV 3/C Cu, EPR 133%, tape shield, gnd, CWA, red PVC | MV15AX¦3/C¦2 | 3/C | 2 | 1 | 1 | 13800 | 1500 | 70 | HV duct bank | 4010 | 38
I-MV-0003 | I | Modular / portable power | Modular-yard fuel-gas compressor | MOD-EH | MOD-EH: 13.8 kV modular collector e-house |  | Fuel-gas compressors 3 x 100% electric | MV 15 kV | ARMOR-X MC-HL / MV-105 15 kV 3/C Cu, EPR 133%, tape shield, gnd, CWA, red PVC | MV15AX¦3/C¦2 | 3/C | 2 | 1 | 1 | 13800 | 1500 | 70 | HV duct bank | 4010 | 38
I-MV-0004 | I | Modular / portable power | SC-1 PCM to MOD-EH |  | SC-1 PCM + 15 kV GCB | MOD-EH | MOD-EH: 13.8 kV modular collector e-house | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦750 | 1/C | 750 kcmil | 5 | 3 | 13800 | 50000 | 2092 | Duct bank | 390 | 32
I-MV-0005 | I | Modular / portable power | SC-2 PCM to MOD-EH |  | SC-2 PCM + 15 kV GCB | MOD-EH | MOD-EH: 13.8 kV modular collector e-house | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦750 | 1/C | 750 kcmil | 5 | 3 | 13800 | 50000 | 2092 | HV duct bank | 4028 | 38
I-MV-0006 | I | Modular / portable power | MOD-LV step-up to MOD-EH |  | MOD-LV 480 V board + 480 V : 13.8 kV step-up | MOD-EH | MOD-EH: 13.8 kV modular collector e-house | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦500 | 1/C | 500 kcmil | 1 | 3 | 13800 | 7500 | 314 | Duct bank | 368 | 34
I-MV-0007 | I | Modular / portable power | CONT-3 13.8 kV to PAD-EH (extension section, ground tray) | CONT-3 | CONT-3: containerized gas genset 13.8 kV (40 ft) | PAD-EH | PAD-EH 13.8 kV switchgear e-house | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦2 | 1/C | 2 | 1 | 3 | 13800 | 2000 | 93 | Surface | 191 | 32
I-MV-0008 | I | Modular / portable power | CONT-4 13.8 kV to PAD-EH (extension section, ground tray) | CONT-4 | CONT-4: containerized gas genset 13.8 kV (40 ft) | PAD-EH | PAD-EH 13.8 kV switchgear e-house | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦2 | 1/C | 2 | 1 | 3 | 13800 | 2000 | 93 | Surface | 71 | 72
I-MV-0009 | I | Modular / portable power | CONT-5 13.8 kV to PAD-EH (extension section, ground tray) | CONT-5 | CONT-5: containerized gas genset 13.8 kV (40 ft) | PAD-EH | PAD-EH 13.8 kV switchgear e-house | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦2 | 1/C | 2 | 1 | 3 | 13800 | 2000 | 93 | Duct bank | 47 | 36
I-MV-0010 | I | Modular / portable power | CONT-6 13.8 kV to PAD-EH (extension section, ground tray) | CONT-6 | CONT-6: containerized gas genset 13.8 kV (40 ft) | PAD-EH | PAD-EH 13.8 kV switchgear e-house | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦2 | 1/C | 2 | 1 | 3 | 13800 | 2000 | 93 | Surface | 242 | 32
I-MV-0011 | I | Modular / portable power | CONT-7 13.8 kV to PAD-EH (extension section, ground tray) | CONT-7 | CONT-7: containerized gas genset 13.8 kV (40 ft) | PAD-EH | PAD-EH 13.8 kV switchgear e-house | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦2 | 1/C | 2 | 1 | 3 | 13800 | 2000 | 93 | Surface | 228 | 46
I-MV-0012 | I | Modular / portable power | CONT-8 13.8 kV to PAD-EH (extension section, ground tray) | CONT-8 | CONT-8: containerized gas genset 13.8 kV (40 ft) | PAD-EH | PAD-EH 13.8 kV switchgear e-house | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦2 | 1/C | 2 | 1 | 3 | 13800 | 2000 | 93 | Surface | 97 | 36
I-MV-0013 | I | Modular / portable power | TM-1 (TM2500) generator leads to PAD-EH | TM-1 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | PAD-EH | PAD-EH 13.8 kV switchgear e-house | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦1000 | 1/C | 1000 kcmil | 3 | 3 | 13800 | 35000 | 1464 | Surface | 405 | 27 |  |  |  |  | 3 per phase for 125 % (the model shows 2 per phase: update the model)
I-MV-0014 | I | Modular / portable power | TM-2 (TM2500) generator leads to PAD-EH | TM-2 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | PAD-EH | PAD-EH 13.8 kV switchgear e-house | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦1000 | 1/C | 1000 kcmil | 3 | 3 | 13800 | 35000 | 1464 | Surface | 411 | 27 |  |  |  |  | 3 per phase for 125 % (the model shows 2 per phase: update the model)
I-MV-0015 | I | Modular / portable power | RICE-1 generator leads to the PCM | RICE-1 | RICE engine-generator 1 |  | PCM: power control module | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦750 | 1/C | 750 kcmil | 2 | 3 | 13800 | 18400 | 770 | Duct bank | 576 | 111 |  |  |  |  | 18V50 class ~18 MW (typ.)
I-MV-0016 | I | Modular / portable power | RICE-2 generator leads to the PCM | RICE-2 | RICE engine-generator 2 |  | PCM: power control module | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦750 | 1/C | 750 kcmil | 2 | 3 | 13800 | 18400 | 770 | Duct bank | 550 | 109 |  |  |  |  | 18V50 class ~18 MW (typ.)
I-MV-0017 | I | Modular / portable power | RICE-3 generator leads to the PCM | RICE-3 | RICE engine-generator 3 |  | PCM: power control module | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦750 | 1/C | 750 kcmil | 2 | 3 | 13800 | 18400 | 770 | Duct bank | 550 | 81 |  |  |  |  | 18V50 class ~18 MW (typ.)
I-MV-0018 | I | Modular / portable power | RICE-4 generator leads to the PCM | RICE-4 | RICE engine-generator 4 |  | PCM: power control module | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦750 | 1/C | 750 kcmil | 2 | 3 | 13800 | 18400 | 770 | Duct bank | 550 | 53 |  |  |  |  | 18V50 class ~18 MW (typ.)
I-MV-0019 | I | Modular / portable power | RICE-5 generator leads to the PCM | RICE-5 | RICE engine-generator 5 |  | PCM: power control module | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦750 | 1/C | 750 kcmil | 2 | 3 | 13800 | 18400 | 770 | Duct bank | 525 | 50 |  |  |  |  | 18V50 class ~18 MW (typ.)
I-MV-0020 | I | Modular / portable power | RICE-6 generator leads to the PCM | RICE-6 | RICE engine-generator 6 |  | PCM: power control module | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦750 | 1/C | 750 kcmil | 2 | 3 | 13800 | 18400 | 770 | Duct bank | 469 | 78 |  |  |  |  | 18V50 class ~18 MW (typ.)
I-MV-0021 | I | Modular / portable power | RICE-7 generator leads to the PCM | RICE-7 | RICE engine-generator 7 |  | PCM: power control module | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦750 | 1/C | 750 kcmil | 2 | 3 | 13800 | 18400 | 770 | Tray | 83 | 106 |  |  |  |  | 18V50 class ~18 MW (typ.)
I-MV-0022 | I | Modular / portable power | RICE-8 generator leads to the PCM | RICE-8 | RICE engine-generator 8 |  | PCM: power control module | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦750 | 1/C | 750 kcmil | 2 | 3 | 13800 | 18400 | 770 | Tray | 37 | 124 |  |  |  |  | 18V50 class ~18 MW (typ.)
I-MV-0023 | I | Modular / portable power | SC-1 (LM6000 class) generator leads to its PCM / GCB | SC-1 | SC-1: aeroderivative simple-cycle unit (LM6000 class) |  | SC-1 PCM + 15 kV GCB | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦750 | 1/C | 750 kcmil | 5 | 3 | 13800 | 50000 | 2092 | Tray | 12 | 52
I-MV-0024 | I | Modular / portable power | SC-2 (LM6000 class) generator leads to its PCM / GCB | SC-2 | SC-2: aeroderivative simple-cycle unit (LM6000 class) |  | SC-2 PCM + 15 kV GCB | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦750 | 1/C | 750 kcmil | 5 | 3 | 13800 | 50000 | 2092 | Tray | 0 | 62
I-PP-0001 | I | Modular / portable power | GEN-E 480 V to PAD-LV (Type W sets, cam-lock) | GEN-E | GEN-E: enclosed industrial gas genset 2 MW | PAD-LV | PAD-LV 480 V paralleling switchboard | Portable LV | Type W 2 kV 1/C Cu, EPDM / CPE (portable, cam-lock) | W¦1/C¦4/0 | 1/C | 4/0 | 8 | 4 | 480 | 2000 | 2406 | Surface | 143 | 27 |  |  |  |  | 4 x 1/C per set incl. ground
I-PP-0002 | I | Modular / portable power | GEN-O 480 V to PAD-LV (Type W sets, cam-lock) | GEN-O | GEN-O: open engine-generator skid | PAD-LV | PAD-LV 480 V paralleling switchboard | Portable LV | Type W 2 kV 1/C Cu, EPDM / CPE (portable, cam-lock) | W¦1/C¦4/0 | 1/C | 4/0 | 4 | 4 | 480 | 1000 | 1203 | Surface | 132 | 27 |  |  |  |  | 4 x 1/C per set incl. ground
I-PP-0003 | I | Modular / portable power | CONT-1 13.8 kV leads to GSP-1 | CONT-1 | CONT-1: containerized genset 13.8 kV (40 ft) | GSP-1 | GSP-1: generator breaker / protection | Portable MV | Type SHD-GC 15 kV 3/C Cu, 2 grounds + GC, yellow CPE (portable) | SHD¦3/C¦2 | 3/C | 2 | 1 | 1 | 13800 | 2000 | 93 | Tray | 0 | 29 |  |  |  |  | portable, on grade
I-PP-0004 | I | Modular / portable power | CONT-2 13.8 kV leads to GSP-2 | CONT-2 | CONT-2: containerized genset 13.8 kV (40 ft) | GSP-2 | GSP-2: generator breaker / protection | Portable MV | Type SHD-GC 15 kV 3/C Cu, 2 grounds + GC, yellow CPE (portable) | SHD¦3/C¦2 | 3/C | 2 | 1 | 1 | 13800 | 2000 | 93 | Riser | 2 | 27 |  |  |  |  | portable, on grade
I-PP-0005 | I | Modular / portable power | PIC to commissioning load bank | PIC | PIC: portable input cabinet | LB | LB: commissioning load bank (trailer) | Portable MV | Type SHD-GC 15 kV 3/C Cu, 2 grounds + GC, yellow CPE (portable) | SHD¦3/C¦2 | 3/C | 2 | 1 | 1 | 13800 | 2000 | 93 | Surface | 27 | 39 |  |  |  |  | portable
I-PP-0006 | I | Modular / portable power | GSP-1 to PAD-EH | GSP-1 | GSP-1: generator breaker / protection | PAD-EH | PAD-EH 13.8 kV switchgear e-house | Portable MV | Type SHD-GC 15 kV 3/C Cu, 2 grounds + GC, yellow CPE (portable) | SHD¦3/C¦2 | 3/C | 2 | 1 | 1 | 13800 | 2000 | 93 | Surface | 298 | 37 |  |  |  |  | portable, on grade
I-PP-0007 | I | Modular / portable power | GSP-2 to PAD-EH | GSP-2 | GSP-2: generator breaker / protection | PAD-EH | PAD-EH 13.8 kV switchgear e-house | Portable MV | Type SHD-GC 15 kV 3/C Cu, 2 grounds + GC, yellow CPE (portable) | SHD¦3/C¦2 | 3/C | 2 | 1 | 1 | 13800 | 2000 | 93 | Surface | 269 | 37 |  |  |  |  | portable, on grade
I-PP-0008 | I | Modular / portable power | MOB-1 13.8 kV to PIC through the C-L01 ramp | MOB-1 | MOB-1: trailer genset | PIC | PIC: portable input cabinet | Portable MV | Type SHD-GC 15 kV 3/C Cu, 2 grounds + GC, yellow CPE (portable) | SHD¦3/C¦2 | 3/C | 2 | 1 | 1 | 13800 | 2000 | 93 | Surface | 162 | 27 |  |  |  |  | portable
J-C-0001 | J | GT inlet chilling | Motor 1 of 4: control / local station |  | Inlet-chilling e-house / transformer |  | CHW pumps | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 579 | 32
J-C-0002 | J | GT inlet chilling | Motor 2 of 4: control / local station |  | Inlet-chilling e-house / transformer |  | CHW pumps | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 579 | 32
J-C-0003 | J | GT inlet chilling | Motor 3 of 4: control / local station |  | Inlet-chilling e-house / transformer |  | CHW pumps | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 579 | 32
J-C-0004 | J | GT inlet chilling | Motor 4 of 4: control / local station |  | Inlet-chilling e-house / transformer |  | CHW pumps | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 579 | 32
J-C-0005 | J | GT inlet chilling | Motor 1 of 6: control / local station |  | Inlet-chilling e-house / transformer |  | Chillers x6 (water-cooled) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 10 | 32
J-C-0006 | J | GT inlet chilling | Motor 2 of 6: control / local station |  | Inlet-chilling e-house / transformer |  | Chillers x6 (water-cooled) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 10 | 32
J-C-0007 | J | GT inlet chilling | Motor 3 of 6: control / local station |  | Inlet-chilling e-house / transformer |  | Chillers x6 (water-cooled) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 10 | 32
J-C-0008 | J | GT inlet chilling | Motor 4 of 6: control / local station |  | Inlet-chilling e-house / transformer |  | Chillers x6 (water-cooled) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 10 | 32
J-C-0009 | J | GT inlet chilling | Motor 5 of 6: control / local station |  | Inlet-chilling e-house / transformer |  | Chillers x6 (water-cooled) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 10 | 32
J-C-0010 | J | GT inlet chilling | Motor 6 of 6: control / local station |  | Inlet-chilling e-house / transformer |  | Chillers x6 (water-cooled) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 10 | 32
J-C-0011 | J | GT inlet chilling | Control |  | Inlet-chilling e-house / transformer |  | Inlet-chilling e-house / transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 32
J-C-0012 | J | GT inlet chilling | Control |  | Inlet-chilling e-house / transformer |  | Inlet-chilling e-house / transformer | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 32
J-C-0013 | J | GT inlet chilling | CT / VT |  | Inlet-chilling e-house / transformer |  | Inlet-chilling e-house / transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 0 | 32
J-C-0014 | J | GT inlet chilling | CT / VT |  | Inlet-chilling e-house / transformer |  | Inlet-chilling e-house / transformer | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Tray | 0 | 32
J-C-0015 | J | GT inlet chilling | Motor 1 of 12: control / local station |  | Inlet-chilling e-house / transformer |  | Inlet-chilling tower (12 cells): chiller heat rejection | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 478 | 38
J-C-0016 | J | GT inlet chilling | Motor 2 of 12: control / local station |  | Inlet-chilling e-house / transformer |  | Inlet-chilling tower (12 cells): chiller heat rejection | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 478 | 38
J-C-0017 | J | GT inlet chilling | Motor 3 of 12: control / local station |  | Inlet-chilling e-house / transformer |  | Inlet-chilling tower (12 cells): chiller heat rejection | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 478 | 38
J-C-0018 | J | GT inlet chilling | Motor 4 of 12: control / local station |  | Inlet-chilling e-house / transformer |  | Inlet-chilling tower (12 cells): chiller heat rejection | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 478 | 38
J-C-0019 | J | GT inlet chilling | Motor 5 of 12: control / local station |  | Inlet-chilling e-house / transformer |  | Inlet-chilling tower (12 cells): chiller heat rejection | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 478 | 38
J-C-0020 | J | GT inlet chilling | Motor 6 of 12: control / local station |  | Inlet-chilling e-house / transformer |  | Inlet-chilling tower (12 cells): chiller heat rejection | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 478 | 38
J-C-0021 | J | GT inlet chilling | Motor 7 of 12: control / local station |  | Inlet-chilling e-house / transformer |  | Inlet-chilling tower (12 cells): chiller heat rejection | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 478 | 38
J-C-0022 | J | GT inlet chilling | Motor 8 of 12: control / local station |  | Inlet-chilling e-house / transformer |  | Inlet-chilling tower (12 cells): chiller heat rejection | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 478 | 38
J-C-0023 | J | GT inlet chilling | Motor 9 of 12: control / local station |  | Inlet-chilling e-house / transformer |  | Inlet-chilling tower (12 cells): chiller heat rejection | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 478 | 38
J-C-0024 | J | GT inlet chilling | Motor 10 of 12: control / local station |  | Inlet-chilling e-house / transformer |  | Inlet-chilling tower (12 cells): chiller heat rejection | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 478 | 38
J-C-0025 | J | GT inlet chilling | Motor 11 of 12: control / local station |  | Inlet-chilling e-house / transformer |  | Inlet-chilling tower (12 cells): chiller heat rejection | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 478 | 38
J-C-0026 | J | GT inlet chilling | Motor 12 of 12: control / local station |  | Inlet-chilling e-house / transformer |  | Inlet-chilling tower (12 cells): chiller heat rejection | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 478 | 38
J-I-0001 | J | GT inlet chilling | Analog instrument to JB JB-CHW pumps-AI01: 12 x 1 pr (field cables) |  | CHW pumps | JB-CHW pumps-AI01 | CHW pumps | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 92 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
J-I-0002 | J | GT inlet chilling | Home run JB-CHW pumps-AI01 to the control / marshalling room |  | Inlet-chilling e-house / transformer | JB-CHW pumps-AI01 | CHW pumps | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 579 | 32
J-I-0003 | J | GT inlet chilling | Discrete device to JB JB-CHW pumps-DI01: 12 x 1 pr (field cables) |  | CHW pumps | JB-CHW pumps-DI01 | CHW pumps | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 92 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
J-I-0004 | J | GT inlet chilling | Home run JB-CHW pumps-DI01 to the control / marshalling room |  | Inlet-chilling e-house / transformer | JB-CHW pumps-DI01 | CHW pumps | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 579 | 32
J-I-0005 | J | GT inlet chilling | Analog instrument to JB JB-CONDITIONAL: TES c-AI01: 4 x 1 pr (field cables) |  | CONDITIONAL: TES chilled-water tank | JB-CONDITIONAL: TES c-AI01 | CONDITIONAL: TES chilled-water tank | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 91 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
J-I-0006 | J | GT inlet chilling | Home run JB-CONDITIONAL: TES c-AI01 to the control / marshalling room |  | Inlet-chilling e-house / transformer | JB-CONDITIONAL: TES c-AI01 | CONDITIONAL: TES chilled-water tank | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 271 | 217
J-I-0007 | J | GT inlet chilling | Discrete device to JB JB-CONDITIONAL: TES c-DI01: 4 x 1 pr (field cables) |  | CONDITIONAL: TES chilled-water tank | JB-CONDITIONAL: TES c-DI01 | CONDITIONAL: TES chilled-water tank | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 91 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
J-I-0008 | J | GT inlet chilling | Home run JB-CONDITIONAL: TES c-DI01 to the control / marshalling room |  | Inlet-chilling e-house / transformer | JB-CONDITIONAL: TES c-DI01 | CONDITIONAL: TES chilled-water tank | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 271 | 217
J-I-0009 | J | GT inlet chilling | Analog instrument to JB JB-CW pumps (inlet ch-AI01: 20 x 1 pr (field cables) |  | CW pumps (inlet chilling) | JB-CW pumps (inlet ch-AI01 | CW pumps (inlet chilling) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 92 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
J-I-0010 | J | GT inlet chilling | Home run JB-CW pumps (inlet ch-AI01 to the control / marshalling room |  | Inlet-chilling e-house / transformer | JB-CW pumps (inlet ch-AI01 | CW pumps (inlet chilling) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 70
J-I-0011 | J | GT inlet chilling | Analog instrument to JB JB-CW pumps (inlet ch-AI02: 4 x 1 pr (field cables) |  | CW pumps (inlet chilling) | JB-CW pumps (inlet ch-AI02 | CW pumps (inlet chilling) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 92 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
J-I-0012 | J | GT inlet chilling | Home run JB-CW pumps (inlet ch-AI02 to the control / marshalling room |  | Inlet-chilling e-house / transformer | JB-CW pumps (inlet ch-AI02 | CW pumps (inlet chilling) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 70
J-I-0013 | J | GT inlet chilling | Discrete device to JB JB-CW pumps (inlet ch-DI01: 20 x 1 pr (field cables) |  | CW pumps (inlet chilling) | JB-CW pumps (inlet ch-DI01 | CW pumps (inlet chilling) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 92 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
J-I-0014 | J | GT inlet chilling | Home run JB-CW pumps (inlet ch-DI01 to the control / marshalling room |  | Inlet-chilling e-house / transformer | JB-CW pumps (inlet ch-DI01 | CW pumps (inlet chilling) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 70
J-I-0015 | J | GT inlet chilling | Discrete device to JB JB-CW pumps (inlet ch-DI02: 4 x 1 pr (field cables) |  | CW pumps (inlet chilling) | JB-CW pumps (inlet ch-DI02 | CW pumps (inlet chilling) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 92 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
J-I-0016 | J | GT inlet chilling | Home run JB-CW pumps (inlet ch-DI02 to the control / marshalling room |  | Inlet-chilling e-house / transformer | JB-CW pumps (inlet ch-DI02 | CW pumps (inlet chilling) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 70
J-I-0017 | J | GT inlet chilling | Analog instrument to JB JB-Chillers x6 (water-AI01: 20 x 1 pr (field cables) |  | Chillers x6 (water-cooled) | JB-Chillers x6 (water-AI01 | Chillers x6 (water-cooled) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 190 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
J-I-0018 | J | GT inlet chilling | Home run JB-Chillers x6 (water-AI01 to the control / marshalling room |  | Inlet-chilling e-house / transformer | JB-Chillers x6 (water-AI01 | Chillers x6 (water-cooled) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 10 | 32
J-I-0019 | J | GT inlet chilling | Analog instrument to JB JB-Chillers x6 (water-AI02: 20 x 1 pr (field cables) |  | Chillers x6 (water-cooled) | JB-Chillers x6 (water-AI02 | Chillers x6 (water-cooled) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 190 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
J-I-0020 | J | GT inlet chilling | Home run JB-Chillers x6 (water-AI02 to the control / marshalling room |  | Inlet-chilling e-house / transformer | JB-Chillers x6 (water-AI02 | Chillers x6 (water-cooled) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 10 | 32
J-I-0021 | J | GT inlet chilling | Analog instrument to JB JB-Chillers x6 (water-AI03: 20 x 1 pr (field cables) |  | Chillers x6 (water-cooled) | JB-Chillers x6 (water-AI03 | Chillers x6 (water-cooled) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 190 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
J-I-0022 | J | GT inlet chilling | Home run JB-Chillers x6 (water-AI03 to the control / marshalling room |  | Inlet-chilling e-house / transformer | JB-Chillers x6 (water-AI03 | Chillers x6 (water-cooled) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 10 | 32
J-I-0023 | J | GT inlet chilling | Analog instrument to JB JB-Chillers x6 (water-AI04: 20 x 1 pr (field cables) |  | Chillers x6 (water-cooled) | JB-Chillers x6 (water-AI04 | Chillers x6 (water-cooled) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 190 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
J-I-0024 | J | GT inlet chilling | Home run JB-Chillers x6 (water-AI04 to the control / marshalling room |  | Inlet-chilling e-house / transformer | JB-Chillers x6 (water-AI04 | Chillers x6 (water-cooled) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 10 | 32
J-I-0025 | J | GT inlet chilling | Analog instrument to JB JB-Chillers x6 (water-AI05: 20 x 1 pr (field cables) |  | Chillers x6 (water-cooled) | JB-Chillers x6 (water-AI05 | Chillers x6 (water-cooled) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 190 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
J-I-0026 | J | GT inlet chilling | Home run JB-Chillers x6 (water-AI05 to the control / marshalling room |  | Inlet-chilling e-house / transformer | JB-Chillers x6 (water-AI05 | Chillers x6 (water-cooled) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 10 | 32
J-I-0027 | J | GT inlet chilling | Analog instrument to JB JB-Chillers x6 (water-AI06: 20 x 1 pr (field cables) |  | Chillers x6 (water-cooled) | JB-Chillers x6 (water-AI06 | Chillers x6 (water-cooled) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 190 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
J-I-0028 | J | GT inlet chilling | Home run JB-Chillers x6 (water-AI06 to the control / marshalling room |  | Inlet-chilling e-house / transformer | JB-Chillers x6 (water-AI06 | Chillers x6 (water-cooled) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 10 | 32
J-I-0029 | J | GT inlet chilling | Discrete device to JB JB-Chillers x6 (water-DI01: 20 x 1 pr (field cables) |  | Chillers x6 (water-cooled) | JB-Chillers x6 (water-DI01 | Chillers x6 (water-cooled) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 190 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
J-I-0030 | J | GT inlet chilling | Home run JB-Chillers x6 (water-DI01 to the control / marshalling room |  | Inlet-chilling e-house / transformer | JB-Chillers x6 (water-DI01 | Chillers x6 (water-cooled) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 10 | 32
J-I-0031 | J | GT inlet chilling | Discrete device to JB JB-Chillers x6 (water-DI02: 20 x 1 pr (field cables) |  | Chillers x6 (water-cooled) | JB-Chillers x6 (water-DI02 | Chillers x6 (water-cooled) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 190 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
J-I-0032 | J | GT inlet chilling | Home run JB-Chillers x6 (water-DI02 to the control / marshalling room |  | Inlet-chilling e-house / transformer | JB-Chillers x6 (water-DI02 | Chillers x6 (water-cooled) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 10 | 32
J-I-0033 | J | GT inlet chilling | Discrete device to JB JB-Chillers x6 (water-DI03: 20 x 1 pr (field cables) |  | Chillers x6 (water-cooled) | JB-Chillers x6 (water-DI03 | Chillers x6 (water-cooled) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 190 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
J-I-0034 | J | GT inlet chilling | Home run JB-Chillers x6 (water-DI03 to the control / marshalling room |  | Inlet-chilling e-house / transformer | JB-Chillers x6 (water-DI03 | Chillers x6 (water-cooled) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 10 | 32
J-I-0035 | J | GT inlet chilling | Discrete device to JB JB-Chillers x6 (water-DI04: 20 x 1 pr (field cables) |  | Chillers x6 (water-cooled) | JB-Chillers x6 (water-DI04 | Chillers x6 (water-cooled) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 190 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
J-I-0036 | J | GT inlet chilling | Home run JB-Chillers x6 (water-DI04 to the control / marshalling room |  | Inlet-chilling e-house / transformer | JB-Chillers x6 (water-DI04 | Chillers x6 (water-cooled) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 10 | 32
J-I-0037 | J | GT inlet chilling | Discrete device to JB JB-Chillers x6 (water-DI05: 20 x 1 pr (field cables) |  | Chillers x6 (water-cooled) | JB-Chillers x6 (water-DI05 | Chillers x6 (water-cooled) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 190 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
J-I-0038 | J | GT inlet chilling | Home run JB-Chillers x6 (water-DI05 to the control / marshalling room |  | Inlet-chilling e-house / transformer | JB-Chillers x6 (water-DI05 | Chillers x6 (water-cooled) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 10 | 32
J-I-0039 | J | GT inlet chilling | Discrete device to JB JB-Chillers x6 (water-DI06: 20 x 1 pr (field cables) |  | Chillers x6 (water-cooled) | JB-Chillers x6 (water-DI06 | Chillers x6 (water-cooled) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 190 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
J-I-0040 | J | GT inlet chilling | Home run JB-Chillers x6 (water-DI06 to the control / marshalling room |  | Inlet-chilling e-house / transformer | JB-Chillers x6 (water-DI06 | Chillers x6 (water-cooled) | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 10 | 32
J-I-0041 | J | GT inlet chilling | Instrumentation |  | Inlet-chilling e-house / transformer |  | Inlet-chilling e-house / transformer | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 32
J-I-0042 | J | GT inlet chilling | Analog instrument to JB JB-Inlet-chilling tow-AI01: 12 x 1 pr (field cables) |  | Inlet-chilling tower (12 cells): chiller heat rejection | JB-Inlet-chilling tow-AI01 | Inlet-chilling tower (12 cells): chiller heat rejection | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 205 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
J-I-0043 | J | GT inlet chilling | Home run JB-Inlet-chilling tow-AI01 to the control / marshalling room |  | Inlet-chilling e-house / transformer | JB-Inlet-chilling tow-AI01 | Inlet-chilling tower (12 cells): chiller heat rejection | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 478 | 38
J-I-0044 | J | GT inlet chilling | Discrete device to JB JB-Inlet-chilling tow-DI01: 20 x 1 pr (field cables) |  | Inlet-chilling tower (12 cells): chiller heat rejection | JB-Inlet-chilling tow-DI01 | Inlet-chilling tower (12 cells): chiller heat rejection | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 205 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
J-I-0045 | J | GT inlet chilling | Home run JB-Inlet-chilling tow-DI01 to the control / marshalling room |  | Inlet-chilling e-house / transformer | JB-Inlet-chilling tow-DI01 | Inlet-chilling tower (12 cells): chiller heat rejection | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 478 | 38
J-I-0046 | J | GT inlet chilling | Discrete device to JB JB-Inlet-chilling tow-DI02: 4 x 1 pr (field cables) |  | Inlet-chilling tower (12 cells): chiller heat rejection | JB-Inlet-chilling tow-DI02 | Inlet-chilling tower (12 cells): chiller heat rejection | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 205 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
J-I-0047 | J | GT inlet chilling | Home run JB-Inlet-chilling tow-DI02 to the control / marshalling room |  | Inlet-chilling e-house / transformer | JB-Inlet-chilling tow-DI02 | Inlet-chilling tower (12 cells): chiller heat rejection | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 478 | 38
J-P-0001 | J | GT inlet chilling | Motor 1 of 4, 150 kW |  | Inlet-chilling e-house / transformer |  | CHW pumps | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 150 | 212.3 | Duct bank | 579 | 32 |  |  |  |  | VD 1.9 %
J-P-0002 | J | GT inlet chilling | Motor 2 of 4, 150 kW |  | Inlet-chilling e-house / transformer |  | CHW pumps | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 150 | 212.3 | Duct bank | 579 | 32 |  |  |  |  | VD 1.9 %
J-P-0003 | J | GT inlet chilling | Motor 3 of 4, 150 kW |  | Inlet-chilling e-house / transformer |  | CHW pumps | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 150 | 212.3 | Duct bank | 579 | 32 |  |  |  |  | VD 1.9 %
J-P-0004 | J | GT inlet chilling | Motor 4 of 4, 150 kW |  | Inlet-chilling e-house / transformer |  | CHW pumps | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦350 | 3/C+G | 350 kcmil | 1 | 1 | 480 | 150 | 212.3 | Duct bank | 579 | 32 |  |  |  |  | VD 1.9 %
J-P-0005 | J | GT inlet chilling | LV power feeder |  | Inlet-chilling e-house / transformer |  | CONDITIONAL: TES chilled-water tank | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 10 | 14.2 | Duct bank | 271 | 217 |  |  |  |  | VD 2.1 %
J-P-0006 | J | GT inlet chilling | Motor 1 of 6, 7 kW |  | Inlet-chilling e-house / transformer |  | Chillers x6 (water-cooled) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 10 | 32 |  |  |  |  | VD 0.2 %
J-P-0007 | J | GT inlet chilling | Motor 2 of 6, 7 kW |  | Inlet-chilling e-house / transformer |  | Chillers x6 (water-cooled) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 10 | 32 |  |  |  |  | VD 0.2 %
J-P-0008 | J | GT inlet chilling | Motor 3 of 6, 7 kW |  | Inlet-chilling e-house / transformer |  | Chillers x6 (water-cooled) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 10 | 32 |  |  |  |  | VD 0.2 %
J-P-0009 | J | GT inlet chilling | Motor 4 of 6, 7 kW |  | Inlet-chilling e-house / transformer |  | Chillers x6 (water-cooled) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 10 | 32 |  |  |  |  | VD 0.2 %
J-P-0010 | J | GT inlet chilling | Motor 5 of 6, 7 kW |  | Inlet-chilling e-house / transformer |  | Chillers x6 (water-cooled) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 10 | 32 |  |  |  |  | VD 0.2 %
J-P-0011 | J | GT inlet chilling | Motor 6 of 6, 7 kW |  | Inlet-chilling e-house / transformer |  | Chillers x6 (water-cooled) | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 7 | 9.9 | Duct bank | 10 | 32 |  |  |  |  | VD 0.2 %
J-P-0012 | J | GT inlet chilling | Motor 1 of 12, 75 kW (VFD output) |  | Inlet-chilling e-house / transformer |  | Inlet-chilling tower (12 cells): chiller heat rejection | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦2/0 | 3/C+3G | 2/0 | 1 | 1 | 480 | 75 | 106 | Duct bank | 683 | 38 |  |  |  |  | VD 2.9 %
J-P-0013 | J | GT inlet chilling | Motor 2 of 12, 75 kW (VFD output) |  | Inlet-chilling e-house / transformer |  | Inlet-chilling tower (12 cells): chiller heat rejection | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦2/0 | 3/C+3G | 2/0 | 1 | 1 | 480 | 75 | 106 | Duct bank | 683 | 38 |  |  |  |  | VD 2.9 %
J-P-0014 | J | GT inlet chilling | Motor 3 of 12, 75 kW (VFD output) |  | Inlet-chilling e-house / transformer |  | Inlet-chilling tower (12 cells): chiller heat rejection | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦2/0 | 3/C+3G | 2/0 | 1 | 1 | 480 | 75 | 106 | Duct bank | 683 | 38 |  |  |  |  | VD 2.9 %
J-P-0015 | J | GT inlet chilling | Motor 4 of 12, 75 kW (VFD output) |  | Inlet-chilling e-house / transformer |  | Inlet-chilling tower (12 cells): chiller heat rejection | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦2/0 | 3/C+3G | 2/0 | 1 | 1 | 480 | 75 | 106 | Duct bank | 683 | 38 |  |  |  |  | VD 2.9 %
J-P-0016 | J | GT inlet chilling | Motor 5 of 12, 75 kW (VFD output) |  | Inlet-chilling e-house / transformer |  | Inlet-chilling tower (12 cells): chiller heat rejection | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦2/0 | 3/C+3G | 2/0 | 1 | 1 | 480 | 75 | 106 | Duct bank | 683 | 38 |  |  |  |  | VD 2.9 %
J-P-0017 | J | GT inlet chilling | Motor 6 of 12, 75 kW (VFD output) |  | Inlet-chilling e-house / transformer |  | Inlet-chilling tower (12 cells): chiller heat rejection | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦2/0 | 3/C+3G | 2/0 | 1 | 1 | 480 | 75 | 106 | Duct bank | 683 | 38 |  |  |  |  | VD 2.9 %
J-P-0018 | J | GT inlet chilling | Motor 7 of 12, 75 kW (VFD output) |  | Inlet-chilling e-house / transformer |  | Inlet-chilling tower (12 cells): chiller heat rejection | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦2/0 | 3/C+3G | 2/0 | 1 | 1 | 480 | 75 | 106 | Duct bank | 683 | 38 |  |  |  |  | VD 2.9 %
J-P-0019 | J | GT inlet chilling | Motor 8 of 12, 75 kW (VFD output) |  | Inlet-chilling e-house / transformer |  | Inlet-chilling tower (12 cells): chiller heat rejection | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦2/0 | 3/C+3G | 2/0 | 1 | 1 | 480 | 75 | 106 | Duct bank | 683 | 38 |  |  |  |  | VD 2.9 %
J-P-0020 | J | GT inlet chilling | Motor 9 of 12, 75 kW (VFD output) |  | Inlet-chilling e-house / transformer |  | Inlet-chilling tower (12 cells): chiller heat rejection | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦2/0 | 3/C+3G | 2/0 | 1 | 1 | 480 | 75 | 106 | Duct bank | 683 | 38 |  |  |  |  | VD 2.9 %
J-P-0021 | J | GT inlet chilling | Motor 10 of 12, 75 kW (VFD output) |  | Inlet-chilling e-house / transformer |  | Inlet-chilling tower (12 cells): chiller heat rejection | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦2/0 | 3/C+3G | 2/0 | 1 | 1 | 480 | 75 | 106 | Duct bank | 683 | 38 |  |  |  |  | VD 2.9 %
J-P-0022 | J | GT inlet chilling | Motor 11 of 12, 75 kW (VFD output) |  | Inlet-chilling e-house / transformer |  | Inlet-chilling tower (12 cells): chiller heat rejection | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦2/0 | 3/C+3G | 2/0 | 1 | 1 | 480 | 75 | 106 | Duct bank | 683 | 38 |  |  |  |  | VD 2.9 %
J-P-0023 | J | GT inlet chilling | Motor 12 of 12, 75 kW (VFD output) |  | Inlet-chilling e-house / transformer |  | Inlet-chilling tower (12 cells): chiller heat rejection | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | VFD¦3/C+3G¦2/0 | 3/C+3G | 2/0 | 1 | 1 | 480 | 75 | 106 | Duct bank | 683 | 38 |  |  |  |  | VD 2.9 %
J-P-0024 | J | GT inlet chilling | Area / platform lighting circuit 1 (12 fixtures) |  | Inlet-chilling e-house / transformer |  | Inlet-chilling tower (12 cells): chiller heat rejection | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 3 | 5 | Duct bank | 778 | 38 |  |  |  |  | fixture-to-fixture run included
J-MV-0001 | J | GT inlet chilling | Inlet-chilling e-house / transformer | SWGR-13.8-1 | R1 SWGR-13.8-1 (11 x 36 in cubicles, 15 kV metal-clad) |  | Inlet-chilling e-house / transformer | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦1000 | 1/C | 1000 kcmil | 1 | 3 | 13800 | 12000 | 502 | Duct bank | 629 | 38
J-MV-0002 | J | GT inlet chilling | Inlet-chilling CW pump 1 |  | Inlet-chilling e-house / transformer |  | CW pumps (inlet chilling) | MV 5 kV | MV-105 5 kV 3/C Cu, EPR 133%, tape shield, gnd, PVC jacket | MV5¦3/C¦2 | 3/C | 2 | 1 | 1 | 4160 | 450 | 69 | Tray | 0 | 70
J-MV-0003 | J | GT inlet chilling | Inlet-chilling CW pump 2 |  | Inlet-chilling e-house / transformer |  | CW pumps (inlet chilling) | MV 5 kV | MV-105 5 kV 3/C Cu, EPR 133%, tape shield, gnd, PVC jacket | MV5¦3/C¦2 | 3/C | 2 | 1 | 1 | 4160 | 450 | 69 | Tray | 0 | 70
J-MV-0004 | J | GT inlet chilling | Inlet-chilling CW pump 3 |  | Inlet-chilling e-house / transformer |  | CW pumps (inlet chilling) | MV 5 kV | MV-105 5 kV 3/C Cu, EPR 133%, tape shield, gnd, PVC jacket | MV5¦3/C¦2 | 3/C | 2 | 1 | 1 | 4160 | 450 | 69 | Tray | 0 | 70
J-MV-0005 | J | GT inlet chilling | Inlet-chilling CW pump 4 |  | Inlet-chilling e-house / transformer |  | CW pumps (inlet chilling) | MV 5 kV | MV-105 5 kV 3/C Cu, EPR 133%, tape shield, gnd, PVC jacket | MV5¦3/C¦2 | 3/C | 2 | 1 | 1 | 4160 | 450 | 69 | Tray | 0 | 70
J-MV-0006 | J | GT inlet chilling | Water-cooled chiller CH-1 |  | Inlet-chilling e-house / transformer |  | Chillers x6 (water-cooled) | MV 5 kV | MV-105 5 kV 3/C Cu, EPR 133%, tape shield, gnd, PVC jacket | MV5¦3/C¦250 | 3/C | 250 kcmil | 1 | 1 | 4160 | 1500 | 231 | Duct bank | 10 | 32
J-MV-0007 | J | GT inlet chilling | Water-cooled chiller CH-2 |  | Inlet-chilling e-house / transformer |  | Chillers x6 (water-cooled) | MV 5 kV | MV-105 5 kV 3/C Cu, EPR 133%, tape shield, gnd, PVC jacket | MV5¦3/C¦250 | 3/C | 250 kcmil | 1 | 1 | 4160 | 1500 | 231 | Duct bank | 10 | 32
J-MV-0008 | J | GT inlet chilling | Water-cooled chiller CH-3 |  | Inlet-chilling e-house / transformer |  | Chillers x6 (water-cooled) | MV 5 kV | MV-105 5 kV 3/C Cu, EPR 133%, tape shield, gnd, PVC jacket | MV5¦3/C¦250 | 3/C | 250 kcmil | 1 | 1 | 4160 | 1500 | 231 | Duct bank | 10 | 32
J-MV-0009 | J | GT inlet chilling | Water-cooled chiller CH-4 |  | Inlet-chilling e-house / transformer |  | Chillers x6 (water-cooled) | MV 5 kV | MV-105 5 kV 3/C Cu, EPR 133%, tape shield, gnd, PVC jacket | MV5¦3/C¦250 | 3/C | 250 kcmil | 1 | 1 | 4160 | 1500 | 231 | Duct bank | 10 | 32
J-MV-0010 | J | GT inlet chilling | Water-cooled chiller CH-5 |  | Inlet-chilling e-house / transformer |  | Chillers x6 (water-cooled) | MV 5 kV | MV-105 5 kV 3/C Cu, EPR 133%, tape shield, gnd, PVC jacket | MV5¦3/C¦250 | 3/C | 250 kcmil | 1 | 1 | 4160 | 1500 | 231 | Duct bank | 10 | 32
J-MV-0011 | J | GT inlet chilling | Water-cooled chiller CH-6 |  | Inlet-chilling e-house / transformer |  | Chillers x6 (water-cooled) | MV 5 kV | MV-105 5 kV 3/C Cu, EPR 133%, tape shield, gnd, PVC jacket | MV5¦3/C¦250 | 3/C | 250 kcmil | 1 | 1 | 4160 | 1500 | 231 | Duct bank | 10 | 32
K-L-0001 | K | Fuel supply (adjacent market) | Lighting, receptacles and small power branch circuits (allowance) |  | H2 20: 13.8 kV e-house |  | H2 20: 13.8 kV e-house | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | THHN¦1/C¦12 | 1/C | 12 | 1 | 1 | 277 |  |  | Conduit | 1536 | 0 |  |  |  |  | allowance: 1.6 ft of conductor per ft2 of floor
K-L-0002 | K | Fuel supply (adjacent market) | Lighting, receptacles and small power branch circuits (allowance) |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | LNG 17: LNG e-house (13.8 kV / 480 V) | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | THHN¦1/C¦12 | 1/C | 12 | 1 | 1 | 277 |  |  | Conduit | 896 | 0 |  |  |  |  | allowance: 1.6 ft of conductor per ft2 of floor
K-L-0003 | K | Fuel supply (adjacent market) | Lighting, receptacles and small power branch circuits (allowance) |  | M&R 6: regulation / flow control building |  | M&R 6: regulation / flow control building | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | THHN¦1/C¦12 | 1/C | 12 | 1 | 1 | 277 |  |  | Conduit | 1440 | 0 |  |  |  |  | allowance: 1.6 ft of conductor per ft2 of floor
K-L-0004 | K | Fuel supply (adjacent market) | Lighting, receptacles and small power branch circuits (allowance) |  | M&R 7: gas quality + measurement building |  | M&R 7: gas quality + measurement building | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | THHN¦1/C¦12 | 1/C | 12 | 1 | 1 | 277 |  |  | Conduit | 205 | 0 |  |  |  |  | allowance: 1.6 ft of conductor per ft2 of floor
K-C-0001 | K | Fuel supply (adjacent market) | Motor 1 of 1: control / local station |  | H2 20: 13.8 kV e-house | T-H2 | H2 19: T-H2 230/13.8 kV (about 40 MVA) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 35 | 32
K-C-0002 | K | Fuel supply (adjacent market) | Solenoid to JB JB-T-H2-SOL01: 2 x 2/C (field cables) | T-H2 | H2 19: T-H2 230/13.8 kV (about 40 MVA) | JB-T-H2-SOL01 | H2 19: T-H2 230/13.8 kV (about 40 MVA) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 2 | 1 |  |  |  | Tray / conduit | 80 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0003 | K | Fuel supply (adjacent market) | Home run JB-T-H2-SOL01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-T-H2-SOL01 | H2 19: T-H2 230/13.8 kV (about 40 MVA) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 35 | 32
K-C-0004 | K | Fuel supply (adjacent market) | Motor 1 of 1: control / local station |  | H2 20: 13.8 kV e-house |  | H2 20: 13.8 kV e-house | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 32
K-C-0005 | K | Fuel supply (adjacent market) | Solenoid to JB JB-H2 20: 13.8 kV e-h-SOL01: 2 x 2/C (field cables) |  | H2 20: 13.8 kV e-house | JB-H2 20: 13.8 kV e-h-SOL01 | H2 20: 13.8 kV e-house | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 2 | 1 |  |  |  | Tray / conduit | 69 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0006 | K | Fuel supply (adjacent market) | Home run JB-H2 20: 13.8 kV e-h-SOL01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 20: 13.8 kV e-h-SOL01 | H2 20: 13.8 kV e-house | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 32
K-C-0007 | K | Fuel supply (adjacent market) | Motor 1 of 1: control / local station |  | H2 20: 13.8 kV e-house |  | H2 21: rectifier transformer 1 (7 MVA) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 356 | 48
K-C-0008 | K | Fuel supply (adjacent market) | Solenoid to JB JB-H2 21: rectifier t-SOL01: 2 x 2/C (field cables) |  | H2 21: rectifier transformer 1 (7 MVA) | JB-H2 21: rectifier t-SOL01 | H2 21: rectifier transformer 1 (7 MVA) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 2 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0009 | K | Fuel supply (adjacent market) | Home run JB-H2 21: rectifier t-SOL01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 21: rectifier t-SOL01 | H2 21: rectifier transformer 1 (7 MVA) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 356 | 48
K-C-0010 | K | Fuel supply (adjacent market) | Control |  | H2 20: 13.8 kV e-house |  | H2 21: rectifier transformer 1 (7 MVA) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 356 | 48
K-C-0011 | K | Fuel supply (adjacent market) | Control |  | H2 20: 13.8 kV e-house |  | H2 21: rectifier transformer 1 (7 MVA) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 356 | 48
K-C-0012 | K | Fuel supply (adjacent market) | CT / VT |  | H2 20: 13.8 kV e-house |  | H2 21: rectifier transformer 1 (7 MVA) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Duct bank | 356 | 48
K-C-0013 | K | Fuel supply (adjacent market) | CT / VT |  | H2 20: 13.8 kV e-house |  | H2 21: rectifier transformer 1 (7 MVA) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Duct bank | 356 | 48
K-C-0014 | K | Fuel supply (adjacent market) | Motor 1 of 1: control / local station |  | H2 20: 13.8 kV e-house |  | H2 21: rectifier transformer 2 (7 MVA) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 356 | 32
K-C-0015 | K | Fuel supply (adjacent market) | Solenoid to JB JB-H2 21: rectifier t-SOL01: 2 x 2/C (field cables) |  | H2 21: rectifier transformer 2 (7 MVA) | JB-H2 21: rectifier t-SOL01 | H2 21: rectifier transformer 2 (7 MVA) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 2 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0016 | K | Fuel supply (adjacent market) | Home run JB-H2 21: rectifier t-SOL01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 21: rectifier t-SOL01 | H2 21: rectifier transformer 2 (7 MVA) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 356 | 32
K-C-0017 | K | Fuel supply (adjacent market) | Control |  | H2 20: 13.8 kV e-house |  | H2 21: rectifier transformer 2 (7 MVA) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 356 | 32
K-C-0018 | K | Fuel supply (adjacent market) | Control |  | H2 20: 13.8 kV e-house |  | H2 21: rectifier transformer 2 (7 MVA) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 356 | 32
K-C-0019 | K | Fuel supply (adjacent market) | CT / VT |  | H2 20: 13.8 kV e-house |  | H2 21: rectifier transformer 2 (7 MVA) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Duct bank | 356 | 32
K-C-0020 | K | Fuel supply (adjacent market) | CT / VT |  | H2 20: 13.8 kV e-house |  | H2 21: rectifier transformer 2 (7 MVA) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Duct bank | 356 | 32
K-C-0021 | K | Fuel supply (adjacent market) | Motor 1 of 1: control / local station |  | H2 20: 13.8 kV e-house |  | H2 21: rectifier transformer 3 (7 MVA) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 334 | 32
K-C-0022 | K | Fuel supply (adjacent market) | Solenoid to JB JB-H2 21: rectifier t-SOL01: 2 x 2/C (field cables) |  | H2 21: rectifier transformer 3 (7 MVA) | JB-H2 21: rectifier t-SOL01 | H2 21: rectifier transformer 3 (7 MVA) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 2 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0023 | K | Fuel supply (adjacent market) | Home run JB-H2 21: rectifier t-SOL01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 21: rectifier t-SOL01 | H2 21: rectifier transformer 3 (7 MVA) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 334 | 32
K-C-0024 | K | Fuel supply (adjacent market) | Control |  | H2 20: 13.8 kV e-house |  | H2 21: rectifier transformer 3 (7 MVA) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 334 | 32
K-C-0025 | K | Fuel supply (adjacent market) | Control |  | H2 20: 13.8 kV e-house |  | H2 21: rectifier transformer 3 (7 MVA) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 334 | 32
K-C-0026 | K | Fuel supply (adjacent market) | CT / VT |  | H2 20: 13.8 kV e-house |  | H2 21: rectifier transformer 3 (7 MVA) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Duct bank | 334 | 32
K-C-0027 | K | Fuel supply (adjacent market) | CT / VT |  | H2 20: 13.8 kV e-house |  | H2 21: rectifier transformer 3 (7 MVA) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Duct bank | 334 | 32
K-C-0028 | K | Fuel supply (adjacent market) | Motor 1 of 1: control / local station |  | H2 20: 13.8 kV e-house |  | H2 21: rectifier transformer 4 (7 MVA) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 312 | 32
K-C-0029 | K | Fuel supply (adjacent market) | Solenoid to JB JB-H2 21: rectifier t-SOL01: 2 x 2/C (field cables) |  | H2 21: rectifier transformer 4 (7 MVA) | JB-H2 21: rectifier t-SOL01 | H2 21: rectifier transformer 4 (7 MVA) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 2 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0030 | K | Fuel supply (adjacent market) | Home run JB-H2 21: rectifier t-SOL01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 21: rectifier t-SOL01 | H2 21: rectifier transformer 4 (7 MVA) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 312 | 32
K-C-0031 | K | Fuel supply (adjacent market) | Control |  | H2 20: 13.8 kV e-house |  | H2 21: rectifier transformer 4 (7 MVA) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 312 | 32
K-C-0032 | K | Fuel supply (adjacent market) | Control |  | H2 20: 13.8 kV e-house |  | H2 21: rectifier transformer 4 (7 MVA) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 312 | 32
K-C-0033 | K | Fuel supply (adjacent market) | CT / VT |  | H2 20: 13.8 kV e-house |  | H2 21: rectifier transformer 4 (7 MVA) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Duct bank | 312 | 32
K-C-0034 | K | Fuel supply (adjacent market) | CT / VT |  | H2 20: 13.8 kV e-house |  | H2 21: rectifier transformer 4 (7 MVA) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Duct bank | 312 | 32
K-C-0035 | K | Fuel supply (adjacent market) | Motor 1 of 1: control / local station |  | H2 20: 13.8 kV e-house |  | H2 21: rectifier transformer 5 (7 MVA) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 254 | 32
K-C-0036 | K | Fuel supply (adjacent market) | Solenoid to JB JB-H2 21: rectifier t-SOL01: 2 x 2/C (field cables) |  | H2 21: rectifier transformer 5 (7 MVA) | JB-H2 21: rectifier t-SOL01 | H2 21: rectifier transformer 5 (7 MVA) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 2 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0037 | K | Fuel supply (adjacent market) | Home run JB-H2 21: rectifier t-SOL01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 21: rectifier t-SOL01 | H2 21: rectifier transformer 5 (7 MVA) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 254 | 32
K-C-0038 | K | Fuel supply (adjacent market) | Control |  | H2 20: 13.8 kV e-house |  | H2 21: rectifier transformer 5 (7 MVA) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 254 | 32
K-C-0039 | K | Fuel supply (adjacent market) | Control |  | H2 20: 13.8 kV e-house |  | H2 21: rectifier transformer 5 (7 MVA) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦12/C¦14 | 12/C | 14 | 1 | 1 |  |  |  | Duct bank | 254 | 32
K-C-0040 | K | Fuel supply (adjacent market) | CT / VT |  | H2 20: 13.8 kV e-house |  | H2 21: rectifier transformer 5 (7 MVA) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Duct bank | 254 | 32
K-C-0041 | K | Fuel supply (adjacent market) | CT / VT |  | H2 20: 13.8 kV e-house |  | H2 21: rectifier transformer 5 (7 MVA) | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | CTCT¦4/C¦10 | 4/C | 10 | 1 | 1 |  |  |  | Duct bank | 254 | 32
K-C-0042 | K | Fuel supply (adjacent market) | Motor 1 of 1: control / local station |  | H2 20: 13.8 kV e-house | H2-EL | H2 22: electrolyzer building (5 x HyLYZER-1000 + 5 rectifiers) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 346 | 32
K-C-0043 | K | Fuel supply (adjacent market) | Solenoid to JB JB-H2-EL-SOL01: 2 x 2/C (field cables) | H2-EL | H2 22: electrolyzer building (5 x HyLYZER-1000 + 5 rectifiers) | JB-H2-EL-SOL01 | H2 22: electrolyzer building (5 x HyLYZER-1000 + 5 rectifiers) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 2 | 1 |  |  |  | Tray / conduit | 157 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0044 | K | Fuel supply (adjacent market) | Home run JB-H2-EL-SOL01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2-EL-SOL01 | H2 22: electrolyzer building (5 x HyLYZER-1000 + 5 rectifiers) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 346 | 32
K-C-0045 | K | Fuel supply (adjacent market) | Motor 1 of 1: control / local station |  | H2 20: 13.8 kV e-house |  | H2 23: dry coolers | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 100 | 32
K-C-0046 | K | Fuel supply (adjacent market) | Solenoid to JB JB-H2 23: dry coolers-SOL01: 2 x 2/C (field cables) |  | H2 23: dry coolers | JB-H2 23: dry coolers-SOL01 | H2 23: dry coolers | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 2 | 1 |  |  |  | Tray / conduit | 111 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0047 | K | Fuel supply (adjacent market) | Home run JB-H2 23: dry coolers-SOL01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 23: dry coolers-SOL01 | H2 23: dry coolers | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 100 | 32
K-C-0048 | K | Fuel supply (adjacent market) | Motor 1 of 1: control / local station |  | H2 20: 13.8 kV e-house |  | H2 24: water purification (RO / EDI) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 146 | 32
K-C-0049 | K | Fuel supply (adjacent market) | Solenoid to JB JB-H2 24: water purif-SOL01: 2 x 2/C (field cables) |  | H2 24: water purification (RO / EDI) | JB-H2 24: water purif-SOL01 | H2 24: water purification (RO / EDI) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 2 | 1 |  |  |  | Tray / conduit | 60 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0050 | K | Fuel supply (adjacent market) | Home run JB-H2 24: water purif-SOL01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 24: water purif-SOL01 | H2 24: water purification (RO / EDI) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 146 | 32
K-C-0051 | K | Fuel supply (adjacent market) | Motor 1 of 1: control / local station |  | H2 20: 13.8 kV e-house |  | H2 25: H2 dryer / purification | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 0 | 49
K-C-0052 | K | Fuel supply (adjacent market) | Solenoid to JB JB-H2 25: H2 dryer / -SOL01: 2 x 2/C (field cables) |  | H2 25: H2 dryer / purification | JB-H2 25: H2 dryer / -SOL01 | H2 25: H2 dryer / purification | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 2 | 1 |  |  |  | Tray / conduit | 60 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0053 | K | Fuel supply (adjacent market) | Home run JB-H2 25: H2 dryer / -SOL01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 25: H2 dryer / -SOL01 | H2 25: H2 dryer / purification | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 0 | 49
K-C-0054 | K | Fuel supply (adjacent market) | Motor 1 of 1: control / local station |  | H2 20: 13.8 kV e-house |  | H2 26: H2 compressor 1 (40 ft ISO) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 50 | 32
K-C-0055 | K | Fuel supply (adjacent market) | Solenoid to JB JB-H2 26: H2 compress-SOL01: 2 x 2/C (field cables) |  | H2 26: H2 compressor 1 (40 ft ISO) | JB-H2 26: H2 compress-SOL01 | H2 26: H2 compressor 1 (40 ft ISO) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 2 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0056 | K | Fuel supply (adjacent market) | Home run JB-H2 26: H2 compress-SOL01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 26: H2 compress-SOL01 | H2 26: H2 compressor 1 (40 ft ISO) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 50 | 32
K-C-0057 | K | Fuel supply (adjacent market) | Motor 1 of 1: control / local station |  | H2 20: 13.8 kV e-house |  | H2 26: H2 compressor 2 (40 ft ISO) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 50 | 47
K-C-0058 | K | Fuel supply (adjacent market) | Solenoid to JB JB-H2 26: H2 compress-SOL01: 2 x 2/C (field cables) |  | H2 26: H2 compressor 2 (40 ft ISO) | JB-H2 26: H2 compress-SOL01 | H2 26: H2 compressor 2 (40 ft ISO) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 2 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0059 | K | Fuel supply (adjacent market) | Home run JB-H2 26: H2 compress-SOL01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 26: H2 compress-SOL01 | H2 26: H2 compressor 2 (40 ft ISO) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 50 | 47
K-C-0060 | K | Fuel supply (adjacent market) | Motor 1 of 1: control / local station |  | H2 20: 13.8 kV e-house |  | H2 27: storage tube bank (~40 ft tubes) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 50 | 97
K-C-0061 | K | Fuel supply (adjacent market) | Solenoid to JB JB-H2 27: storage tub-SOL01: 2 x 2/C (field cables) |  | H2 27: storage tube bank (~40 ft tubes) | JB-H2 27: storage tub-SOL01 | H2 27: storage tube bank (~40 ft tubes) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 2 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0062 | K | Fuel supply (adjacent market) | Home run JB-H2 27: storage tub-SOL01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 27: storage tub-SOL01 | H2 27: storage tube bank (~40 ft tubes) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 50 | 97
K-C-0063 | K | Fuel supply (adjacent market) | Motor 1 of 1: control / local station |  | H2 20: 13.8 kV e-house |  | H2 27: storage tube bank (~40 ft tubes) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 50 | 117
K-C-0064 | K | Fuel supply (adjacent market) | Solenoid to JB JB-H2 27: storage tub-SOL01: 2 x 2/C (field cables) |  | H2 27: storage tube bank (~40 ft tubes) | JB-H2 27: storage tub-SOL01 | H2 27: storage tube bank (~40 ft tubes) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 2 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0065 | K | Fuel supply (adjacent market) | Home run JB-H2 27: storage tub-SOL01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 27: storage tub-SOL01 | H2 27: storage tube bank (~40 ft tubes) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 50 | 117
K-C-0066 | K | Fuel supply (adjacent market) | Motor 1 of 1: control / local station |  | H2 20: 13.8 kV e-house |  | H2 27: storage tube bank (~40 ft tubes) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 50 | 97
K-C-0067 | K | Fuel supply (adjacent market) | Solenoid to JB JB-H2 27: storage tub-SOL01: 2 x 2/C (field cables) |  | H2 27: storage tube bank (~40 ft tubes) | JB-H2 27: storage tub-SOL01 | H2 27: storage tube bank (~40 ft tubes) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 2 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0068 | K | Fuel supply (adjacent market) | Home run JB-H2 27: storage tub-SOL01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 27: storage tub-SOL01 | H2 27: storage tube bank (~40 ft tubes) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 50 | 97
K-C-0069 | K | Fuel supply (adjacent market) | Motor 1 of 1: control / local station |  | H2 20: 13.8 kV e-house |  | H2 27: storage tube bank (~40 ft tubes) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 50 | 117
K-C-0070 | K | Fuel supply (adjacent market) | Solenoid to JB JB-H2 27: storage tub-SOL01: 2 x 2/C (field cables) |  | H2 27: storage tube bank (~40 ft tubes) | JB-H2 27: storage tub-SOL01 | H2 27: storage tube bank (~40 ft tubes) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 2 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0071 | K | Fuel supply (adjacent market) | Home run JB-H2 27: storage tub-SOL01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 27: storage tub-SOL01 | H2 27: storage tube bank (~40 ft tubes) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 50 | 117
K-C-0072 | K | Fuel supply (adjacent market) | Motor 1 of 1: control / local station |  | H2 20: 13.8 kV e-house |  | H2 28: N2 purge supply | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 53 | 36
K-C-0073 | K | Fuel supply (adjacent market) | Solenoid to JB JB-H2 28: N2 purge su-SOL01: 2 x 2/C (field cables) |  | H2 28: N2 purge supply | JB-H2 28: N2 purge su-SOL01 | H2 28: N2 purge supply | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 2 | 1 |  |  |  | Tray / conduit | 56 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0074 | K | Fuel supply (adjacent market) | Home run JB-H2 28: N2 purge su-SOL01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 28: N2 purge su-SOL01 | H2 28: N2 purge supply | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 53 | 36
K-C-0075 | K | Fuel supply (adjacent market) | Motor 1 of 1: control / local station |  | H2 20: 13.8 kV e-house |  | H2 29: vent stack | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 55 | 205
K-C-0076 | K | Fuel supply (adjacent market) | Solenoid to JB JB-H2 29: vent stack-SOL01: 2 x 2/C (field cables) |  | H2 29: vent stack | JB-H2 29: vent stack-SOL01 | H2 29: vent stack | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 2 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0077 | K | Fuel supply (adjacent market) | Home run JB-H2 29: vent stack-SOL01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 29: vent stack-SOL01 | H2 29: vent stack | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 55 | 205
K-C-0078 | K | Fuel supply (adjacent market) | Motor 1 of 1: control / local station |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | H2 30: H2 / gas blending station (plant gas yard) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 994 | 114
K-C-0079 | K | Fuel supply (adjacent market) | Solenoid to JB JB-H2 30: H2 / gas bl-SOL01: 2 x 2/C (field cables) |  | H2 30: H2 / gas blending station (plant gas yard) | JB-H2 30: H2 / gas bl-SOL01 | H2 30: H2 / gas blending station (plant gas yard) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 2 | 1 |  |  |  | Tray / conduit | 129 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0080 | K | Fuel supply (adjacent market) | Home run JB-H2 30: H2 / gas bl-SOL01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-H2 30: H2 / gas bl-SOL01 | H2 30: H2 / gas blending station (plant gas yard) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 994 | 114
K-C-0081 | K | Fuel supply (adjacent market) | Motor 1 of 2: control / local station |  | H2 20: 13.8 kV e-house |  | H2 pipe track and cable trench, hall -> dryer / compressors (N2, instr | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 53 | 62
K-C-0082 | K | Fuel supply (adjacent market) | Motor 2 of 2: control / local station |  | H2 20: 13.8 kV e-house |  | H2 pipe track and cable trench, hall -> dryer / compressors (N2, instr | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 53 | 62
K-C-0083 | K | Fuel supply (adjacent market) | Control |  | H2 20: 13.8 kV e-house | H2-ST | H2 storage tube banks x4 | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 50 | 92
K-C-0084 | K | Fuel supply (adjacent market) | Motor 1 of 1: control / local station |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | LNG 10: truck unloading bay 1 | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 237 | 61
K-C-0085 | K | Fuel supply (adjacent market) | Solenoid to JB JB-LNG 10: truck unlo-SOL01: 2 x 2/C (field cables) |  | LNG 10: truck unloading bay 1 | JB-LNG 10: truck unlo-SOL01 | LNG 10: truck unloading bay 1 | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 2 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0086 | K | Fuel supply (adjacent market) | Home run JB-LNG 10: truck unlo-SOL01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 10: truck unlo-SOL01 | LNG 10: truck unloading bay 1 | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 237 | 61
K-C-0087 | K | Fuel supply (adjacent market) | Motor 1 of 1: control / local station |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | LNG 10: truck unloading bay 2 | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 147 | 66
K-C-0088 | K | Fuel supply (adjacent market) | Solenoid to JB JB-LNG 10: truck unlo-SOL01: 2 x 2/C (field cables) |  | LNG 10: truck unloading bay 2 | JB-LNG 10: truck unlo-SOL01 | LNG 10: truck unloading bay 2 | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 2 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0089 | K | Fuel supply (adjacent market) | Home run JB-LNG 10: truck unlo-SOL01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 10: truck unlo-SOL01 | LNG 10: truck unloading bay 2 | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 147 | 66
K-C-0090 | K | Fuel supply (adjacent market) | Motor 1 of 1: control / local station |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | LNG 10: unloading skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 237 | 32
K-C-0091 | K | Fuel supply (adjacent market) | Solenoid to JB JB-LNG 10: unloading -SOL01: 2 x 2/C (field cables) |  | LNG 10: unloading skid | JB-LNG 10: unloading -SOL01 | LNG 10: unloading skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 2 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0092 | K | Fuel supply (adjacent market) | Home run JB-LNG 10: unloading -SOL01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 10: unloading -SOL01 | LNG 10: unloading skid | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 237 | 32
K-C-0093 | K | Fuel supply (adjacent market) | Motor 1 of 1: control / local station |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | LNG 12: spill impoundment (NFPA 59A, to verify) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 230 | 32
K-C-0094 | K | Fuel supply (adjacent market) | Solenoid to JB JB-LNG 12: spill impo-SOL01: 2 x 2/C (field cables) |  | LNG 12: spill impoundment (NFPA 59A, to verify) | JB-LNG 12: spill impo-SOL01 | LNG 12: spill impoundment (NFPA 59A, to verify) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 2 | 1 |  |  |  | Tray / conduit | 170 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0095 | K | Fuel supply (adjacent market) | Home run JB-LNG 12: spill impo-SOL01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 12: spill impo-SOL01 | LNG 12: spill impoundment (NFPA 59A, to verify) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 230 | 32
K-C-0096 | K | Fuel supply (adjacent market) | Motor 1 of 1: control / local station |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | LNG 13: send-out pumps 2 x 100% | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 110 | 32
K-C-0097 | K | Fuel supply (adjacent market) | Solenoid to JB JB-LNG 13: send-out p-SOL01: 2 x 2/C (field cables) |  | LNG 13: send-out pumps 2 x 100% | JB-LNG 13: send-out p-SOL01 | LNG 13: send-out pumps 2 x 100% | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 2 | 1 |  |  |  | Tray / conduit | 63 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0098 | K | Fuel supply (adjacent market) | Home run JB-LNG 13: send-out p-SOL01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 13: send-out p-SOL01 | LNG 13: send-out pumps 2 x 100% | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 110 | 32
K-C-0099 | K | Fuel supply (adjacent market) | Motor 1 of 1: control / local station |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | LNG 14: vaporizers + glycol heater | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 259 | 32
K-C-0100 | K | Fuel supply (adjacent market) | Solenoid to JB JB-LNG 14: vaporizers-SOL01: 2 x 2/C (field cables) |  | LNG 14: vaporizers + glycol heater | JB-LNG 14: vaporizers-SOL01 | LNG 14: vaporizers + glycol heater | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 2 | 1 |  |  |  | Tray / conduit | 122 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0101 | K | Fuel supply (adjacent market) | Home run JB-LNG 14: vaporizers-SOL01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 14: vaporizers-SOL01 | LNG 14: vaporizers + glycol heater | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 259 | 32
K-C-0102 | K | Fuel supply (adjacent market) | Motor 1 of 1: control / local station |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | LNG 15: boil-off gas compressor | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 25 | 54
K-C-0103 | K | Fuel supply (adjacent market) | Solenoid to JB JB-LNG 15: boil-off g-SOL01: 2 x 2/C (field cables) |  | LNG 15: boil-off gas compressor | JB-LNG 15: boil-off g-SOL01 | LNG 15: boil-off gas compressor | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 2 | 1 |  |  |  | Tray / conduit | 67 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0104 | K | Fuel supply (adjacent market) | Home run JB-LNG 15: boil-off g-SOL01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 15: boil-off g-SOL01 | LNG 15: boil-off gas compressor | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 25 | 54
K-C-0105 | K | Fuel supply (adjacent market) | Motor 1 of 1: control / local station |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | LNG 16: send-out metering + pressure control | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 20 | 32
K-C-0106 | K | Fuel supply (adjacent market) | Solenoid to JB JB-LNG 16: send-out m-SOL01: 2 x 2/C (field cables) |  | LNG 16: send-out metering + pressure control | JB-LNG 16: send-out m-SOL01 | LNG 16: send-out metering + pressure control | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 2 | 1 |  |  |  | Tray / conduit | 74 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0107 | K | Fuel supply (adjacent market) | Home run JB-LNG 16: send-out m-SOL01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 16: send-out m-SOL01 | LNG 16: send-out metering + pressure control | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 20 | 32
K-C-0108 | K | Fuel supply (adjacent market) | Motor 1 of 1: control / local station |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | LNG 17: LNG e-house (13.8 kV / 480 V) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 32
K-C-0109 | K | Fuel supply (adjacent market) | Solenoid to JB JB-LNG 17: LNG e-hous-SOL01: 2 x 2/C (field cables) |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 17: LNG e-hous-SOL01 | LNG 17: LNG e-house (13.8 kV / 480 V) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 2 | 1 |  |  |  | Tray / conduit | 58 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0110 | K | Fuel supply (adjacent market) | Home run JB-LNG 17: LNG e-hous-SOL01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 17: LNG e-hous-SOL01 | LNG 17: LNG e-house (13.8 kV / 480 V) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 32
K-C-0111 | K | Fuel supply (adjacent market) | Motor 1 of 1: control / local station |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | LNG 18: vent stack | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 25 | 117
K-C-0112 | K | Fuel supply (adjacent market) | Solenoid to JB JB-LNG 18: vent stack-SOL01: 2 x 2/C (field cables) |  | LNG 18: vent stack | JB-LNG 18: vent stack-SOL01 | LNG 18: vent stack | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 2 | 1 |  |  |  | Tray / conduit | 55 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0113 | K | Fuel supply (adjacent market) | Home run JB-LNG 18: vent stack-SOL01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 18: vent stack-SOL01 | LNG 18: vent stack | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 25 | 117
K-C-0114 | K | Fuel supply (adjacent market) | Solenoid to JB JB-M&R 2: insulating -SOL01: 4 x 2/C (field cables) |  | M&R 2: insulating joint + ESD valve | JB-M&R 2: insulating -SOL01 | M&R 2: insulating joint + ESD valve | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 4 | 1 |  |  |  | Tray / conduit | 40 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0115 | K | Fuel supply (adjacent market) | Home run JB-M&R 2: insulating -SOL01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-M&R 2: insulating -SOL01 | M&R 2: insulating joint + ESD valve | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 758 | 32
K-C-0116 | K | Fuel supply (adjacent market) | Solenoid to JB JB-M&R 3: horizontal -SOL01: 4 x 2/C (field cables) |  | M&R 3: horizontal filter-separator | JB-M&R 3: horizontal -SOL01 | M&R 3: horizontal filter-separator | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 4 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0117 | K | Fuel supply (adjacent market) | Home run JB-M&R 3: horizontal -SOL01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-M&R 3: horizontal -SOL01 | M&R 3: horizontal filter-separator | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 797 | 32
K-C-0118 | K | Fuel supply (adjacent market) | Control |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | M&R 4: line heater 1 (water bath) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 593 | 32
K-C-0119 | K | Fuel supply (adjacent market) | Control |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | M&R 4: line heater 2 (water bath) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 593 | 50
K-C-0120 | K | Fuel supply (adjacent market) | Control |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | M&R 4: line heater 3 (water bath) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 593 | 68
K-C-0121 | K | Fuel supply (adjacent market) | Solenoid to JB JB-M&R 6: regulation -SOL01: 6 x 2/C (field cables) |  | M&R 6: regulation / flow control building | JB-M&R 6: regulation -SOL01 | M&R 6: regulation / flow control building | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦2/C¦14 | 2/C | 14 | 6 | 1 |  |  |  | Tray / conduit | 61 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-C-0122 | K | Fuel supply (adjacent market) | Home run JB-M&R 6: regulation -SOL01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-M&R 6: regulation -SOL01 | M&R 6: regulation / flow control building | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦25/C¦14 | 25/C | 14 | 1 | 1 |  |  |  | Duct bank | 470 | 70
K-C-0123 | K | Fuel supply (adjacent market) | Control |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | M&R 9: service panel + UPS, SCADA RTU, CP | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 466 | 32
K-C-0124 | K | Fuel supply (adjacent market) | Control |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | M&R CP test station (as drawn) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 441 | 42
K-C-0125 | K | Fuel supply (adjacent market) | Control |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | M&R SCADA antenna mast base (as drawn) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 433 | 32
K-C-0126 | K | Fuel supply (adjacent market) | Control |  | H2 20: 13.8 kV e-house |  | PEM electrolyzer 1 (HyLYZER-1000) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 358 | 32
K-C-0127 | K | Fuel supply (adjacent market) | Control |  | H2 20: 13.8 kV e-house |  | PEM electrolyzer 2 (HyLYZER-1000) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 358 | 48
K-C-0128 | K | Fuel supply (adjacent market) | Control |  | H2 20: 13.8 kV e-house |  | PEM electrolyzer 3 (HyLYZER-1000) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 348 | 49
K-C-0129 | K | Fuel supply (adjacent market) | Control |  | H2 20: 13.8 kV e-house |  | PEM electrolyzer 4 (HyLYZER-1000) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 328 | 49
K-C-0130 | K | Fuel supply (adjacent market) | Control |  | H2 20: 13.8 kV e-house |  | PEM electrolyzer 5 (HyLYZER-1000) | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | CTAX¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 328 | 32
K-C-0131 | K | Fuel supply (adjacent market) | Control |  | H2 20: 13.8 kV e-house |  | Rectifier 1 (7 MVA) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 346 | 32
K-C-0132 | K | Fuel supply (adjacent market) | Control |  | H2 20: 13.8 kV e-house |  | Rectifier 2 (7 MVA) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 361 | 32
K-C-0133 | K | Fuel supply (adjacent market) | Control |  | H2 20: 13.8 kV e-house |  | Rectifier 3 (7 MVA) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 341 | 32
K-C-0134 | K | Fuel supply (adjacent market) | Control |  | H2 20: 13.8 kV e-house |  | Rectifier 4 (7 MVA) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 321 | 32
K-C-0135 | K | Fuel supply (adjacent market) | Control |  | H2 20: 13.8 kV e-house |  | Rectifier 5 (7 MVA) | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Duct bank | 301 | 32
K-F-0001 | K | Fuel supply (adjacent market) | Plant network / DCS fibre | CR | Control / admin building (main control room) |  | H2 20: 13.8 kV e-house | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Trench | 4293 | 36
K-F-0002 | K | Fuel supply (adjacent market) | Plant network / DCS fibre | CR | Control / admin building (main control room) |  | LNG 17: LNG e-house (13.8 kV / 480 V) | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Duct bank | 3499 | 359
K-F-0003 | K | Fuel supply (adjacent market) | Plant network / DCS fibre | CR | Control / admin building (main control room) |  | M&R 6: regulation / flow control building | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Duct bank | 3128 | 302
K-F-0004 | K | Fuel supply (adjacent market) | Plant network / DCS fibre | CR | Control / admin building (main control room) |  | M&R 7: gas quality + measurement building | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | FO¦12 SM¦- | 12 SM | - | 1 | 1 |  |  |  | Duct bank | 2978 | 284
K-FA-0001 | K | Fuel supply (adjacent market) | Fire alarm / F&G loop (to the local FACP / F&G node) |  | H2 20: 13.8 kV e-house |  | H2 20: 13.8 kV e-house | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 32
K-FA-0002 | K | Fuel supply (adjacent market) | Fire alarm / F&G loop (to the local FACP / F&G node) |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | LNG 17: LNG e-house (13.8 kV / 480 V) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Tray | 0 | 32
K-FA-0003 | K | Fuel supply (adjacent market) | Fire alarm / F&G loop (to the local FACP / F&G node) |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | M&R 6: regulation / flow control building | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 470 | 70
K-FA-0004 | K | Fuel supply (adjacent market) | Fire alarm / F&G loop (to the local FACP / F&G node) |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | M&R 9: service panel + UPS, SCADA RTU, CP | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 466 | 32
K-FA-0005 | K | Fuel supply (adjacent market) | Fire alarm / F&G loop (to the local FACP / F&G node) |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | M&R SCADA antenna mast base (as drawn) | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | FA¦2/C¦14 | 2/C | 14 | 1 | 1 |  |  |  | Duct bank | 433 | 32
K-I-0001 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-T-H2-AI01: 12 x 1 pr (field cables) | T-H2 | H2 19: T-H2 230/13.8 kV (about 40 MVA) | JB-T-H2-AI01 | H2 19: T-H2 230/13.8 kV (about 40 MVA) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 80 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0002 | K | Fuel supply (adjacent market) | Home run JB-T-H2-AI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-T-H2-AI01 | H2 19: T-H2 230/13.8 kV (about 40 MVA) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 35 | 32
K-I-0003 | K | Fuel supply (adjacent market) | Discrete device to JB JB-T-H2-DI01: 12 x 1 pr (field cables) | T-H2 | H2 19: T-H2 230/13.8 kV (about 40 MVA) | JB-T-H2-DI01 | H2 19: T-H2 230/13.8 kV (about 40 MVA) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 80 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0004 | K | Fuel supply (adjacent market) | Home run JB-T-H2-DI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-T-H2-DI01 | H2 19: T-H2 230/13.8 kV (about 40 MVA) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 35 | 32
K-I-0005 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-H2 20: 13.8 kV e-h-AI01: 12 x 1 pr (field cables) |  | H2 20: 13.8 kV e-house | JB-H2 20: 13.8 kV e-h-AI01 | H2 20: 13.8 kV e-house | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 69 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0006 | K | Fuel supply (adjacent market) | Home run JB-H2 20: 13.8 kV e-h-AI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 20: 13.8 kV e-h-AI01 | H2 20: 13.8 kV e-house | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 32
K-I-0007 | K | Fuel supply (adjacent market) | Discrete device to JB JB-H2 20: 13.8 kV e-h-DI01: 12 x 1 pr (field cables) |  | H2 20: 13.8 kV e-house | JB-H2 20: 13.8 kV e-h-DI01 | H2 20: 13.8 kV e-house | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 69 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0008 | K | Fuel supply (adjacent market) | Home run JB-H2 20: 13.8 kV e-h-DI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 20: 13.8 kV e-h-DI01 | H2 20: 13.8 kV e-house | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 32
K-I-0009 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-H2 21: rectifier t-AI01: 12 x 1 pr (field cables) |  | H2 21: rectifier transformer 1 (7 MVA) | JB-H2 21: rectifier t-AI01 | H2 21: rectifier transformer 1 (7 MVA) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0010 | K | Fuel supply (adjacent market) | Home run JB-H2 21: rectifier t-AI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 21: rectifier t-AI01 | H2 21: rectifier transformer 1 (7 MVA) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 356 | 48
K-I-0011 | K | Fuel supply (adjacent market) | Discrete device to JB JB-H2 21: rectifier t-DI01: 12 x 1 pr (field cables) |  | H2 21: rectifier transformer 1 (7 MVA) | JB-H2 21: rectifier t-DI01 | H2 21: rectifier transformer 1 (7 MVA) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0012 | K | Fuel supply (adjacent market) | Home run JB-H2 21: rectifier t-DI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 21: rectifier t-DI01 | H2 21: rectifier transformer 1 (7 MVA) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 356 | 48
K-I-0013 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-H2 21: rectifier t-AI01: 12 x 1 pr (field cables) |  | H2 21: rectifier transformer 2 (7 MVA) | JB-H2 21: rectifier t-AI01 | H2 21: rectifier transformer 2 (7 MVA) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0014 | K | Fuel supply (adjacent market) | Home run JB-H2 21: rectifier t-AI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 21: rectifier t-AI01 | H2 21: rectifier transformer 2 (7 MVA) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 356 | 32
K-I-0015 | K | Fuel supply (adjacent market) | Discrete device to JB JB-H2 21: rectifier t-DI01: 12 x 1 pr (field cables) |  | H2 21: rectifier transformer 2 (7 MVA) | JB-H2 21: rectifier t-DI01 | H2 21: rectifier transformer 2 (7 MVA) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0016 | K | Fuel supply (adjacent market) | Home run JB-H2 21: rectifier t-DI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 21: rectifier t-DI01 | H2 21: rectifier transformer 2 (7 MVA) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 356 | 32
K-I-0017 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-H2 21: rectifier t-AI01: 12 x 1 pr (field cables) |  | H2 21: rectifier transformer 3 (7 MVA) | JB-H2 21: rectifier t-AI01 | H2 21: rectifier transformer 3 (7 MVA) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0018 | K | Fuel supply (adjacent market) | Home run JB-H2 21: rectifier t-AI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 21: rectifier t-AI01 | H2 21: rectifier transformer 3 (7 MVA) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 334 | 32
K-I-0019 | K | Fuel supply (adjacent market) | Discrete device to JB JB-H2 21: rectifier t-DI01: 12 x 1 pr (field cables) |  | H2 21: rectifier transformer 3 (7 MVA) | JB-H2 21: rectifier t-DI01 | H2 21: rectifier transformer 3 (7 MVA) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0020 | K | Fuel supply (adjacent market) | Home run JB-H2 21: rectifier t-DI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 21: rectifier t-DI01 | H2 21: rectifier transformer 3 (7 MVA) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 334 | 32
K-I-0021 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-H2 21: rectifier t-AI01: 12 x 1 pr (field cables) |  | H2 21: rectifier transformer 4 (7 MVA) | JB-H2 21: rectifier t-AI01 | H2 21: rectifier transformer 4 (7 MVA) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0022 | K | Fuel supply (adjacent market) | Home run JB-H2 21: rectifier t-AI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 21: rectifier t-AI01 | H2 21: rectifier transformer 4 (7 MVA) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 312 | 32
K-I-0023 | K | Fuel supply (adjacent market) | Discrete device to JB JB-H2 21: rectifier t-DI01: 12 x 1 pr (field cables) |  | H2 21: rectifier transformer 4 (7 MVA) | JB-H2 21: rectifier t-DI01 | H2 21: rectifier transformer 4 (7 MVA) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0024 | K | Fuel supply (adjacent market) | Home run JB-H2 21: rectifier t-DI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 21: rectifier t-DI01 | H2 21: rectifier transformer 4 (7 MVA) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 312 | 32
K-I-0025 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-H2 21: rectifier t-AI01: 12 x 1 pr (field cables) |  | H2 21: rectifier transformer 5 (7 MVA) | JB-H2 21: rectifier t-AI01 | H2 21: rectifier transformer 5 (7 MVA) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0026 | K | Fuel supply (adjacent market) | Home run JB-H2 21: rectifier t-AI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 21: rectifier t-AI01 | H2 21: rectifier transformer 5 (7 MVA) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 254 | 32
K-I-0027 | K | Fuel supply (adjacent market) | Discrete device to JB JB-H2 21: rectifier t-DI01: 12 x 1 pr (field cables) |  | H2 21: rectifier transformer 5 (7 MVA) | JB-H2 21: rectifier t-DI01 | H2 21: rectifier transformer 5 (7 MVA) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0028 | K | Fuel supply (adjacent market) | Home run JB-H2 21: rectifier t-DI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 21: rectifier t-DI01 | H2 21: rectifier transformer 5 (7 MVA) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 254 | 32
K-I-0029 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-H2-EL-AI01: 12 x 1 pr (field cables) | H2-EL | H2 22: electrolyzer building (5 x HyLYZER-1000 + 5 rectifiers) | JB-H2-EL-AI01 | H2 22: electrolyzer building (5 x HyLYZER-1000 + 5 rectifiers) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 157 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0030 | K | Fuel supply (adjacent market) | Home run JB-H2-EL-AI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2-EL-AI01 | H2 22: electrolyzer building (5 x HyLYZER-1000 + 5 rectifiers) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 346 | 32
K-I-0031 | K | Fuel supply (adjacent market) | Discrete device to JB JB-H2-EL-DI01: 12 x 1 pr (field cables) | H2-EL | H2 22: electrolyzer building (5 x HyLYZER-1000 + 5 rectifiers) | JB-H2-EL-DI01 | H2 22: electrolyzer building (5 x HyLYZER-1000 + 5 rectifiers) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 157 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0032 | K | Fuel supply (adjacent market) | Home run JB-H2-EL-DI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2-EL-DI01 | H2 22: electrolyzer building (5 x HyLYZER-1000 + 5 rectifiers) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 346 | 32
K-I-0033 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-H2 23: dry coolers-AI01: 12 x 1 pr (field cables) |  | H2 23: dry coolers | JB-H2 23: dry coolers-AI01 | H2 23: dry coolers | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 111 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0034 | K | Fuel supply (adjacent market) | Home run JB-H2 23: dry coolers-AI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 23: dry coolers-AI01 | H2 23: dry coolers | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 100 | 32
K-I-0035 | K | Fuel supply (adjacent market) | Discrete device to JB JB-H2 23: dry coolers-DI01: 12 x 1 pr (field cables) |  | H2 23: dry coolers | JB-H2 23: dry coolers-DI01 | H2 23: dry coolers | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 111 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0036 | K | Fuel supply (adjacent market) | Home run JB-H2 23: dry coolers-DI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 23: dry coolers-DI01 | H2 23: dry coolers | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 100 | 32
K-I-0037 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-H2 24: water purif-AI01: 12 x 1 pr (field cables) |  | H2 24: water purification (RO / EDI) | JB-H2 24: water purif-AI01 | H2 24: water purification (RO / EDI) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 60 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0038 | K | Fuel supply (adjacent market) | Home run JB-H2 24: water purif-AI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 24: water purif-AI01 | H2 24: water purification (RO / EDI) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 146 | 32
K-I-0039 | K | Fuel supply (adjacent market) | Discrete device to JB JB-H2 24: water purif-DI01: 12 x 1 pr (field cables) |  | H2 24: water purification (RO / EDI) | JB-H2 24: water purif-DI01 | H2 24: water purification (RO / EDI) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 60 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0040 | K | Fuel supply (adjacent market) | Home run JB-H2 24: water purif-DI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 24: water purif-DI01 | H2 24: water purification (RO / EDI) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 146 | 32
K-I-0041 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-H2 25: H2 dryer / -AI01: 12 x 1 pr (field cables) |  | H2 25: H2 dryer / purification | JB-H2 25: H2 dryer / -AI01 | H2 25: H2 dryer / purification | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 60 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0042 | K | Fuel supply (adjacent market) | Home run JB-H2 25: H2 dryer / -AI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 25: H2 dryer / -AI01 | H2 25: H2 dryer / purification | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 0 | 49
K-I-0043 | K | Fuel supply (adjacent market) | Discrete device to JB JB-H2 25: H2 dryer / -DI01: 12 x 1 pr (field cables) |  | H2 25: H2 dryer / purification | JB-H2 25: H2 dryer / -DI01 | H2 25: H2 dryer / purification | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 60 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0044 | K | Fuel supply (adjacent market) | Home run JB-H2 25: H2 dryer / -DI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 25: H2 dryer / -DI01 | H2 25: H2 dryer / purification | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 0 | 49
K-I-0045 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-H2 26: H2 compress-AI01: 12 x 1 pr (field cables) |  | H2 26: H2 compressor 1 (40 ft ISO) | JB-H2 26: H2 compress-AI01 | H2 26: H2 compressor 1 (40 ft ISO) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0046 | K | Fuel supply (adjacent market) | Home run JB-H2 26: H2 compress-AI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 26: H2 compress-AI01 | H2 26: H2 compressor 1 (40 ft ISO) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 50 | 32
K-I-0047 | K | Fuel supply (adjacent market) | Discrete device to JB JB-H2 26: H2 compress-DI01: 12 x 1 pr (field cables) |  | H2 26: H2 compressor 1 (40 ft ISO) | JB-H2 26: H2 compress-DI01 | H2 26: H2 compressor 1 (40 ft ISO) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0048 | K | Fuel supply (adjacent market) | Home run JB-H2 26: H2 compress-DI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 26: H2 compress-DI01 | H2 26: H2 compressor 1 (40 ft ISO) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 50 | 32
K-I-0049 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-H2 26: H2 compress-AI01: 12 x 1 pr (field cables) |  | H2 26: H2 compressor 2 (40 ft ISO) | JB-H2 26: H2 compress-AI01 | H2 26: H2 compressor 2 (40 ft ISO) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0050 | K | Fuel supply (adjacent market) | Home run JB-H2 26: H2 compress-AI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 26: H2 compress-AI01 | H2 26: H2 compressor 2 (40 ft ISO) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 50 | 47
K-I-0051 | K | Fuel supply (adjacent market) | Discrete device to JB JB-H2 26: H2 compress-DI01: 12 x 1 pr (field cables) |  | H2 26: H2 compressor 2 (40 ft ISO) | JB-H2 26: H2 compress-DI01 | H2 26: H2 compressor 2 (40 ft ISO) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0052 | K | Fuel supply (adjacent market) | Home run JB-H2 26: H2 compress-DI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 26: H2 compress-DI01 | H2 26: H2 compressor 2 (40 ft ISO) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 50 | 47
K-I-0053 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-H2 27: storage tub-AI01: 12 x 1 pr (field cables) |  | H2 27: storage tube bank (~40 ft tubes) | JB-H2 27: storage tub-AI01 | H2 27: storage tube bank (~40 ft tubes) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0054 | K | Fuel supply (adjacent market) | Home run JB-H2 27: storage tub-AI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 27: storage tub-AI01 | H2 27: storage tube bank (~40 ft tubes) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 50 | 97
K-I-0055 | K | Fuel supply (adjacent market) | Discrete device to JB JB-H2 27: storage tub-DI01: 12 x 1 pr (field cables) |  | H2 27: storage tube bank (~40 ft tubes) | JB-H2 27: storage tub-DI01 | H2 27: storage tube bank (~40 ft tubes) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0056 | K | Fuel supply (adjacent market) | Home run JB-H2 27: storage tub-DI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 27: storage tub-DI01 | H2 27: storage tube bank (~40 ft tubes) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 50 | 97
K-I-0057 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-H2 27: storage tub-AI01: 12 x 1 pr (field cables) |  | H2 27: storage tube bank (~40 ft tubes) | JB-H2 27: storage tub-AI01 | H2 27: storage tube bank (~40 ft tubes) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0058 | K | Fuel supply (adjacent market) | Home run JB-H2 27: storage tub-AI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 27: storage tub-AI01 | H2 27: storage tube bank (~40 ft tubes) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 50 | 117
K-I-0059 | K | Fuel supply (adjacent market) | Discrete device to JB JB-H2 27: storage tub-DI01: 12 x 1 pr (field cables) |  | H2 27: storage tube bank (~40 ft tubes) | JB-H2 27: storage tub-DI01 | H2 27: storage tube bank (~40 ft tubes) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0060 | K | Fuel supply (adjacent market) | Home run JB-H2 27: storage tub-DI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 27: storage tub-DI01 | H2 27: storage tube bank (~40 ft tubes) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 50 | 117
K-I-0061 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-H2 27: storage tub-AI01: 12 x 1 pr (field cables) |  | H2 27: storage tube bank (~40 ft tubes) | JB-H2 27: storage tub-AI01 | H2 27: storage tube bank (~40 ft tubes) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0062 | K | Fuel supply (adjacent market) | Home run JB-H2 27: storage tub-AI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 27: storage tub-AI01 | H2 27: storage tube bank (~40 ft tubes) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 50 | 97
K-I-0063 | K | Fuel supply (adjacent market) | Discrete device to JB JB-H2 27: storage tub-DI01: 12 x 1 pr (field cables) |  | H2 27: storage tube bank (~40 ft tubes) | JB-H2 27: storage tub-DI01 | H2 27: storage tube bank (~40 ft tubes) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0064 | K | Fuel supply (adjacent market) | Home run JB-H2 27: storage tub-DI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 27: storage tub-DI01 | H2 27: storage tube bank (~40 ft tubes) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 50 | 97
K-I-0065 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-H2 27: storage tub-AI01: 12 x 1 pr (field cables) |  | H2 27: storage tube bank (~40 ft tubes) | JB-H2 27: storage tub-AI01 | H2 27: storage tube bank (~40 ft tubes) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0066 | K | Fuel supply (adjacent market) | Home run JB-H2 27: storage tub-AI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 27: storage tub-AI01 | H2 27: storage tube bank (~40 ft tubes) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 50 | 117
K-I-0067 | K | Fuel supply (adjacent market) | Discrete device to JB JB-H2 27: storage tub-DI01: 12 x 1 pr (field cables) |  | H2 27: storage tube bank (~40 ft tubes) | JB-H2 27: storage tub-DI01 | H2 27: storage tube bank (~40 ft tubes) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0068 | K | Fuel supply (adjacent market) | Home run JB-H2 27: storage tub-DI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 27: storage tub-DI01 | H2 27: storage tube bank (~40 ft tubes) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 50 | 117
K-I-0069 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-H2 28: N2 purge su-AI01: 12 x 1 pr (field cables) |  | H2 28: N2 purge supply | JB-H2 28: N2 purge su-AI01 | H2 28: N2 purge supply | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 56 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0070 | K | Fuel supply (adjacent market) | Home run JB-H2 28: N2 purge su-AI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 28: N2 purge su-AI01 | H2 28: N2 purge supply | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 53 | 36
K-I-0071 | K | Fuel supply (adjacent market) | Discrete device to JB JB-H2 28: N2 purge su-DI01: 12 x 1 pr (field cables) |  | H2 28: N2 purge supply | JB-H2 28: N2 purge su-DI01 | H2 28: N2 purge supply | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 56 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0072 | K | Fuel supply (adjacent market) | Home run JB-H2 28: N2 purge su-DI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 28: N2 purge su-DI01 | H2 28: N2 purge supply | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 53 | 36
K-I-0073 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-H2 29: vent stack-AI01: 12 x 1 pr (field cables) |  | H2 29: vent stack | JB-H2 29: vent stack-AI01 | H2 29: vent stack | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0074 | K | Fuel supply (adjacent market) | Home run JB-H2 29: vent stack-AI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 29: vent stack-AI01 | H2 29: vent stack | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 55 | 205
K-I-0075 | K | Fuel supply (adjacent market) | Discrete device to JB JB-H2 29: vent stack-DI01: 12 x 1 pr (field cables) |  | H2 29: vent stack | JB-H2 29: vent stack-DI01 | H2 29: vent stack | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 45 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0076 | K | Fuel supply (adjacent market) | Home run JB-H2 29: vent stack-DI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 29: vent stack-DI01 | H2 29: vent stack | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 55 | 205
K-I-0077 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-H2 30: H2 / gas bl-AI01: 12 x 1 pr (field cables) |  | H2 30: H2 / gas blending station (plant gas yard) | JB-H2 30: H2 / gas bl-AI01 | H2 30: H2 / gas blending station (plant gas yard) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 129 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0078 | K | Fuel supply (adjacent market) | Home run JB-H2 30: H2 / gas bl-AI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-H2 30: H2 / gas bl-AI01 | H2 30: H2 / gas blending station (plant gas yard) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 994 | 114
K-I-0079 | K | Fuel supply (adjacent market) | Discrete device to JB JB-H2 30: H2 / gas bl-DI01: 12 x 1 pr (field cables) |  | H2 30: H2 / gas blending station (plant gas yard) | JB-H2 30: H2 / gas bl-DI01 | H2 30: H2 / gas blending station (plant gas yard) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 129 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0080 | K | Fuel supply (adjacent market) | Home run JB-H2 30: H2 / gas bl-DI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-H2 30: H2 / gas bl-DI01 | H2 30: H2 / gas blending station (plant gas yard) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 994 | 114
K-I-0081 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-H2 pipe track and -AI01: 10 x 1 pr (field cables) |  | H2 pipe track and cable trench, hall -> dryer / compressors (N2, instr | JB-H2 pipe track and -AI01 | H2 pipe track and cable trench, hall -> dryer / compressors (N2, instr | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 70 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0082 | K | Fuel supply (adjacent market) | Home run JB-H2 pipe track and -AI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 pipe track and -AI01 | H2 pipe track and cable trench, hall -> dryer / compressors (N2, instr | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 53 | 62
K-I-0083 | K | Fuel supply (adjacent market) | Discrete device to JB JB-H2 pipe track and -DI01: 10 x 1 pr (field cables) |  | H2 pipe track and cable trench, hall -> dryer / compressors (N2, instr | JB-H2 pipe track and -DI01 | H2 pipe track and cable trench, hall -> dryer / compressors (N2, instr | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 70 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0084 | K | Fuel supply (adjacent market) | Home run JB-H2 pipe track and -DI01 to the control / marshalling room |  | H2 20: 13.8 kV e-house | JB-H2 pipe track and -DI01 | H2 pipe track and cable trench, hall -> dryer / compressors (N2, instr | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 53 | 62
K-I-0085 | K | Fuel supply (adjacent market) | Instrumentation |  | H2 20: 13.8 kV e-house | H2-ST | H2 storage tube banks x4 | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Duct bank | 50 | 92
K-I-0086 | K | Fuel supply (adjacent market) | Instrumentation |  | H2 20: 13.8 kV e-house | H2R | H2R: hydrogen pipeline receiving station (pig receiver, filters, meter | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Duct bank | 40 | 32
K-I-0087 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-LNG 10: truck unlo-AI01: 12 x 1 pr (field cables) |  | LNG 10: truck unloading bay 1 | JB-LNG 10: truck unlo-AI01 | LNG 10: truck unloading bay 1 | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0088 | K | Fuel supply (adjacent market) | Home run JB-LNG 10: truck unlo-AI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 10: truck unlo-AI01 | LNG 10: truck unloading bay 1 | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 237 | 61
K-I-0089 | K | Fuel supply (adjacent market) | Discrete device to JB JB-LNG 10: truck unlo-DI01: 12 x 1 pr (field cables) |  | LNG 10: truck unloading bay 1 | JB-LNG 10: truck unlo-DI01 | LNG 10: truck unloading bay 1 | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0090 | K | Fuel supply (adjacent market) | Home run JB-LNG 10: truck unlo-DI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 10: truck unlo-DI01 | LNG 10: truck unloading bay 1 | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 237 | 61
K-I-0091 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-LNG 10: truck unlo-AI01: 12 x 1 pr (field cables) |  | LNG 10: truck unloading bay 2 | JB-LNG 10: truck unlo-AI01 | LNG 10: truck unloading bay 2 | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0092 | K | Fuel supply (adjacent market) | Home run JB-LNG 10: truck unlo-AI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 10: truck unlo-AI01 | LNG 10: truck unloading bay 2 | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 147 | 66
K-I-0093 | K | Fuel supply (adjacent market) | Discrete device to JB JB-LNG 10: truck unlo-DI01: 12 x 1 pr (field cables) |  | LNG 10: truck unloading bay 2 | JB-LNG 10: truck unlo-DI01 | LNG 10: truck unloading bay 2 | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 72 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0094 | K | Fuel supply (adjacent market) | Home run JB-LNG 10: truck unlo-DI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 10: truck unlo-DI01 | LNG 10: truck unloading bay 2 | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 147 | 66
K-I-0095 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-LNG 10: unloading -AI01: 12 x 1 pr (field cables) |  | LNG 10: unloading skid | JB-LNG 10: unloading -AI01 | LNG 10: unloading skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0096 | K | Fuel supply (adjacent market) | Home run JB-LNG 10: unloading -AI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 10: unloading -AI01 | LNG 10: unloading skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 237 | 32
K-I-0097 | K | Fuel supply (adjacent market) | Discrete device to JB JB-LNG 10: unloading -DI01: 12 x 1 pr (field cables) |  | LNG 10: unloading skid | JB-LNG 10: unloading -DI01 | LNG 10: unloading skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 54 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0098 | K | Fuel supply (adjacent market) | Home run JB-LNG 10: unloading -DI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 10: unloading -DI01 | LNG 10: unloading skid | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 237 | 32
K-I-0099 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-LNG-T1-AI01: 4 x 1 pr (field cables) | LNG-T1 | LNG 11: tank 1, Chart HS 50000 (51,780 gal) | JB-LNG-T1-AI01 | LNG 11: tank 1, Chart HS 50000 (51,780 gal) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 77 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0100 | K | Fuel supply (adjacent market) | Home run JB-LNG-T1-AI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG-T1-AI01 | LNG 11: tank 1, Chart HS 50000 (51,780 gal) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 210 | 32
K-I-0101 | K | Fuel supply (adjacent market) | Discrete device to JB JB-LNG-T1-DI01: 4 x 1 pr (field cables) | LNG-T1 | LNG 11: tank 1, Chart HS 50000 (51,780 gal) | JB-LNG-T1-DI01 | LNG 11: tank 1, Chart HS 50000 (51,780 gal) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 77 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0102 | K | Fuel supply (adjacent market) | Home run JB-LNG-T1-DI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG-T1-DI01 | LNG 11: tank 1, Chart HS 50000 (51,780 gal) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 210 | 32
K-I-0103 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-LNG-T2-AI01: 4 x 1 pr (field cables) | LNG-T2 | LNG 11: tank 2, Chart HS 50000 (51,780 gal) | JB-LNG-T2-AI01 | LNG 11: tank 2, Chart HS 50000 (51,780 gal) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 77 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0104 | K | Fuel supply (adjacent market) | Home run JB-LNG-T2-AI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG-T2-AI01 | LNG 11: tank 2, Chart HS 50000 (51,780 gal) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 230 | 32
K-I-0105 | K | Fuel supply (adjacent market) | Discrete device to JB JB-LNG-T2-DI01: 4 x 1 pr (field cables) | LNG-T2 | LNG 11: tank 2, Chart HS 50000 (51,780 gal) | JB-LNG-T2-DI01 | LNG 11: tank 2, Chart HS 50000 (51,780 gal) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 77 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0106 | K | Fuel supply (adjacent market) | Home run JB-LNG-T2-DI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG-T2-DI01 | LNG 11: tank 2, Chart HS 50000 (51,780 gal) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 230 | 32
K-I-0107 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-LNG-T3-AI01: 4 x 1 pr (field cables) | LNG-T3 | LNG 11: tank 3, Chart HS 50000 (51,780 gal) | JB-LNG-T3-AI01 | LNG 11: tank 3, Chart HS 50000 (51,780 gal) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 77 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0108 | K | Fuel supply (adjacent market) | Home run JB-LNG-T3-AI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG-T3-AI01 | LNG 11: tank 3, Chart HS 50000 (51,780 gal) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 250 | 32
K-I-0109 | K | Fuel supply (adjacent market) | Discrete device to JB JB-LNG-T3-DI01: 4 x 1 pr (field cables) | LNG-T3 | LNG 11: tank 3, Chart HS 50000 (51,780 gal) | JB-LNG-T3-DI01 | LNG 11: tank 3, Chart HS 50000 (51,780 gal) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 77 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0110 | K | Fuel supply (adjacent market) | Home run JB-LNG-T3-DI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG-T3-DI01 | LNG 11: tank 3, Chart HS 50000 (51,780 gal) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 250 | 32
K-I-0111 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-LNG-T4-AI01: 4 x 1 pr (field cables) | LNG-T4 | LNG 11: tank 4, Chart HS 50000 (51,780 gal) | JB-LNG-T4-AI01 | LNG 11: tank 4, Chart HS 50000 (51,780 gal) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 77 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0112 | K | Fuel supply (adjacent market) | Home run JB-LNG-T4-AI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG-T4-AI01 | LNG 11: tank 4, Chart HS 50000 (51,780 gal) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 270 | 32
K-I-0113 | K | Fuel supply (adjacent market) | Discrete device to JB JB-LNG-T4-DI01: 4 x 1 pr (field cables) | LNG-T4 | LNG 11: tank 4, Chart HS 50000 (51,780 gal) | JB-LNG-T4-DI01 | LNG 11: tank 4, Chart HS 50000 (51,780 gal) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 77 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0114 | K | Fuel supply (adjacent market) | Home run JB-LNG-T4-DI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG-T4-DI01 | LNG 11: tank 4, Chart HS 50000 (51,780 gal) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 270 | 32
K-I-0115 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-LNG-T5-AI01: 4 x 1 pr (field cables) | LNG-T5 | LNG 11: tank 5, Chart HS 50000 (51,780 gal) | JB-LNG-T5-AI01 | LNG 11: tank 5, Chart HS 50000 (51,780 gal) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 77 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0116 | K | Fuel supply (adjacent market) | Home run JB-LNG-T5-AI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG-T5-AI01 | LNG 11: tank 5, Chart HS 50000 (51,780 gal) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 290 | 32
K-I-0117 | K | Fuel supply (adjacent market) | Discrete device to JB JB-LNG-T5-DI01: 4 x 1 pr (field cables) | LNG-T5 | LNG 11: tank 5, Chart HS 50000 (51,780 gal) | JB-LNG-T5-DI01 | LNG 11: tank 5, Chart HS 50000 (51,780 gal) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 77 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0118 | K | Fuel supply (adjacent market) | Home run JB-LNG-T5-DI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG-T5-DI01 | LNG 11: tank 5, Chart HS 50000 (51,780 gal) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 290 | 32
K-I-0119 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-LNG-T6-AI01: 4 x 1 pr (field cables) | LNG-T6 | LNG 11: tank 6, Chart HS 50000 (51,780 gal) | JB-LNG-T6-AI01 | LNG 11: tank 6, Chart HS 50000 (51,780 gal) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 77 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0120 | K | Fuel supply (adjacent market) | Home run JB-LNG-T6-AI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG-T6-AI01 | LNG 11: tank 6, Chart HS 50000 (51,780 gal) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 310 | 32
K-I-0121 | K | Fuel supply (adjacent market) | Discrete device to JB JB-LNG-T6-DI01: 4 x 1 pr (field cables) | LNG-T6 | LNG 11: tank 6, Chart HS 50000 (51,780 gal) | JB-LNG-T6-DI01 | LNG 11: tank 6, Chart HS 50000 (51,780 gal) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 77 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0122 | K | Fuel supply (adjacent market) | Home run JB-LNG-T6-DI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG-T6-DI01 | LNG 11: tank 6, Chart HS 50000 (51,780 gal) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 310 | 32
K-I-0123 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-LNG-T7-AI01: 4 x 1 pr (field cables) | LNG-T7 | LNG 11: tank 7, Chart HS 50000 (51,780 gal) | JB-LNG-T7-AI01 | LNG 11: tank 7, Chart HS 50000 (51,780 gal) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 77 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0124 | K | Fuel supply (adjacent market) | Home run JB-LNG-T7-AI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG-T7-AI01 | LNG 11: tank 7, Chart HS 50000 (51,780 gal) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 330 | 32
K-I-0125 | K | Fuel supply (adjacent market) | Discrete device to JB JB-LNG-T7-DI01: 4 x 1 pr (field cables) | LNG-T7 | LNG 11: tank 7, Chart HS 50000 (51,780 gal) | JB-LNG-T7-DI01 | LNG 11: tank 7, Chart HS 50000 (51,780 gal) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 77 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0126 | K | Fuel supply (adjacent market) | Home run JB-LNG-T7-DI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG-T7-DI01 | LNG 11: tank 7, Chart HS 50000 (51,780 gal) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 330 | 32
K-I-0127 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-LNG-T8-AI01: 4 x 1 pr (field cables) | LNG-T8 | LNG 11: tank 8, Chart HS 50000 (51,780 gal) | JB-LNG-T8-AI01 | LNG 11: tank 8, Chart HS 50000 (51,780 gal) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 77 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0128 | K | Fuel supply (adjacent market) | Home run JB-LNG-T8-AI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG-T8-AI01 | LNG 11: tank 8, Chart HS 50000 (51,780 gal) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 350 | 32
K-I-0129 | K | Fuel supply (adjacent market) | Discrete device to JB JB-LNG-T8-DI01: 4 x 1 pr (field cables) | LNG-T8 | LNG 11: tank 8, Chart HS 50000 (51,780 gal) | JB-LNG-T8-DI01 | LNG 11: tank 8, Chart HS 50000 (51,780 gal) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 77 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0130 | K | Fuel supply (adjacent market) | Home run JB-LNG-T8-DI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG-T8-DI01 | LNG 11: tank 8, Chart HS 50000 (51,780 gal) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 350 | 32
K-I-0131 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-LNG 12: spill impo-AI01: 12 x 1 pr (field cables) |  | LNG 12: spill impoundment (NFPA 59A, to verify) | JB-LNG 12: spill impo-AI01 | LNG 12: spill impoundment (NFPA 59A, to verify) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 170 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0132 | K | Fuel supply (adjacent market) | Home run JB-LNG 12: spill impo-AI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 12: spill impo-AI01 | LNG 12: spill impoundment (NFPA 59A, to verify) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 230 | 32
K-I-0133 | K | Fuel supply (adjacent market) | Discrete device to JB JB-LNG 12: spill impo-DI01: 12 x 1 pr (field cables) |  | LNG 12: spill impoundment (NFPA 59A, to verify) | JB-LNG 12: spill impo-DI01 | LNG 12: spill impoundment (NFPA 59A, to verify) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 170 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0134 | K | Fuel supply (adjacent market) | Home run JB-LNG 12: spill impo-DI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 12: spill impo-DI01 | LNG 12: spill impoundment (NFPA 59A, to verify) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 230 | 32
K-I-0135 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-LNG 13: send-out p-AI01: 12 x 1 pr (field cables) |  | LNG 13: send-out pumps 2 x 100% | JB-LNG 13: send-out p-AI01 | LNG 13: send-out pumps 2 x 100% | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 63 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0136 | K | Fuel supply (adjacent market) | Home run JB-LNG 13: send-out p-AI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 13: send-out p-AI01 | LNG 13: send-out pumps 2 x 100% | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 110 | 32
K-I-0137 | K | Fuel supply (adjacent market) | Discrete device to JB JB-LNG 13: send-out p-DI01: 12 x 1 pr (field cables) |  | LNG 13: send-out pumps 2 x 100% | JB-LNG 13: send-out p-DI01 | LNG 13: send-out pumps 2 x 100% | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 63 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0138 | K | Fuel supply (adjacent market) | Home run JB-LNG 13: send-out p-DI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 13: send-out p-DI01 | LNG 13: send-out pumps 2 x 100% | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 110 | 32
K-I-0139 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-LNG 14: vaporizers-AI01: 12 x 1 pr (field cables) |  | LNG 14: vaporizers + glycol heater | JB-LNG 14: vaporizers-AI01 | LNG 14: vaporizers + glycol heater | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 122 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0140 | K | Fuel supply (adjacent market) | Home run JB-LNG 14: vaporizers-AI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 14: vaporizers-AI01 | LNG 14: vaporizers + glycol heater | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 259 | 32
K-I-0141 | K | Fuel supply (adjacent market) | Discrete device to JB JB-LNG 14: vaporizers-DI01: 12 x 1 pr (field cables) |  | LNG 14: vaporizers + glycol heater | JB-LNG 14: vaporizers-DI01 | LNG 14: vaporizers + glycol heater | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 122 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0142 | K | Fuel supply (adjacent market) | Home run JB-LNG 14: vaporizers-DI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 14: vaporizers-DI01 | LNG 14: vaporizers + glycol heater | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 259 | 32
K-I-0143 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-LNG 15: boil-off g-AI01: 12 x 1 pr (field cables) |  | LNG 15: boil-off gas compressor | JB-LNG 15: boil-off g-AI01 | LNG 15: boil-off gas compressor | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 67 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0144 | K | Fuel supply (adjacent market) | Home run JB-LNG 15: boil-off g-AI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 15: boil-off g-AI01 | LNG 15: boil-off gas compressor | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 25 | 54
K-I-0145 | K | Fuel supply (adjacent market) | Discrete device to JB JB-LNG 15: boil-off g-DI01: 12 x 1 pr (field cables) |  | LNG 15: boil-off gas compressor | JB-LNG 15: boil-off g-DI01 | LNG 15: boil-off gas compressor | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 67 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0146 | K | Fuel supply (adjacent market) | Home run JB-LNG 15: boil-off g-DI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 15: boil-off g-DI01 | LNG 15: boil-off gas compressor | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 25 | 54
K-I-0147 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-LNG 16: send-out m-AI01: 12 x 1 pr (field cables) |  | LNG 16: send-out metering + pressure control | JB-LNG 16: send-out m-AI01 | LNG 16: send-out metering + pressure control | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 74 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0148 | K | Fuel supply (adjacent market) | Home run JB-LNG 16: send-out m-AI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 16: send-out m-AI01 | LNG 16: send-out metering + pressure control | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 20 | 32
K-I-0149 | K | Fuel supply (adjacent market) | Discrete device to JB JB-LNG 16: send-out m-DI01: 12 x 1 pr (field cables) |  | LNG 16: send-out metering + pressure control | JB-LNG 16: send-out m-DI01 | LNG 16: send-out metering + pressure control | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 74 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0150 | K | Fuel supply (adjacent market) | Home run JB-LNG 16: send-out m-DI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 16: send-out m-DI01 | LNG 16: send-out metering + pressure control | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 20 | 32
K-I-0151 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-LNG 17: LNG e-hous-AI01: 12 x 1 pr (field cables) |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 17: LNG e-hous-AI01 | LNG 17: LNG e-house (13.8 kV / 480 V) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 58 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0152 | K | Fuel supply (adjacent market) | Home run JB-LNG 17: LNG e-hous-AI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 17: LNG e-hous-AI01 | LNG 17: LNG e-house (13.8 kV / 480 V) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 32
K-I-0153 | K | Fuel supply (adjacent market) | Discrete device to JB JB-LNG 17: LNG e-hous-DI01: 12 x 1 pr (field cables) |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 17: LNG e-hous-DI01 | LNG 17: LNG e-house (13.8 kV / 480 V) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 58 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0154 | K | Fuel supply (adjacent market) | Home run JB-LNG 17: LNG e-hous-DI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 17: LNG e-hous-DI01 | LNG 17: LNG e-house (13.8 kV / 480 V) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 0 | 32
K-I-0155 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-LNG 18: vent stack-AI01: 12 x 1 pr (field cables) |  | LNG 18: vent stack | JB-LNG 18: vent stack-AI01 | LNG 18: vent stack | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 55 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0156 | K | Fuel supply (adjacent market) | Home run JB-LNG 18: vent stack-AI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 18: vent stack-AI01 | LNG 18: vent stack | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 25 | 117
K-I-0157 | K | Fuel supply (adjacent market) | Discrete device to JB JB-LNG 18: vent stack-DI01: 12 x 1 pr (field cables) |  | LNG 18: vent stack | JB-LNG 18: vent stack-DI01 | LNG 18: vent stack | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 55 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0158 | K | Fuel supply (adjacent market) | Home run JB-LNG 18: vent stack-DI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-LNG 18: vent stack-DI01 | LNG 18: vent stack | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 25 | 117
K-I-0159 | K | Fuel supply (adjacent market) | Instrumentation |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | LNG impoundment sump pump | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Duct bank | 334 | 32
K-I-0160 | K | Fuel supply (adjacent market) | Instrumentation |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | M&R 1: pig receiver, lateral terminus | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Duct bank | 773 | 37
K-I-0161 | K | Fuel supply (adjacent market) | Discrete device to JB JB-M&R 2: insulating -DI01: 8 x 1 pr (field cables) |  | M&R 2: insulating joint + ESD valve | JB-M&R 2: insulating -DI01 | M&R 2: insulating joint + ESD valve | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 40 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0162 | K | Fuel supply (adjacent market) | Home run JB-M&R 2: insulating -DI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-M&R 2: insulating -DI01 | M&R 2: insulating joint + ESD valve | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 758 | 32
K-I-0163 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-M&R 3: horizontal -AI01: 8 x 1 pr (field cables) |  | M&R 3: horizontal filter-separator | JB-M&R 3: horizontal -AI01 | M&R 3: horizontal filter-separator | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0164 | K | Fuel supply (adjacent market) | Home run JB-M&R 3: horizontal -AI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-M&R 3: horizontal -AI01 | M&R 3: horizontal filter-separator | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 797 | 32
K-I-0165 | K | Fuel supply (adjacent market) | Discrete device to JB JB-M&R 3: horizontal -DI01: 12 x 1 pr (field cables) |  | M&R 3: horizontal filter-separator | JB-M&R 3: horizontal -DI01 | M&R 3: horizontal filter-separator | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 53 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0166 | K | Fuel supply (adjacent market) | Home run JB-M&R 3: horizontal -DI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-M&R 3: horizontal -DI01 | M&R 3: horizontal filter-separator | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 797 | 32
K-I-0167 | K | Fuel supply (adjacent market) | Instrumentation |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | M&R 4: line heater 1 (water bath) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Duct bank | 593 | 32
K-I-0168 | K | Fuel supply (adjacent market) | Instrumentation |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | M&R 4: line heater 1 (water bath) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Duct bank | 593 | 32
K-I-0169 | K | Fuel supply (adjacent market) | Instrumentation |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | M&R 4: line heater 2 (water bath) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Duct bank | 593 | 50
K-I-0170 | K | Fuel supply (adjacent market) | Instrumentation |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | M&R 4: line heater 2 (water bath) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Duct bank | 593 | 50
K-I-0171 | K | Fuel supply (adjacent market) | Instrumentation |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | M&R 4: line heater 3 (water bath) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Duct bank | 593 | 68
K-I-0172 | K | Fuel supply (adjacent market) | Instrumentation |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | M&R 4: line heater 3 (water bath) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦12 pr¦18 | 12 pr | 18 | 1 | 1 |  |  |  | Duct bank | 593 | 68
K-I-0173 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-M&R 5: ultrasonic -AI01: 20 x 1 pr (field cables) |  | M&R 5: ultrasonic meters, 2 runs (custody transfer) | JB-M&R 5: ultrasonic -AI01 | M&R 5: ultrasonic meters, 2 runs (custody transfer) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 60 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0174 | K | Fuel supply (adjacent market) | Home run JB-M&R 5: ultrasonic -AI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-M&R 5: ultrasonic -AI01 | M&R 5: ultrasonic meters, 2 runs (custody transfer) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 651 | 57
K-I-0175 | K | Fuel supply (adjacent market) | Discrete device to JB JB-M&R 5: ultrasonic -DI01: 8 x 1 pr (field cables) |  | M&R 5: ultrasonic meters, 2 runs (custody transfer) | JB-M&R 5: ultrasonic -DI01 | M&R 5: ultrasonic meters, 2 runs (custody transfer) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 60 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0176 | K | Fuel supply (adjacent market) | Home run JB-M&R 5: ultrasonic -DI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-M&R 5: ultrasonic -DI01 | M&R 5: ultrasonic meters, 2 runs (custody transfer) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 651 | 57
K-I-0177 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-M&R 6: regulation -AI01: 12 x 1 pr (field cables) |  | M&R 6: regulation / flow control building | JB-M&R 6: regulation -AI01 | M&R 6: regulation / flow control building | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 61 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0178 | K | Fuel supply (adjacent market) | Home run JB-M&R 6: regulation -AI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-M&R 6: regulation -AI01 | M&R 6: regulation / flow control building | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 470 | 70
K-I-0179 | K | Fuel supply (adjacent market) | Discrete device to JB JB-M&R 6: regulation -DI01: 12 x 1 pr (field cables) |  | M&R 6: regulation / flow control building | JB-M&R 6: regulation -DI01 | M&R 6: regulation / flow control building | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 12 | 1 |  |  |  | Tray / conduit | 61 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0180 | K | Fuel supply (adjacent market) | Home run JB-M&R 6: regulation -DI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-M&R 6: regulation -DI01 | M&R 6: regulation / flow control building | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 470 | 70
K-I-0181 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-M&R 7: gas quality-AI01: 20 x 1 pr (field cables) |  | M&R 7: gas quality + measurement building | JB-M&R 7: gas quality-AI01 | M&R 7: gas quality + measurement building | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 20 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0182 | K | Fuel supply (adjacent market) | Home run JB-M&R 7: gas quality-AI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-M&R 7: gas quality-AI01 | M&R 7: gas quality + measurement building | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 616 | 52
K-I-0183 | K | Fuel supply (adjacent market) | Discrete device to JB JB-M&R 7: gas quality-DI01: 8 x 1 pr (field cables) |  | M&R 7: gas quality + measurement building | JB-M&R 7: gas quality-DI01 | M&R 7: gas quality + measurement building | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 8 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0184 | K | Fuel supply (adjacent market) | Home run JB-M&R 7: gas quality-DI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-M&R 7: gas quality-DI01 | M&R 7: gas quality + measurement building | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 616 | 52
K-I-0185 | K | Fuel supply (adjacent market) | Analog instrument to JB JB-M&R 8: condensate -AI01: 4 x 1 pr (field cables) |  | M&R 8: condensate tank | JB-M&R 8: condensate -AI01 | M&R 8: condensate tank | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0186 | K | Fuel supply (adjacent market) | Home run JB-M&R 8: condensate -AI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-M&R 8: condensate -AI01 | M&R 8: condensate tank | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 530 | 87
K-I-0187 | K | Fuel supply (adjacent market) | Discrete device to JB JB-M&R 8: condensate -DI01: 4 x 1 pr (field cables) |  | M&R 8: condensate tank | JB-M&R 8: condensate -DI01 | M&R 8: condensate tank | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦1 pr¦16 | 1 pr | 16 | 4 | 1 |  |  |  | Tray / conduit | 41 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
K-I-0188 | K | Fuel supply (adjacent market) | Home run JB-M&R 8: condensate -DI01 to the control / marshalling room |  | LNG 17: LNG e-house (13.8 kV / 480 V) | JB-M&R 8: condensate -DI01 | M&R 8: condensate tank | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Duct bank | 530 | 87
K-I-0189 | K | Fuel supply (adjacent market) | Instrumentation |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | M&R CP test station (as drawn) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Duct bank | 441 | 42
K-I-0190 | K | Fuel supply (adjacent market) | Instrumentation |  | H2 20: 13.8 kV e-house |  | PEM electrolyzer 1 (HyLYZER-1000) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Duct bank | 358 | 32
K-I-0191 | K | Fuel supply (adjacent market) | Instrumentation |  | H2 20: 13.8 kV e-house |  | PEM electrolyzer 2 (HyLYZER-1000) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Duct bank | 358 | 48
K-I-0192 | K | Fuel supply (adjacent market) | Instrumentation |  | H2 20: 13.8 kV e-house |  | PEM electrolyzer 3 (HyLYZER-1000) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Duct bank | 348 | 49
K-I-0193 | K | Fuel supply (adjacent market) | Instrumentation |  | H2 20: 13.8 kV e-house |  | PEM electrolyzer 4 (HyLYZER-1000) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Duct bank | 328 | 49
K-I-0194 | K | Fuel supply (adjacent market) | Instrumentation |  | H2 20: 13.8 kV e-house |  | PEM electrolyzer 5 (HyLYZER-1000) | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | ITC¦4 pr¦18 | 4 pr | 18 | 1 | 1 |  |  |  | Duct bank | 328 | 32
K-P-0001 | K | Fuel supply (adjacent market) | Motor 1 of 1, 15 kW |  | H2 20: 13.8 kV e-house | T-H2 | H2 19: T-H2 230/13.8 kV (about 40 MVA) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 35 | 32 |  |  |  |  | VD 0.7 %
K-P-0002 | K | Fuel supply (adjacent market) | Motor 1 of 1, 15 kW |  | H2 20: 13.8 kV e-house |  | H2 20: 13.8 kV e-house | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Tray | 0 | 32 |  |  |  |  | VD 0.3 %
K-P-0003 | K | Fuel supply (adjacent market) | Motor 1 of 1, 15 kW |  | H2 20: 13.8 kV e-house |  | H2 21: rectifier transformer 1 (7 MVA) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 356 | 48 |  |  |  |  | VD 2.6 %
K-P-0004 | K | Fuel supply (adjacent market) | Motor 1 of 1, 15 kW |  | H2 20: 13.8 kV e-house |  | H2 21: rectifier transformer 2 (7 MVA) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 356 | 32 |  |  |  |  | VD 2.5 %
K-P-0005 | K | Fuel supply (adjacent market) | Motor 1 of 1, 15 kW |  | H2 20: 13.8 kV e-house |  | H2 21: rectifier transformer 3 (7 MVA) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 334 | 32 |  |  |  |  | VD 2.4 %
K-P-0006 | K | Fuel supply (adjacent market) | Motor 1 of 1, 15 kW |  | H2 20: 13.8 kV e-house |  | H2 21: rectifier transformer 4 (7 MVA) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 312 | 32 |  |  |  |  | VD 2.2 %
K-P-0007 | K | Fuel supply (adjacent market) | Motor 1 of 1, 15 kW |  | H2 20: 13.8 kV e-house |  | H2 21: rectifier transformer 5 (7 MVA) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 254 | 32 |  |  |  |  | VD 2.9 %
K-P-0008 | K | Fuel supply (adjacent market) | Motor 1 of 1, 15 kW |  | H2 20: 13.8 kV e-house | H2-EL | H2 22: electrolyzer building (5 x HyLYZER-1000 + 5 rectifiers) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 346 | 32 |  |  |  |  | VD 2.4 %
K-P-0009 | K | Fuel supply (adjacent market) | Motor 1 of 1, 15 kW |  | H2 20: 13.8 kV e-house |  | H2 23: dry coolers | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 100 | 32 |  |  |  |  | VD 1.3 %
K-P-0010 | K | Fuel supply (adjacent market) | Motor 1 of 1, 15 kW |  | H2 20: 13.8 kV e-house |  | H2 24: water purification (RO / EDI) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 146 | 32 |  |  |  |  | VD 1.8 %
K-P-0011 | K | Fuel supply (adjacent market) | Motor 1 of 1, 15 kW |  | H2 20: 13.8 kV e-house |  | H2 25: H2 dryer / purification | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 0 | 49 |  |  |  |  | VD 0.5 %
K-P-0012 | K | Fuel supply (adjacent market) | Motor 1 of 1, 15 kW |  | H2 20: 13.8 kV e-house |  | H2 26: H2 compressor 1 (40 ft ISO) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 50 | 32 |  |  |  |  | VD 0.8 %
K-P-0013 | K | Fuel supply (adjacent market) | Motor 1 of 1, 15 kW |  | H2 20: 13.8 kV e-house |  | H2 26: H2 compressor 2 (40 ft ISO) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 50 | 47 |  |  |  |  | VD 1.0 %
K-P-0014 | K | Fuel supply (adjacent market) | Motor 1 of 1, 15 kW |  | H2 20: 13.8 kV e-house |  | H2 27: storage tube bank (~40 ft tubes) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 50 | 97 |  |  |  |  | VD 1.5 %
K-P-0015 | K | Fuel supply (adjacent market) | Motor 1 of 1, 15 kW |  | H2 20: 13.8 kV e-house |  | H2 27: storage tube bank (~40 ft tubes) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 50 | 117 |  |  |  |  | VD 1.7 %
K-P-0016 | K | Fuel supply (adjacent market) | Motor 1 of 1, 15 kW |  | H2 20: 13.8 kV e-house |  | H2 27: storage tube bank (~40 ft tubes) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 50 | 97 |  |  |  |  | VD 1.5 %
K-P-0017 | K | Fuel supply (adjacent market) | Motor 1 of 1, 15 kW |  | H2 20: 13.8 kV e-house |  | H2 27: storage tube bank (~40 ft tubes) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 50 | 117 |  |  |  |  | VD 1.7 %
K-P-0018 | K | Fuel supply (adjacent market) | Motor 1 of 1, 15 kW |  | H2 20: 13.8 kV e-house |  | H2 28: N2 purge supply | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 53 | 36 |  |  |  |  | VD 0.9 %
K-P-0019 | K | Fuel supply (adjacent market) | Motor 1 of 1, 15 kW |  | H2 20: 13.8 kV e-house |  | H2 29: vent stack | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 55 | 205 |  |  |  |  | VD 2.7 %
K-P-0020 | K | Fuel supply (adjacent market) | Motor 1 of 1, 15 kW |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | H2 30: H2 / gas blending station (plant gas yard) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 994 | 114 |  |  |  |  | VD 2.9 %
K-P-0021 | K | Fuel supply (adjacent market) | Motor 1 of 2, 250 kW |  | H2 20: 13.8 kV e-house |  | H2 pipe track and cable trench, hall -> dryer / compressors (N2, instr | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦4/0 | 3/C+G | 4/0 | 2 | 1 | 480 | 250 | 353.8 | Duct bank | 53 | 62 |  |  |  |  | VD 0.5 %
K-P-0022 | K | Fuel supply (adjacent market) | Motor 2 of 2, 250 kW |  | H2 20: 13.8 kV e-house |  | H2 pipe track and cable trench, hall -> dryer / compressors (N2, instr | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦4/0 | 3/C+G | 4/0 | 2 | 1 | 480 | 250 | 353.8 | Duct bank | 53 | 62 |  |  |  |  | VD 0.5 %
K-P-0023 | K | Fuel supply (adjacent market) | LV power feeder |  | H2 20: 13.8 kV e-house | H2-ST | H2 storage tube banks x4 | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 50 | 92 |  |  |  |  | VD 1.4 %
K-P-0024 | K | Fuel supply (adjacent market) | LV power feeder |  | H2 20: 13.8 kV e-house | H2R | H2R: hydrogen pipeline receiving station (pig receiver, filters, meter | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 40 | 32 |  |  |  |  | VD 0.7 %
K-P-0025 | K | Fuel supply (adjacent market) | Motor 1 of 1, 15 kW |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | LNG 10: truck unloading bay 1 | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 237 | 61 |  |  |  |  | VD 1.9 %
K-P-0026 | K | Fuel supply (adjacent market) | Motor 1 of 1, 15 kW |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | LNG 10: truck unloading bay 2 | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 147 | 66 |  |  |  |  | VD 2.2 %
K-P-0027 | K | Fuel supply (adjacent market) | Motor 1 of 1, 15 kW |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | LNG 10: unloading skid | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 237 | 32 |  |  |  |  | VD 2.7 %
K-P-0028 | K | Fuel supply (adjacent market) | LV power feeder |  | LNG 17: LNG e-house (13.8 kV / 480 V) | LNG-T1 | LNG 11: tank 1, Chart HS 50000 (51,780 gal) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 10 | 14.2 | Duct bank | 210 | 32 |  |  |  |  | VD 1.6 %
K-P-0029 | K | Fuel supply (adjacent market) | LV power feeder |  | LNG 17: LNG e-house (13.8 kV / 480 V) | LNG-T2 | LNG 11: tank 2, Chart HS 50000 (51,780 gal) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 10 | 14.2 | Duct bank | 230 | 32 |  |  |  |  | VD 1.8 %
K-P-0030 | K | Fuel supply (adjacent market) | LV power feeder |  | LNG 17: LNG e-house (13.8 kV / 480 V) | LNG-T3 | LNG 11: tank 3, Chart HS 50000 (51,780 gal) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 10 | 14.2 | Duct bank | 250 | 32 |  |  |  |  | VD 1.9 %
K-P-0031 | K | Fuel supply (adjacent market) | LV power feeder |  | LNG 17: LNG e-house (13.8 kV / 480 V) | LNG-T4 | LNG 11: tank 4, Chart HS 50000 (51,780 gal) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 10 | 14.2 | Duct bank | 270 | 32 |  |  |  |  | VD 2.1 %
K-P-0032 | K | Fuel supply (adjacent market) | LV power feeder |  | LNG 17: LNG e-house (13.8 kV / 480 V) | LNG-T5 | LNG 11: tank 5, Chart HS 50000 (51,780 gal) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 10 | 14.2 | Duct bank | 290 | 32 |  |  |  |  | VD 2.2 %
K-P-0033 | K | Fuel supply (adjacent market) | LV power feeder |  | LNG 17: LNG e-house (13.8 kV / 480 V) | LNG-T6 | LNG 11: tank 6, Chart HS 50000 (51,780 gal) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 10 | 14.2 | Duct bank | 310 | 32 |  |  |  |  | VD 2.3 %
K-P-0034 | K | Fuel supply (adjacent market) | LV power feeder |  | LNG 17: LNG e-house (13.8 kV / 480 V) | LNG-T7 | LNG 11: tank 7, Chart HS 50000 (51,780 gal) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 10 | 14.2 | Duct bank | 330 | 32 |  |  |  |  | VD 2.5 %
K-P-0035 | K | Fuel supply (adjacent market) | LV power feeder |  | LNG 17: LNG e-house (13.8 kV / 480 V) | LNG-T8 | LNG 11: tank 8, Chart HS 50000 (51,780 gal) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 10 | 14.2 | Duct bank | 350 | 32 |  |  |  |  | VD 2.6 %
K-P-0036 | K | Fuel supply (adjacent market) | Motor 1 of 1, 15 kW |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | LNG 12: spill impoundment (NFPA 59A, to verify) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 230 | 32 |  |  |  |  | VD 2.7 %
K-P-0037 | K | Fuel supply (adjacent market) | Motor 1 of 1, 15 kW |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | LNG 13: send-out pumps 2 x 100% | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 110 | 32 |  |  |  |  | VD 1.4 %
K-P-0038 | K | Fuel supply (adjacent market) | Motor 1 of 1, 15 kW |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | LNG 14: vaporizers + glycol heater | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 259 | 32 |  |  |  |  | VD 3.0 %
K-P-0039 | K | Fuel supply (adjacent market) | Motor 1 of 1, 15 kW |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | LNG 15: boil-off gas compressor | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 25 | 54 |  |  |  |  | VD 0.8 %
K-P-0040 | K | Fuel supply (adjacent market) | Motor 1 of 1, 15 kW |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | LNG 16: send-out metering + pressure control | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 20 | 32 |  |  |  |  | VD 0.5 %
K-P-0041 | K | Fuel supply (adjacent market) | Motor 1 of 1, 15 kW |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | LNG 17: LNG e-house (13.8 kV / 480 V) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Tray | 0 | 32 |  |  |  |  | VD 0.3 %
K-P-0042 | K | Fuel supply (adjacent market) | Motor 1 of 1, 15 kW |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | LNG 18: vent stack | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦10 | 3/C+G | 10 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 25 | 117 |  |  |  |  | VD 1.4 %
K-P-0043 | K | Fuel supply (adjacent market) | LV power feeder |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | LNG impoundment sump pump | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 334 | 32 |  |  |  |  | VD 2.4 %
K-P-0044 | K | Fuel supply (adjacent market) | LV power feeder |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | M&R 2: insulating joint + ESD valve | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 10 | 14.2 | Duct bank | 758 | 32 |  |  |  |  | VD 2.2 %
K-P-0045 | K | Fuel supply (adjacent market) | LV power feeder |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | M&R 3: horizontal filter-separator | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦4 | 3/C+G | 4 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 797 | 32 |  |  |  |  | VD 2.2 %
K-P-0046 | K | Fuel supply (adjacent market) | LV power feeder |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | M&R 4: line heater 1 (water bath) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 593 | 32 |  |  |  |  | VD 2.6 %
K-P-0047 | K | Fuel supply (adjacent market) | LV power feeder |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | M&R 4: line heater 2 (water bath) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 593 | 50 |  |  |  |  | VD 2.7 %
K-P-0048 | K | Fuel supply (adjacent market) | LV power feeder |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | M&R 4: line heater 3 (water bath) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 593 | 68 |  |  |  |  | VD 2.7 %
K-P-0049 | K | Fuel supply (adjacent market) | LV panel / distribution feeder |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | M&R 6: regulation / flow control building | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 10 | 14.2 | Duct bank | 470 | 70 |  |  |  |  | VD 2.3 %
K-P-0050 | K | Fuel supply (adjacent market) | LV panel / distribution feeder |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | M&R 7: gas quality + measurement building | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦2 | 3/C+G | 2 | 1 | 1 | 480 | 30 | 42.5 | Duct bank | 616 | 52 |  |  |  |  | VD 2.2 %
K-P-0051 | K | Fuel supply (adjacent market) | LV power feeder |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | M&R 8: condensate tank | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 10 | 14.2 | Duct bank | 530 | 87 |  |  |  |  | VD 2.6 %
K-P-0052 | K | Fuel supply (adjacent market) | LV power feeder |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | M&R 9: service panel + UPS, SCADA RTU, CP | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 466 | 32 |  |  |  |  | VD 2.1 %
K-P-0053 | K | Fuel supply (adjacent market) | LV power feeder |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | M&R CP test station (as drawn) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦6 | 3/C+G | 6 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 441 | 42 |  |  |  |  | VD 2.0 %
K-P-0054 | K | Fuel supply (adjacent market) | LV power feeder |  | LNG 17: LNG e-house (13.8 kV / 480 V) |  | M&R SCADA antenna mast base (as drawn) | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | LVAX¦3/C+G¦8 | 3/C+G | 8 | 1 | 1 | 480 | 15 | 21.2 | Duct bank | 433 | 32 |  |  |  |  | VD 3.0 %
K-MV-0001 | K | Fuel supply (adjacent market) | H2 13.8 kV e-house (electrolyzers) | SWGR-13.8-3 | R1 SWGR-13.8-3 (11 x 36 in cubicles, 15 kV metal-clad) |  | H2 20: 13.8 kV e-house | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦750 | 1/C | 750 kcmil | 2 | 3 | 13800 | 20000 | 837 | HV duct bank | 4013 | 128
K-MV-0002 | K | Fuel supply (adjacent market) | LNG e-house | SWGR-13.8-3 | R1 SWGR-13.8-3 (11 x 36 in cubicles, 15 kV metal-clad) |  | LNG 17: LNG e-house (13.8 kV / 480 V) | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | MV15¦1/C¦4/0 | 1/C | 4/0 | 1 | 3 | 13800 | 5000 | 209 | Duct bank | 2649 | 219
C-C-0128 | C | Grid interface | Motor 1 of 2: control / local station | MCC-C1 | R1 MCC-C1 |  | Small-bore piping: instrument air, service water, nitrogen, HRSG drain | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 614 | 145
C-C-0129 | C | Grid interface | Motor 2 of 2: control / local station | MCC-C1 | R1 MCC-C1 |  | Small-bore piping: instrument air, service water, nitrogen, HRSG drain | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | CT¦7/C¦14 | 7/C | 14 | 1 | 1 |  |  |  | Tray | 614 | 145
C-I-0081 | C | Grid interface | Analog instrument to JB JB-Small-bore piping:-AI01: 10 x 1 pr (field cables) |  | Small-bore piping: instrument air, service water, nitrogen, HRSG drain | JB-Small-bore piping:-AI01 | Small-bore piping: instrument air, service water, nitrogen, HRSG drain | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 250 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0082 | C | Grid interface | Home run JB-Small-bore piping:-AI01 to the control / marshalling room | R1 | R1: main electrical building (64 x 180 ft) | JB-Small-bore piping:-AI01 | Small-bore piping: instrument air, service water, nitrogen, HRSG drain | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1218 | 200
C-I-0083 | C | Grid interface | Discrete device to JB JB-Small-bore piping:-DI01: 10 x 1 pr (field cables) |  | Small-bore piping: instrument air, service water, nitrogen, HRSG drain | JB-Small-bore piping:-DI01 | Small-bore piping: instrument air, service water, nitrogen, HRSG drain | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦1 pr¦16 | 1 pr | 16 | 10 | 1 |  |  |  | Tray / conduit | 250 | 10 |  |  |  |  | device-to-JB field wiring, one cable per device
C-I-0084 | C | Grid interface | Home run JB-Small-bore piping:-DI01 to the control / marshalling room | R1 | R1: main electrical building (64 x 180 ft) | JB-Small-bore piping:-DI01 | Small-bore piping: instrument air, service water, nitrogen, HRSG drain | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | PLTC¦24 pr¦18 | 24 pr | 18 | 1 | 1 |  |  |  | Tray | 1218 | 200
C-P-0006 | C | Grid interface | Motor 1 of 2, 250 kW | MCC-C1 | R1 MCC-C1 |  | Small-bore piping: instrument air, service water, nitrogen, HRSG drain | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦250 | 3/C+G | 250 kcmil | 2 | 1 | 480 | 250 | 353.8 | Tray | 614 | 145 |  |  |  |  | VD 2.7 %
C-P-0007 | C | Grid interface | Motor 2 of 2, 250 kW | MCC-C1 | R1 MCC-C1 |  | Small-bore piping: instrument air, service water, nitrogen, HRSG drain | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | LV¦3/C+G¦250 | 3/C+G | 250 kcmil | 2 | 1 | 480 | 250 | 353.8 | Tray | 614 | 145 |  |  |  |  | VD 2.7 %

## Cable BOM
Product key | Class | Product (typical Southwire family) | Conductors | Size | Cables | Total length (ft) | Waste | Order length (ft) | Standard reel (ft) | Reels | Order length (km)
MV15¦1/C¦2 | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | 1/C | 2 |  |  |  |  | 2500
MV15¦1/C¦1/0 | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | 1/C | 1/0 |  |  |  |  | 2500
MV15¦1/C¦2/0 | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | 1/C | 2/0 |  |  |  |  | 2500
MV15¦1/C¦4/0 | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | 1/C | 4/0 |  |  |  |  | 2500
MV15¦1/C¦250 | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | 1/C | 250 kcmil |  |  |  |  | 2500
MV15¦1/C¦500 | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | 1/C | 500 kcmil |  |  |  |  | 2500
MV15¦1/C¦750 | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | 1/C | 750 kcmil |  |  |  |  | 2500
MV15¦1/C¦1000 | MV 15 kV | MV-105 15 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | 1/C | 1000 kcmil |  |  |  |  | 2500
MV15AX¦3/C¦2 | MV 15 kV | ARMOR-X MC-HL / MV-105 15 kV 3/C Cu, EPR 133%, tape shield, gnd, CWA, red PVC | 3/C | 2 |  |  |  |  | 2000
MV15AX¦3/C¦1/0 | MV 15 kV | ARMOR-X MC-HL / MV-105 15 kV 3/C Cu, EPR 133%, tape shield, gnd, CWA, red PVC | 3/C | 1/0 |  |  |  |  | 2000
MV5¦3/C¦2 | MV 5 kV | MV-105 5 kV 3/C Cu, EPR 133%, tape shield, gnd, PVC jacket | 3/C | 2 |  |  |  |  | 2500
MV5¦3/C¦1/0 | MV 5 kV | MV-105 5 kV 3/C Cu, EPR 133%, tape shield, gnd, PVC jacket | 3/C | 1/0 |  |  |  |  | 2500
MV5¦3/C¦4/0 | MV 5 kV | MV-105 5 kV 3/C Cu, EPR 133%, tape shield, gnd, PVC jacket | 3/C | 4/0 |  |  |  |  | 2500
MV5¦3/C¦250 | MV 5 kV | MV-105 5 kV 3/C Cu, EPR 133%, tape shield, gnd, PVC jacket | 3/C | 250 kcmil |  |  |  |  | 2500
MV5S¦1/C¦1000 | MV 5 kV | MV-105 5 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket (triplexed) | 1/C | 1000 kcmil |  |  |  |  | 2500
MV25¦1/C¦2 | MV 25 kV | MV-105 25 kV 1/C Cu, EPR 133%, Cu tape shield, PVC jacket | 1/C | 2 |  |  |  |  | 2500
MV35¦1/C¦2 | MV 35 kV | MV-105 35 kV 1/C Al, EPR 133%, 1/3 concentric neutral, LLDPE jacket | 1/C | 2 |  |  |  |  | 2500
MV35¦1/C¦350 | MV 35 kV | MV-105 35 kV 1/C Al, EPR 133%, 1/3 concentric neutral, LLDPE jacket | 1/C | 350 kcmil |  |  |  |  | 2500
MV35¦1/C¦750 | MV 35 kV | MV-105 35 kV 1/C Al, EPR 133%, 1/3 concentric neutral, LLDPE jacket | 1/C | 750 kcmil |  |  |  |  | 2500
HV230¦1/C¦2500 | HV 230 kV | HV XLPE 230 kV 1/C 2500 kcmil Cu, Cu wire shield, Al laminate, HDPE jacket | 1/C | 2500 kcmil |  |  |  |  | 1800
LV¦3/C+G¦10 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | 3/C+G | 10 |  |  |  |  | 2500
LV¦1/C¦8 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | 1/C | 8 |  |  |  |  | 2500
LV¦3/C+G¦8 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | 3/C+G | 8 |  |  |  |  | 2500
LV¦3/C+G¦6 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | 3/C+G | 6 |  |  |  |  | 2500
LV¦3/C+G¦4 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | 3/C+G | 4 |  |  |  |  | 2500
LV¦3/C+G¦2 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | 3/C+G | 2 |  |  |  |  | 2500
LV¦3/C+G¦1 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | 3/C+G | 1 |  |  |  |  | 2500
LV¦3/C+G¦1/0 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | 3/C+G | 1/0 |  |  |  |  | 2500
LV¦3/C+G¦2/0 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | 3/C+G | 2/0 |  |  |  |  | 2500
LV¦3/C+G¦3/0 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | 3/C+G | 3/0 |  |  |  |  | 2500
LV¦3/C+G¦4/0 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | 3/C+G | 4/0 |  |  |  |  | 2500
LV¦3/C+G¦250 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | 3/C+G | 250 kcmil |  |  |  |  | 2500
LV¦3/C+G¦350 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | 3/C+G | 350 kcmil |  |  |  |  | 2500
LV¦3/C+G¦500 | LV 600 V | Type TC-ER 600 V 3/C Cu XHHW-2 + ground, PVC jacket | 3/C+G | 500 kcmil |  |  |  |  | 2500
LV1C¦1/C¦500 | LV 600 V | XHHW-2 600 V 1/C Cu (feeder sets in tray / duct) | 1/C | 500 kcmil |  |  |  |  | 2500
LVAX¦3/C+G¦10 | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | 3/C+G | 10 |  |  |  |  | 2000
LVAX¦3/C+G¦8 | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | 3/C+G | 8 |  |  |  |  | 2000
LVAX¦3/C+G¦6 | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | 3/C+G | 6 |  |  |  |  | 2000
LVAX¦3/C+G¦4 | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | 3/C+G | 4 |  |  |  |  | 2000
LVAX¦3/C+G¦2 | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | 3/C+G | 2 |  |  |  |  | 2000
LVAX¦3/C+G¦1 | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | 3/C+G | 1 |  |  |  |  | 2000
LVAX¦3/C+G¦1/0 | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | 3/C+G | 1/0 |  |  |  |  | 2000
LVAX¦3/C+G¦3/0 | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | 3/C+G | 3/0 |  |  |  |  | 2000
LVAX¦3/C+G¦4/0 | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | 3/C+G | 4/0 |  |  |  |  | 2000
LVAX¦3/C+G¦350 | LV 600 V | ARMOR-X MC-HL 600 V 3/C Cu XHHW-2 + ground, CWA, black PVC (Class I Div 2) | 3/C+G | 350 kcmil |  |  |  |  | 2000
VFD¦3/C+3G¦6 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | 3/C+3G | 6 |  |  |  |  | 2500
VFD¦3/C+3G¦2 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | 3/C+3G | 2 |  |  |  |  | 2500
VFD¦3/C+3G¦1 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | 3/C+3G | 1 |  |  |  |  | 2500
VFD¦3/C+3G¦2/0 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | 3/C+3G | 2/0 |  |  |  |  | 2500
VFD¦3/C+3G¦3/0 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | 3/C+3G | 3/0 |  |  |  |  | 2500
VFD¦3/C+3G¦350 | LV 600 V | VFD cable 600 V 3/C Cu XHHW-2, 3 symmetrical grounds, overall Cu tape shield, TC-ER | 3/C+3G | 350 kcmil |  |  |  |  | 2500
CT¦12/C¦14 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | 12/C | 14 |  |  |  |  | 5000
CT¦2/C¦14 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | 2/C | 14 |  |  |  |  | 5000
CT¦25/C¦14 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | 25/C | 14 |  |  |  |  | 5000
CT¦7/C¦14 | Control | Control cable 600 V Type TC-ER, Cu #14 AWG, PVC jacket | 7/C | 14 |  |  |  |  | 5000
CTAX¦12/C¦14 | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | 12/C | 14 |  |  |  |  | 3000
CTAX¦2/C¦14 | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | 2/C | 14 |  |  |  |  | 3000
CTAX¦25/C¦14 | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | 25/C | 14 |  |  |  |  | 3000
CTAX¦7/C¦14 | Control | ARMOR-X MC-HL 600 V control, Cu #14 AWG (Class I Div 2) | 7/C | 14 |  |  |  |  | 3000
CTCT¦4/C¦10 | Control | Control cable 600 V Type TC-ER, Cu #10 AWG (CT / VT circuits) | 4/C | 10 |  |  |  |  | 5000
ITC¦1 pr¦16 | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | 1 pr | 16 |  |  |  |  | 5000
ITC¦12 pr¦18 | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | 12 pr | 18 |  |  |  |  | 5000
ITC¦24 pr¦18 | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | 24 pr | 18 |  |  |  |  | 5000
ITC¦4 pr¦18 | Instrumentation | Instrumentation ITC / PLTC, IS, #18 shielded pairs, blue jacket | 4 pr | 18 |  |  |  |  | 5000
PLTC¦1 pr¦16 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | 1 pr | 16 |  |  |  |  | 5000
PLTC¦12 pr¦18 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | 12 pr | 18 |  |  |  |  | 5000
PLTC¦24 pr¦18 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | 24 pr | 18 |  |  |  |  | 5000
PLTC¦4 pr¦18 | Instrumentation | Instrumentation PLTC / TC-ER 300 V, #18 twisted shielded pairs, overall shield | 4 pr | 18 |  |  |  |  | 5000
RTD¦1 tri¦18 | Instrumentation | RTD cable, #18 shielded triads, PLTC | 1 tri | 18 |  |  |  |  | 5000
RTD¦12 tri¦18 | Instrumentation | RTD cable, #18 shielded triads, PLTC | 12 tri | 18 |  |  |  |  | 5000
TCX¦1 pr¦16 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | 1 pr | 16 |  |  |  |  | 5000
TCX¦12 pr¦16 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | 12 pr | 16 |  |  |  |  | 5000
TCX¦24 pr¦16 | Instrumentation | Thermocouple extension KX, #16 shielded pairs, PLTC | 24 pr | 16 |  |  |  |  | 5000
FA¦2/C¦14 | Fire alarm | Fire alarm FPLR 2/C #14 shielded, red jacket (NEC 760) | 2/C | 14 |  |  |  |  | 5000
FO¦12 SM¦- | Fibre / data | Fibre optic, single-mode, 12-fibre, armored, orange jacket | 12 SM | - |  |  |  |  | 10000
PV¦1/C¦500 | DC 2 kV | PV / RHW-2 2 kV 1/C Cu, XLPE (DC) | 1/C | 500 kcmil |  |  |  |  | 2500
SHD¦3/C¦2 | Portable MV | Type SHD-GC 15 kV 3/C Cu, 2 grounds + GC, yellow CPE (portable) | 3/C | 2 |  |  |  |  | 1000
W¦1/C¦4/0 | Portable LV | Type W 2 kV 1/C Cu, EPDM / CPE (portable, cam-lock) | 1/C | 4/0 |  |  |  |  | 1000
THHN¦1/C¦12 | Building wire | SIMpull THHN/THWN-2 600 V 1/C Cu (lighting, receptacles, small power) | 1/C | 12 |  |  |  |  | 5000
BARE¦1/C¦4/0 | Grounding | Bare Cu 4/0 AWG, 19 strand (ground grid and equipment grounds) | 1/C | 4/0 |  |  |  |  | 5000
ACSR¦1/C¦1590 | Overhead | Overhead conductor ACSR 1590 kcmil 'Falcon' (typ.) | 1/C | 1590 kcmil |  |  |  |  | 7000
Total
Standard reel lengths are typical inputs (blue); edit to the actual reel / SIMpull reel sizes.

## Accessories
Accessory | Quantity
MV termination kits (outdoor / indoor, per conductor or per 3/C end)
ARMOR-X / Type W connectors and glands
MV splice kits (allowance: 1 per 2,500 ft of MV 1/C)
230 kV outdoor terminations
600 V compression lugs (power, 4 per end)
Instrument / control cable glands (2 per run)
Fibre patch / termination (2 per link)
Ground connections: exothermic welds (allowance 1 per 25 ft of grid)

## Summary
Total cable length (ft) by zone and class
Zone | MV 15 kV | MV 5 kV | MV 25 kV | MV 35 kV | HV 230 kV | LV 600 V | Control | Instrumentation | Fire alarm | Fibre / data | DC 2 kV | Portable MV | Portable LV | Building wire | Grounding | Overhead | Total
A Power block
B ACC
C Grid interface
D Fuel gas
E Water / utilities
F Controls / service
G Carbon capture
H BESS
I Modular / portable power
J GT inlet chilling
K Fuel supply (adjacent market)
Total
Total (miles)
Schedule rows
Cables (count)
Device count behind the schedule (typical for each equipment class)
Analog instruments | 5981
Discrete devices | 6285
Thermocouples | 832
RTDs | 450
Solenoids | 544
LV motors | 722
Motor-operated valves | 269

## Load List
Load (to) | Tag | Zone | Service | Voltage (V) | Load (kW) | Current (A) | Source (from) | Product | Size | Sets
Air compressors AC-A/B/C | AC-A/B/C | A | Motor 1 of 3, 250 kW | 480 | 250 | 353.8 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 4/0 | 2
Air compressors AC-A/B/C | AC-A/B/C | A | Motor 2 of 3, 250 kW | 480 | 250 | 353.8 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 4/0 | 2
Air compressors AC-A/B/C | AC-A/B/C | A | Motor 3 of 3, 250 kW | 480 | 250 | 353.8 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 4/0 | 2
BFP-1A/B: boiler feed pumps (13.8 kV DOL) | BFP-1 | A | Motor 1 of 4, 15 kW | 480 | 15 | 21.2 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 6 | 1
BFP-1A/B: boiler feed pumps (13.8 kV DOL) | BFP-1 | A | Motor 2 of 4, 15 kW | 480 | 15 | 21.2 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 6 | 1
BFP-1A/B: boiler feed pumps (13.8 kV DOL) | BFP-1 | A | Motor 3 of 4, 15 kW | 480 | 15 | 21.2 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 6 | 1
BFP-1A/B: boiler feed pumps (13.8 kV DOL) | BFP-1 | A | Motor 4 of 4, 15 kW | 480 | 15 | 21.2 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 6 | 1
BFP-2A/B: boiler feed pumps (13.8 kV DOL) | BFP-2 | A | Motor 1 of 4, 15 kW | 480 | 15 | 21.2 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 6 | 1
BFP-2A/B: boiler feed pumps (13.8 kV DOL) | BFP-2 | A | Motor 2 of 4, 15 kW | 480 | 15 | 21.2 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 6 | 1
BFP-2A/B: boiler feed pumps (13.8 kV DOL) | BFP-2 | A | Motor 3 of 4, 15 kW | 480 | 15 | 21.2 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 6 | 1
BFP-2A/B: boiler feed pumps (13.8 kV DOL) | BFP-2 | A | Motor 4 of 4, 15 kW | 480 | 15 | 21.2 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 6 | 1
BFP-3A/B: boiler feed pumps (13.8 kV DOL) | BFP-3 | A | Motor 1 of 4, 15 kW | 480 | 15 | 21.2 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 6 | 1
BFP-3A/B: boiler feed pumps (13.8 kV DOL) | BFP-3 | A | Motor 2 of 4, 15 kW | 480 | 15 | 21.2 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 6 | 1
BFP-3A/B: boiler feed pumps (13.8 kV DOL) | BFP-3 | A | Motor 3 of 4, 15 kW | 480 | 15 | 21.2 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 6 | 1
BFP-3A/B: boiler feed pumps (13.8 kV DOL) | BFP-3 | A | Motor 4 of 4, 15 kW | 480 | 15 | 21.2 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 6 | 1
Bridge crane (parked over laydown bay) | CRANE | A | Bridge crane conductor-bar feeder (fused disconnect, north wall) | 480 | 150 | 212.3 | R1 LC-480-A (480 V switchgear) | LV 600 V | 350 kcmil | 1
CEMS shelter, HRSG 1 | CEMS-1 | A | Motor 1 of 2, 5 kW | 480 | 5 | 7.1 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
CEMS shelter, HRSG 1 | CEMS-1 | A | Motor 2 of 2, 5 kW | 480 | 5 | 7.1 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
CEMS shelter, HRSG 2 | CEMS-2 | A | Motor 1 of 2, 5 kW | 480 | 5 | 7.1 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
CEMS shelter, HRSG 2 | CEMS-2 | A | Motor 2 of 2, 5 kW | 480 | 5 | 7.1 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
CEMS shelter, HRSG 3 | CEMS-3 | A | Motor 1 of 2, 5 kW | 480 | 5 | 7.1 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
CEMS shelter, HRSG 3 | CEMS-3 | A | Motor 2 of 2, 5 kW | 480 | 5 | 7.1 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
Chemical feed | Chem feed | A | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
Chemical feed | Chem feed | A | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
Chemical feed | Chem feed | A | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
Chemical feed | Chem feed | A | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
Chemical feed | Chem feed | A | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
Chemical feed | Chem feed | A | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
Common turbine hall | HALL | A | LV power feeder | 480 | 15 | 21.2 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 2 | 1
EHC-ST: ST electro-hydraulic control power unit | EHC-ST | A | Motor 1 of 2, 37 kW | 480 | 37 | 52.4 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 4 | 1
EHC-ST: ST electro-hydraulic control power unit | EHC-ST | A | Motor 2 of 2, 37 kW | 480 | 37 | 52.4 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 4 | 1
FH-1 stair tower |  | A | Area / platform lighting circuit 1 (8 fixtures) | 480 | 3 | 5 | R1 MCC-GT1 | LV 600 V | 10 | 1
FH-1: GT inlet filter house on its own frame | FH-1 | A | Motor 1 of 2, 15 kW | 480 | 15 | 21.2 | R1 MCC-GT1 | LV 600 V | 6 | 1
FH-1: GT inlet filter house on its own frame | FH-1 | A | Motor 2 of 2, 15 kW | 480 | 15 | 21.2 | R1 MCC-GT1 | LV 600 V | 6 | 1
FH-1: GT inlet filter house on its own frame | FH-1 | A | Area / platform lighting circuit 1 (12 fixtures) | 480 | 3 | 5 | R1 MCC-GT1 | LV 600 V | 10 | 1
FH-2 stair tower |  | A | Area / platform lighting circuit 1 (8 fixtures) | 480 | 3 | 5 | R1 MCC-GT2 | LV 600 V | 10 | 1
FH-2: GT inlet filter house on its own frame | FH-2 | A | Motor 1 of 2, 15 kW | 480 | 15 | 21.2 | R1 MCC-GT2 | LV 600 V | 4 | 1
FH-2: GT inlet filter house on its own frame | FH-2 | A | Motor 2 of 2, 15 kW | 480 | 15 | 21.2 | R1 MCC-GT2 | LV 600 V | 4 | 1
FH-2: GT inlet filter house on its own frame | FH-2 | A | Area / platform lighting circuit 1 (12 fixtures) | 480 | 3 | 5 | R1 MCC-GT2 | LV 600 V | 10 | 1
FH-3 stair tower |  | A | Area / platform lighting circuit 1 (8 fixtures) | 480 | 3 | 5 | R1 MCC-GT3 | LV 600 V | 8 | 1
FH-3: GT inlet filter house on its own frame | FH-3 | A | Motor 1 of 2, 15 kW | 480 | 15 | 21.2 | R1 MCC-GT3 | LV 600 V | 4 | 1
FH-3: GT inlet filter house on its own frame | FH-3 | A | Motor 2 of 2, 15 kW | 480 | 15 | 21.2 | R1 MCC-GT3 | LV 600 V | 4 | 1
FH-3: GT inlet filter house on its own frame | FH-3 | A | Area / platform lighting circuit 1 (12 fixtures) | 480 | 3 | 5 | R1 MCC-GT3 | LV 600 V | 10 | 1
FS-GT1: CO2 fire-suppression skid | FS-GT1 | A | LV power feeder | 480 | 150 | 212.3 | R1 MCC-GT1 | LV 600 V | 350 kcmil | 1
FS-GT2: CO2 fire-suppression skid | FS-GT2 | A | LV power feeder | 480 | 150 | 212.3 | R1 MCC-GT2 | LV 600 V | 350 kcmil | 1
FS-GT3: CO2 fire-suppression skid | FS-GT3 | A | LV power feeder | 480 | 150 | 212.3 | R1 MCC-GT3 | LV 600 V | 350 kcmil | 1
GFM-1: GT1 gas fuel module (stop / control valves, final strainer) | GFM-1 | A | LV power feeder | 480 | 15 | 21.2 | R1 MCC-GT1 | LV 600 V | 8 | 1
GFM-2: GT2 gas fuel module (stop / control valves, final strainer) | GFM-2 | A | LV power feeder | 480 | 15 | 21.2 | R1 MCC-GT2 | LV 600 V | 6 | 1
GFM-3: GT3 gas fuel module (stop / control valves, final strainer) | GFM-3 | A | LV power feeder | 480 | 15 | 21.2 | R1 MCC-GT3 | LV 600 V | 4 | 1
GSC-ST: gland-steam condenser and exhausters | GSC-ST | A | Motor 1 of 2, 30 kW | 480 | 30 | 42.5 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 6 | 1
GSC-ST: gland-steam condenser and exhausters | GSC-ST | A | Motor 2 of 2, 30 kW | 480 | 30 | 42.5 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 6 | 1
GSU-1 firewall |  | A | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-1 firewall |  | A | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-1 firewall |  | A | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-1 firewall |  | A | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-1 firewall |  | A | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-1 firewall |  | A | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-1: 21/230 kV generator step-up transformer | GSU-1 | A | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-1: 21/230 kV generator step-up transformer | GSU-1 | A | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-1: 21/230 kV generator step-up transformer | GSU-1 | A | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-1: 21/230 kV generator step-up transformer | GSU-1 | A | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-1: 21/230 kV generator step-up transformer | GSU-1 | A | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-1: 21/230 kV generator step-up transformer | GSU-1 | A | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-2 firewall |  | A | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-2 firewall |  | A | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-2 firewall |  | A | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-2 firewall |  | A | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-2 firewall |  | A | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-2 firewall |  | A | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-2: 21/230 kV generator step-up transformer | GSU-2 | A | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-2: 21/230 kV generator step-up transformer | GSU-2 | A | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-2: 21/230 kV generator step-up transformer | GSU-2 | A | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-2: 21/230 kV generator step-up transformer | GSU-2 | A | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-2: 21/230 kV generator step-up transformer | GSU-2 | A | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-2: 21/230 kV generator step-up transformer | GSU-2 | A | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-3 firewall |  | A | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-3 firewall |  | A | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-3 firewall |  | A | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-3 firewall |  | A | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-3 firewall |  | A | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-3 firewall |  | A | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-3: 21/230 kV generator step-up transformer | GSU-3 | A | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-3: 21/230 kV generator step-up transformer | GSU-3 | A | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-3: 21/230 kV generator step-up transformer | GSU-3 | A | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-3: 21/230 kV generator step-up transformer | GSU-3 | A | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-3: 21/230 kV generator step-up transformer | GSU-3 | A | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-3: 21/230 kV generator step-up transformer | GSU-3 | A | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
GSU-ST firewall |  | A | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
GSU-ST firewall |  | A | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
GSU-ST firewall |  | A | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
GSU-ST firewall |  | A | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
GSU-ST firewall |  | A | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
GSU-ST firewall |  | A | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
GSU-ST: 21/230 kV (one ST GSU, baseline) | GSU-ST | A | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
GSU-ST: 21/230 kV (one ST GSU, baseline) | GSU-ST | A | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
GSU-ST: 21/230 kV (one ST GSU, baseline) | GSU-ST | A | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
GSU-ST: 21/230 kV (one ST GSU, baseline) | GSU-ST | A | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
GSU-ST: 21/230 kV (one ST GSU, baseline) | GSU-ST | A | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
GSU-ST: 21/230 kV (one ST GSU, baseline) | GSU-ST | A | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
GT1 aux: lube oil, hydraulics, enclosure fans | GT1 aux | A | Motor 1 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT1 | LV 600 V | 2 | 1
GT1 aux: lube oil, hydraulics, enclosure fans | GT1 aux | A | Motor 2 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT1 | LV 600 V | 2 | 1
GT1 aux: lube oil, hydraulics, enclosure fans | GT1 aux | A | Motor 3 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT1 | LV 600 V | 2 | 1
GT1 aux: lube oil, hydraulics, enclosure fans | GT1 aux | A | Motor 4 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT1 | LV 600 V | 2 | 1
GT1 aux: lube oil, hydraulics, enclosure fans | GT1 aux | A | Motor 5 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT1 | LV 600 V | 2 | 1
GT1 aux: lube oil, hydraulics, enclosure fans | GT1 aux | A | Motor 6 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT1 | LV 600 V | 2 | 1
GT1 aux: lube oil, hydraulics, enclosure fans | GT1 aux | A | Motor 7 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT1 | LV 600 V | 2 | 1
GT1 aux: lube oil, hydraulics, enclosure fans | GT1 aux | A | Motor 8 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT1 | LV 600 V | 2 | 1
GT1 aux: lube oil, hydraulics, enclosure fans | GT1 aux | A | Motor 9 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT1 | LV 600 V | 2 | 1
GT1 aux: lube oil, hydraulics, enclosure fans | GT1 aux | A | Motor 10 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT1 | LV 600 V | 2 | 1
GT1 aux: lube oil, hydraulics, enclosure fans | GT1 aux | A | Motor 11 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT1 | LV 600 V | 2 | 1
GT1 aux: lube oil, hydraulics, enclosure fans | GT1 aux | A | Motor 12 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT1 | LV 600 V | 2 | 1
GT1: H-class gas turbine (60 Hz) | GT1 | A | LV power feeder | 480 | 150 | 212.3 | R1 MCC-GT1 | LV 600 V | 350 kcmil | 1
GT1: H-class gas turbine (60 Hz) | GT1 | A | 480 V welding receptacle 1 | 480 | 60 | 76 | R1 MCC-GT1 | LV 600 V | 2 | 1
GT1: H-class gas turbine (60 Hz) | GT1 | A | 480 V welding receptacle 2 | 480 | 60 | 76 | R1 MCC-GT1 | LV 600 V | 2 | 1
GT1: H-class gas turbine (60 Hz) | GT1 | A | 480 V welding receptacle 3 | 480 | 60 | 76 | R1 MCC-GT1 | LV 600 V | 2 | 1
GT1: H-class gas turbine (60 Hz) | GT1 | A | 480 V welding receptacle 4 | 480 | 60 | 76 | R1 MCC-GT1 | LV 600 V | 2 | 1
GT2 aux: lube oil, hydraulics, enclosure fans | GT2 aux | A | Motor 1 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT2 | LV 600 V | 1 | 1
GT2 aux: lube oil, hydraulics, enclosure fans | GT2 aux | A | Motor 2 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT2 | LV 600 V | 1 | 1
GT2 aux: lube oil, hydraulics, enclosure fans | GT2 aux | A | Motor 3 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT2 | LV 600 V | 1 | 1
GT2 aux: lube oil, hydraulics, enclosure fans | GT2 aux | A | Motor 4 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT2 | LV 600 V | 1 | 1
GT2 aux: lube oil, hydraulics, enclosure fans | GT2 aux | A | Motor 5 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT2 | LV 600 V | 1 | 1
GT2 aux: lube oil, hydraulics, enclosure fans | GT2 aux | A | Motor 6 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT2 | LV 600 V | 1 | 1
GT2 aux: lube oil, hydraulics, enclosure fans | GT2 aux | A | Motor 7 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT2 | LV 600 V | 1 | 1
GT2 aux: lube oil, hydraulics, enclosure fans | GT2 aux | A | Motor 8 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT2 | LV 600 V | 1 | 1
GT2 aux: lube oil, hydraulics, enclosure fans | GT2 aux | A | Motor 9 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT2 | LV 600 V | 1 | 1
GT2 aux: lube oil, hydraulics, enclosure fans | GT2 aux | A | Motor 10 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT2 | LV 600 V | 1 | 1
GT2 aux: lube oil, hydraulics, enclosure fans | GT2 aux | A | Motor 11 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT2 | LV 600 V | 1 | 1
GT2 aux: lube oil, hydraulics, enclosure fans | GT2 aux | A | Motor 12 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT2 | LV 600 V | 1 | 1
GT2: H-class gas turbine (60 Hz) | GT2 | A | LV power feeder | 480 | 150 | 212.3 | R1 MCC-GT2 | LV 600 V | 350 kcmil | 1
GT2: H-class gas turbine (60 Hz) | GT2 | A | 480 V welding receptacle 1 | 480 | 60 | 76 | R1 MCC-GT2 | LV 600 V | 1 | 1
GT2: H-class gas turbine (60 Hz) | GT2 | A | 480 V welding receptacle 2 | 480 | 60 | 76 | R1 MCC-GT2 | LV 600 V | 1 | 1
GT2: H-class gas turbine (60 Hz) | GT2 | A | 480 V welding receptacle 3 | 480 | 60 | 76 | R1 MCC-GT2 | LV 600 V | 1 | 1
GT2: H-class gas turbine (60 Hz) | GT2 | A | 480 V welding receptacle 4 | 480 | 60 | 76 | R1 MCC-GT2 | LV 600 V | 1 | 1
GT3 aux: lube oil, hydraulics, enclosure fans | GT3 aux | A | Motor 1 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT3 | LV 600 V | 1/0 | 1
GT3 aux: lube oil, hydraulics, enclosure fans | GT3 aux | A | Motor 2 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT3 | LV 600 V | 1/0 | 1
GT3 aux: lube oil, hydraulics, enclosure fans | GT3 aux | A | Motor 3 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT3 | LV 600 V | 1/0 | 1
GT3 aux: lube oil, hydraulics, enclosure fans | GT3 aux | A | Motor 4 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT3 | LV 600 V | 1/0 | 1
GT3 aux: lube oil, hydraulics, enclosure fans | GT3 aux | A | Motor 5 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT3 | LV 600 V | 1/0 | 1
GT3 aux: lube oil, hydraulics, enclosure fans | GT3 aux | A | Motor 6 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT3 | LV 600 V | 1/0 | 1
GT3 aux: lube oil, hydraulics, enclosure fans | GT3 aux | A | Motor 7 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT3 | LV 600 V | 1/0 | 1
GT3 aux: lube oil, hydraulics, enclosure fans | GT3 aux | A | Motor 8 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT3 | LV 600 V | 1/0 | 1
GT3 aux: lube oil, hydraulics, enclosure fans | GT3 aux | A | Motor 9 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT3 | LV 600 V | 1/0 | 1
GT3 aux: lube oil, hydraulics, enclosure fans | GT3 aux | A | Motor 10 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT3 | LV 600 V | 1/0 | 1
GT3 aux: lube oil, hydraulics, enclosure fans | GT3 aux | A | Motor 11 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT3 | LV 600 V | 1/0 | 1
GT3 aux: lube oil, hydraulics, enclosure fans | GT3 aux | A | Motor 12 of 12, 45 kW | 480 | 45 | 63.7 | R1 MCC-GT3 | LV 600 V | 1/0 | 1
GT3: H-class gas turbine (60 Hz) | GT3 | A | LV power feeder | 480 | 150 | 212.3 | R1 MCC-GT3 | LV 600 V | 350 kcmil | 1
GT3: H-class gas turbine (60 Hz) | GT3 | A | 480 V welding receptacle 1 | 480 | 60 | 76 | R1 MCC-GT3 | LV 600 V | 1/0 | 1
GT3: H-class gas turbine (60 Hz) | GT3 | A | 480 V welding receptacle 2 | 480 | 60 | 76 | R1 MCC-GT3 | LV 600 V | 1/0 | 1
GT3: H-class gas turbine (60 Hz) | GT3 | A | 480 V welding receptacle 3 | 480 | 60 | 76 | R1 MCC-GT3 | LV 600 V | 1/0 | 1
GT3: H-class gas turbine (60 Hz) | GT3 | A | 480 V welding receptacle 4 | 480 | 60 | 76 | R1 MCC-GT3 | LV 600 V | 1/0 | 1
GTG-1: GT generator | GTG-1 | A | Motor 1 of 4, 2 kW | 480 | 2 | 2.8 | R1 MCC-GT1 | LV 600 V | 10 | 1
GTG-1: GT generator | GTG-1 | A | Motor 2 of 4, 2 kW | 480 | 2 | 2.8 | R1 MCC-GT1 | LV 600 V | 10 | 1
GTG-1: GT generator | GTG-1 | A | Motor 3 of 4, 2 kW | 480 | 2 | 2.8 | R1 MCC-GT1 | LV 600 V | 10 | 1
GTG-1: GT generator | GTG-1 | A | Motor 4 of 4, 2 kW | 480 | 2 | 2.8 | R1 MCC-GT1 | LV 600 V | 10 | 1
GTG-2: GT generator | GTG-2 | A | Motor 1 of 4, 2 kW | 480 | 2 | 2.8 | R1 MCC-GT2 | LV 600 V | 10 | 1
GTG-2: GT generator | GTG-2 | A | Motor 2 of 4, 2 kW | 480 | 2 | 2.8 | R1 MCC-GT2 | LV 600 V | 10 | 1
GTG-2: GT generator | GTG-2 | A | Motor 3 of 4, 2 kW | 480 | 2 | 2.8 | R1 MCC-GT2 | LV 600 V | 10 | 1
GTG-2: GT generator | GTG-2 | A | Motor 4 of 4, 2 kW | 480 | 2 | 2.8 | R1 MCC-GT2 | LV 600 V | 10 | 1
GTG-3: GT generator | GTG-3 | A | Motor 1 of 4, 2 kW | 480 | 2 | 2.8 | R1 MCC-GT3 | LV 600 V | 10 | 1
GTG-3: GT generator | GTG-3 | A | Motor 2 of 4, 2 kW | 480 | 2 | 2.8 | R1 MCC-GT3 | LV 600 V | 10 | 1
GTG-3: GT generator | GTG-3 | A | Motor 3 of 4, 2 kW | 480 | 2 | 2.8 | R1 MCC-GT3 | LV 600 V | 10 | 1
GTG-3: GT generator | GTG-3 | A | Motor 4 of 4, 2 kW | 480 | 2 | 2.8 | R1 MCC-GT3 | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | Motor 1 of 4, 15 kW | 480 | 15 | 21.2 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | Motor 2 of 4, 15 kW | 480 | 15 | 21.2 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | Motor 3 of 4, 15 kW | 480 | 15 | 21.2 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | Motor 4 of 4, 15 kW | 480 | 15 | 21.2 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 1: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 2: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 3: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 4: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 5: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 6: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 7: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 8: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 9: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 10: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 11: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 12: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 13: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 14: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 15: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 16: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 17: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 18: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 19: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 20: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 21: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 22: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 23: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 24: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 25: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 26: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 27: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 28: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 29: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 30: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 31: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 32: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 33: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 34: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 35: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 36: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 37: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 38: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 39: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 40: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 41: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 42: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 43: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 44: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | MOV 45: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | Area / platform lighting circuit 1 (12 fixtures) | 480 | 3 | 5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | Area / platform lighting circuit 2 (12 fixtures) | 480 | 3 | 5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | Area / platform lighting circuit 3 (12 fixtures) | 480 | 3 | 5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | Area / platform lighting circuit 4 (4 fixtures) | 480 | 3 | 5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | 480 V welding receptacle 1 | 480 | 60 | 76 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 2 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | 480 V welding receptacle 2 | 480 | 60 | 76 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 2 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | 480 V welding receptacle 3 | 480 | 60 | 76 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 2 | 1
HRSG 1 + SCR (3P reheat, horizontal) | HRSG-1 | A | 480 V welding receptacle 4 | 480 | 60 | 76 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 2 | 1
HRSG 1 blowdown tank (continuous / intermittent) |  | A | MOV 1: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 blowdown tank (continuous / intermittent) |  | A | MOV 2: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 blowdown tank (continuous / intermittent) |  | A | MOV 3: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 blowdown tank (continuous / intermittent) |  | A | MOV 4: power | 480 | 2.5 | 3.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 blowdown tank (continuous / intermittent) |  | A | LV power feeder | 480 | 10 | 14.2 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 chemical feed skid (phosphate / amine) |  | A | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 chemical feed skid (phosphate / amine) |  | A | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 chemical feed skid (phosphate / amine) |  | A | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 chemical feed skid (phosphate / amine) |  | A | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 chemical feed skid (phosphate / amine) |  | A | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 chemical feed skid (phosphate / amine) |  | A | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 1 stack | STK-1 | A | Area / platform lighting circuit 1 (6 fixtures) | 480 | 3 | 5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | Motor 1 of 4, 15 kW | 480 | 15 | 21.2 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | Motor 2 of 4, 15 kW | 480 | 15 | 21.2 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | Motor 3 of 4, 15 kW | 480 | 15 | 21.2 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | Motor 4 of 4, 15 kW | 480 | 15 | 21.2 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 1: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 2: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 3: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 4: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 5: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 6: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 7: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 8: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 9: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 10: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 11: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 12: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 13: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 14: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 15: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 16: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 17: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 18: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 19: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 20: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 21: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 22: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 23: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 24: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 25: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 26: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 27: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 28: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 29: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 30: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 31: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 32: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 33: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 34: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 35: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 36: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 37: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 38: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 39: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 40: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 41: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 42: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 43: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 44: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | MOV 45: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | Area / platform lighting circuit 1 (12 fixtures) | 480 | 3 | 5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | Area / platform lighting circuit 2 (12 fixtures) | 480 | 3 | 5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | Area / platform lighting circuit 3 (12 fixtures) | 480 | 3 | 5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | Area / platform lighting circuit 4 (4 fixtures) | 480 | 3 | 5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | 480 V welding receptacle 1 | 480 | 60 | 76 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 2 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | 480 V welding receptacle 2 | 480 | 60 | 76 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 2 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | 480 V welding receptacle 3 | 480 | 60 | 76 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 2 | 1
HRSG 2 + SCR (3P reheat, horizontal) | HRSG-2 | A | 480 V welding receptacle 4 | 480 | 60 | 76 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 2 | 1
HRSG 2 blowdown tank (continuous / intermittent) |  | A | MOV 1: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 blowdown tank (continuous / intermittent) |  | A | MOV 2: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 blowdown tank (continuous / intermittent) |  | A | MOV 3: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 blowdown tank (continuous / intermittent) |  | A | MOV 4: power | 480 | 2.5 | 3.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 blowdown tank (continuous / intermittent) |  | A | LV power feeder | 480 | 10 | 14.2 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 chemical feed skid (phosphate / amine) |  | A | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 chemical feed skid (phosphate / amine) |  | A | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 chemical feed skid (phosphate / amine) |  | A | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 chemical feed skid (phosphate / amine) |  | A | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 chemical feed skid (phosphate / amine) |  | A | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 chemical feed skid (phosphate / amine) |  | A | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 2 stack | STK-2 | A | Area / platform lighting circuit 1 (6 fixtures) | 480 | 3 | 5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | Motor 1 of 4, 15 kW | 480 | 15 | 21.2 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | Motor 2 of 4, 15 kW | 480 | 15 | 21.2 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | Motor 3 of 4, 15 kW | 480 | 15 | 21.2 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | Motor 4 of 4, 15 kW | 480 | 15 | 21.2 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 1: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 2: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 3: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 4: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 5: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 6: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 7: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 8: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 9: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 10: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 11: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 12: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 13: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 14: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 15: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 16: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 17: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 18: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 19: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 20: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 21: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 22: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 23: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 24: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 25: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 26: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 27: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 28: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 29: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 30: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 31: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 32: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 33: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 34: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 35: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 36: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 37: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 38: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 39: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 40: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 41: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 42: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 43: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 44: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | MOV 45: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | Area / platform lighting circuit 1 (12 fixtures) | 480 | 3 | 5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | Area / platform lighting circuit 2 (12 fixtures) | 480 | 3 | 5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | Area / platform lighting circuit 3 (12 fixtures) | 480 | 3 | 5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | Area / platform lighting circuit 4 (4 fixtures) | 480 | 3 | 5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | 480 V welding receptacle 1 | 480 | 60 | 76 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 2 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | 480 V welding receptacle 2 | 480 | 60 | 76 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 2 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | 480 V welding receptacle 3 | 480 | 60 | 76 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 2 | 1
HRSG 3 + SCR (3P reheat, horizontal) | HRSG-3 | A | 480 V welding receptacle 4 | 480 | 60 | 76 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 2 | 1
HRSG 3 blowdown tank (continuous / intermittent) |  | A | MOV 1: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 blowdown tank (continuous / intermittent) |  | A | MOV 2: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 blowdown tank (continuous / intermittent) |  | A | MOV 3: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 blowdown tank (continuous / intermittent) |  | A | MOV 4: power | 480 | 2.5 | 3.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 blowdown tank (continuous / intermittent) |  | A | LV power feeder | 480 | 10 | 14.2 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 chemical feed skid (phosphate / amine) |  | A | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 chemical feed skid (phosphate / amine) |  | A | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 chemical feed skid (phosphate / amine) |  | A | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 chemical feed skid (phosphate / amine) |  | A | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 chemical feed skid (phosphate / amine) |  | A | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 chemical feed skid (phosphate / amine) |  | A | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HRSG 3 stack | STK-3 | A | Area / platform lighting circuit 1 (6 fixtures) | 480 | 3 | 5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
HTP-1: heat-trace panel (rack) | HTP-1 | A | LV power feeder | 480 | 120 | 169.8 | R1 LC-480-B (480 V switchgear) | LV 600 V | 4/0 | 1
HTP-1: heat-trace panel (rack) | HTP-1 | A | Heat-trace circuit 1 (power to the trace junction box) | 480 | 4 | 6 | HTP-1: heat-trace panel (rack) | LV 600 V | 10 | 1
HTP-1: heat-trace panel (rack) | HTP-1 | A | Heat-trace circuit 2 (power to the trace junction box) | 480 | 4 | 6 | HTP-1: heat-trace panel (rack) | LV 600 V | 10 | 1
HTP-1: heat-trace panel (rack) | HTP-1 | A | Heat-trace circuit 3 (power to the trace junction box) | 480 | 4 | 6 | HTP-1: heat-trace panel (rack) | LV 600 V | 10 | 1
HTP-1: heat-trace panel (rack) | HTP-1 | A | Heat-trace circuit 4 (power to the trace junction box) | 480 | 4 | 6 | HTP-1: heat-trace panel (rack) | LV 600 V | 10 | 1
HTP-1: heat-trace panel (rack) | HTP-1 | A | Heat-trace circuit 5 (power to the trace junction box) | 480 | 4 | 6 | HTP-1: heat-trace panel (rack) | LV 600 V | 10 | 1
HTP-1: heat-trace panel (rack) | HTP-1 | A | Heat-trace circuit 6 (power to the trace junction box) | 480 | 4 | 6 | HTP-1: heat-trace panel (rack) | LV 600 V | 10 | 1
HTP-1: heat-trace panel (rack) | HTP-1 | A | Heat-trace circuit 7 (power to the trace junction box) | 480 | 4 | 6 | HTP-1: heat-trace panel (rack) | LV 600 V | 10 | 1
HTP-1: heat-trace panel (rack) | HTP-1 | A | Heat-trace circuit 8 (power to the trace junction box) | 480 | 4 | 6 | HTP-1: heat-trace panel (rack) | LV 600 V | 10 | 1
HTP-1: heat-trace panel (rack) | HTP-1 | A | Heat-trace circuit 9 (power to the trace junction box) | 480 | 4 | 6 | HTP-1: heat-trace panel (rack) | LV 600 V | 10 | 1
HTP-1: heat-trace panel (rack) | HTP-1 | A | Heat-trace circuit 10 (power to the trace junction box) | 480 | 4 | 6 | HTP-1: heat-trace panel (rack) | LV 600 V | 10 | 1
HTP-1: heat-trace panel (rack) | HTP-1 | A | Heat-trace circuit 11 (power to the trace junction box) | 480 | 4 | 6 | HTP-1: heat-trace panel (rack) | LV 600 V | 10 | 1
HTP-1: heat-trace panel (rack) | HTP-1 | A | Heat-trace circuit 12 (power to the trace junction box) | 480 | 4 | 6 | HTP-1: heat-trace panel (rack) | LV 600 V | 10 | 1
HTP-1: heat-trace panel (rack) | HTP-1 | A | Heat-trace circuit 13 (power to the trace junction box) | 480 | 4 | 6 | HTP-1: heat-trace panel (rack) | LV 600 V | 10 | 1
HTP-1: heat-trace panel (rack) | HTP-1 | A | Heat-trace circuit 14 (power to the trace junction box) | 480 | 4 | 6 | HTP-1: heat-trace panel (rack) | LV 600 V | 10 | 1
HTP-1: heat-trace panel (rack) | HTP-1 | A | Heat-trace circuit 15 (power to the trace junction box) | 480 | 4 | 6 | HTP-1: heat-trace panel (rack) | LV 600 V | 10 | 1
HTP-1: heat-trace panel (rack) | HTP-1 | A | Heat-trace circuit 16 (power to the trace junction box) | 480 | 4 | 6 | HTP-1: heat-trace panel (rack) | LV 600 V | 10 | 1
HTP-1: heat-trace panel (rack) | HTP-1 | A | Heat-trace circuit 17 (power to the trace junction box) | 480 | 4 | 6 | HTP-1: heat-trace panel (rack) | LV 600 V | 10 | 1
HTP-1: heat-trace panel (rack) | HTP-1 | A | Heat-trace circuit 18 (power to the trace junction box) | 480 | 4 | 6 | HTP-1: heat-trace panel (rack) | LV 600 V | 10 | 1
HTP-1: heat-trace panel (rack) | HTP-1 | A | Heat-trace circuit 19 (power to the trace junction box) | 480 | 4 | 6 | HTP-1: heat-trace panel (rack) | LV 600 V | 10 | 1
HTP-1: heat-trace panel (rack) | HTP-1 | A | Heat-trace circuit 20 (power to the trace junction box) | 480 | 4 | 6 | HTP-1: heat-trace panel (rack) | LV 600 V | 10 | 1
HTP-1: heat-trace panel (rack) | HTP-1 | A | Heat-trace circuit 21 (power to the trace junction box) | 480 | 4 | 6 | HTP-1: heat-trace panel (rack) | LV 600 V | 10 | 1
HTP-1: heat-trace panel (rack) | HTP-1 | A | Heat-trace circuit 22 (power to the trace junction box) | 480 | 4 | 6 | HTP-1: heat-trace panel (rack) | LV 600 V | 10 | 1
HTP-1: heat-trace panel (rack) | HTP-1 | A | Heat-trace circuit 23 (power to the trace junction box) | 480 | 4 | 6 | HTP-1: heat-trace panel (rack) | LV 600 V | 10 | 1
HTP-1: heat-trace panel (rack) | HTP-1 | A | Heat-trace circuit 24 (power to the trace junction box) | 480 | 4 | 6 | HTP-1: heat-trace panel (rack) | LV 600 V | 10 | 1
LCT-A: 13.8/0.48 kV load-centre transformer | LCT-A | A | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | R1 LC-480-B (480 V switchgear) | LV 600 V | 10 | 1
LCT-A: 13.8/0.48 kV load-centre transformer | LCT-A | A | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | R1 LC-480-B (480 V switchgear) | LV 600 V | 10 | 1
LCT-A: 13.8/0.48 kV load-centre transformer | LCT-A | A | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | R1 LC-480-B (480 V switchgear) | LV 600 V | 10 | 1
LCT-A: 13.8/0.48 kV load-centre transformer | LCT-A | A | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | R1 LC-480-B (480 V switchgear) | LV 600 V | 10 | 1
LCT-A: 13.8/0.48 kV load-centre transformer | LCT-A | A | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | R1 LC-480-B (480 V switchgear) | LV 600 V | 10 | 1
LCT-A: 13.8/0.48 kV load-centre transformer | LCT-A | A | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | R1 LC-480-B (480 V switchgear) | LV 600 V | 10 | 1
LCT-B: 13.8/0.48 kV load-centre transformer | LCT-B | A | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | R1 LC-480-B (480 V switchgear) | LV 600 V | 10 | 1
LCT-B: 13.8/0.48 kV load-centre transformer | LCT-B | A | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | R1 LC-480-B (480 V switchgear) | LV 600 V | 10 | 1
LCT-B: 13.8/0.48 kV load-centre transformer | LCT-B | A | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | R1 LC-480-B (480 V switchgear) | LV 600 V | 10 | 1
LCT-B: 13.8/0.48 kV load-centre transformer | LCT-B | A | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | R1 LC-480-B (480 V switchgear) | LV 600 V | 10 | 1
LCT-B: 13.8/0.48 kV load-centre transformer | LCT-B | A | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | R1 LC-480-B (480 V switchgear) | LV 600 V | 10 | 1
LCT-B: 13.8/0.48 kV load-centre transformer | LCT-B | A | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | R1 LC-480-B (480 V switchgear) | LV 600 V | 10 | 1
R1 EMCC (emergency MCC) | EMCC | A | EDG-1 480 V output to EMCC | 480 | 3000 | 3609 | EDG-1: 3 MW emergency diesel generator (480 V) | LV 600 V | 500 kcmil | 13
R1 EMCC (emergency MCC) | EMCC | A | EDG-2 480 V output to EMCC | 480 | 3000 | 3609 | EDG-2: 3 MW emergency diesel generator (480 V) | LV 600 V | 500 kcmil | 13
R1 EMCC (emergency MCC) | EMCC | A | EMCC normal supply from LC-480-A | 480 | 400 | 506.5 | R1 LC-480-A (480 V switchgear) | LV 600 V | 500 kcmil | 2
R1: main electrical building (64 x 180 ft) | R1 | A | LV panel / distribution feeder | 480 | 138 | 195.3 | R1 LC-480-A (480 V switchgear) | LV 600 V | 350 kcmil | 1
R2A: unit / HRSG electrical e-house (32 x 40 ft) | R2A | A | LV panel / distribution feeder | 480 | 30 | 42.5 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 6 | 1
R2B: unit / HRSG electrical e-house (32 x 40 ft) | R2B | A | LV panel / distribution feeder | 480 | 30 | 42.5 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 6 | 1
R2C: unit / HRSG electrical e-house (32 x 40 ft) | R2C | A | LV panel / distribution feeder | 480 | 30 | 42.5 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 6 | 1
R3: ST auxiliary electrical e-house (40 x 65 ft) | R3 | A | LV panel / distribution feeder | 480 | 250 | 353.8 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 4/0 | 2
SCRB-1A/B: SCR dilution-air blowers | SCRB-1 | A | Motor 1 of 2, 110 kW | 480 | 110 | 155.7 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 3/0 | 1
SCRB-1A/B: SCR dilution-air blowers | SCRB-1 | A | Motor 2 of 2, 110 kW | 480 | 110 | 155.7 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 3/0 | 1
SCRB-2A/B: SCR dilution-air blowers | SCRB-2 | A | Motor 1 of 2, 110 kW | 480 | 110 | 155.7 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 3/0 | 1
SCRB-2A/B: SCR dilution-air blowers | SCRB-2 | A | Motor 2 of 2, 110 kW | 480 | 110 | 155.7 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 3/0 | 1
SCRB-3A/B: SCR dilution-air blowers | SCRB-3 | A | Motor 1 of 2, 110 kW | 480 | 110 | 155.7 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 3/0 | 1
SCRB-3A/B: SCR dilution-air blowers | SCRB-3 | A | Motor 2 of 2, 110 kW | 480 | 110 | 155.7 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 3/0 | 1
SOS-1: GTG-1 seal-oil and H2 / CO2 gas-control skid | SOS-1 | A | Motor 1 of 3, 15 kW | 480 | 15 | 21.2 | R1 MCC-GT1 | LV 600 V | 6 | 1
SOS-1: GTG-1 seal-oil and H2 / CO2 gas-control skid | SOS-1 | A | Motor 2 of 3, 15 kW | 480 | 15 | 21.2 | R1 MCC-GT1 | LV 600 V | 6 | 1
SOS-1: GTG-1 seal-oil and H2 / CO2 gas-control skid | SOS-1 | A | Motor 3 of 3, 15 kW | 480 | 15 | 21.2 | R1 MCC-GT1 | LV 600 V | 6 | 1
SOS-2: GTG-2 seal-oil and H2 / CO2 gas-control skid | SOS-2 | A | Motor 1 of 3, 15 kW | 480 | 15 | 21.2 | R1 MCC-GT2 | LV 600 V | 4 | 1
SOS-2: GTG-2 seal-oil and H2 / CO2 gas-control skid | SOS-2 | A | Motor 2 of 3, 15 kW | 480 | 15 | 21.2 | R1 MCC-GT2 | LV 600 V | 4 | 1
SOS-2: GTG-2 seal-oil and H2 / CO2 gas-control skid | SOS-2 | A | Motor 3 of 3, 15 kW | 480 | 15 | 21.2 | R1 MCC-GT2 | LV 600 V | 4 | 1
SOS-3: GTG-3 seal-oil and H2 / CO2 gas-control skid | SOS-3 | A | Motor 1 of 3, 15 kW | 480 | 15 | 21.2 | R1 MCC-GT3 | LV 600 V | 4 | 1
SOS-3: GTG-3 seal-oil and H2 / CO2 gas-control skid | SOS-3 | A | Motor 2 of 3, 15 kW | 480 | 15 | 21.2 | R1 MCC-GT3 | LV 600 V | 4 | 1
SOS-3: GTG-3 seal-oil and H2 / CO2 gas-control skid | SOS-3 | A | Motor 3 of 3, 15 kW | 480 | 15 | 21.2 | R1 MCC-GT3 | LV 600 V | 4 | 1
ST aux: lube oil, turning gear, EHC | ST aux | A | Motor 1 of 10, 40 kW | 480 | 40 | 56.6 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 4 | 1
ST aux: lube oil, turning gear, EHC | ST aux | A | Motor 2 of 10, 40 kW | 480 | 40 | 56.6 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 4 | 1
ST aux: lube oil, turning gear, EHC | ST aux | A | Motor 3 of 10, 40 kW | 480 | 40 | 56.6 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 4 | 1
ST aux: lube oil, turning gear, EHC | ST aux | A | Motor 4 of 10, 40 kW | 480 | 40 | 56.6 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 4 | 1
ST aux: lube oil, turning gear, EHC | ST aux | A | Motor 5 of 10, 40 kW | 480 | 40 | 56.6 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 4 | 1
ST aux: lube oil, turning gear, EHC | ST aux | A | Motor 6 of 10, 40 kW | 480 | 40 | 56.6 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 4 | 1
ST aux: lube oil, turning gear, EHC | ST aux | A | Motor 7 of 10, 40 kW | 480 | 40 | 56.6 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 4 | 1
ST aux: lube oil, turning gear, EHC | ST aux | A | Motor 8 of 10, 40 kW | 480 | 40 | 56.6 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 4 | 1
ST aux: lube oil, turning gear, EHC | ST aux | A | Motor 9 of 10, 40 kW | 480 | 40 | 56.6 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 4 | 1
ST aux: lube oil, turning gear, EHC | ST aux | A | Motor 10 of 10, 40 kW | 480 | 40 | 56.6 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 4 | 1
ST: steam turbine (HP/IP + LP), ACC plant | ST | A | MOV 1: power | 480 | 2.5 | 3.5 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
ST: steam turbine (HP/IP + LP), ACC plant | ST | A | MOV 2: power | 480 | 2.5 | 3.5 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
ST: steam turbine (HP/IP + LP), ACC plant | ST | A | MOV 3: power | 480 | 2.5 | 3.5 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
ST: steam turbine (HP/IP + LP), ACC plant | ST | A | MOV 4: power | 480 | 2.5 | 3.5 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
ST: steam turbine (HP/IP + LP), ACC plant | ST | A | MOV 5: power | 480 | 2.5 | 3.5 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
ST: steam turbine (HP/IP + LP), ACC plant | ST | A | MOV 6: power | 480 | 2.5 | 3.5 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
ST: steam turbine (HP/IP + LP), ACC plant | ST | A | MOV 7: power | 480 | 2.5 | 3.5 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
ST: steam turbine (HP/IP + LP), ACC plant | ST | A | MOV 8: power | 480 | 2.5 | 3.5 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
ST: steam turbine (HP/IP + LP), ACC plant | ST | A | MOV 9: power | 480 | 2.5 | 3.5 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
ST: steam turbine (HP/IP + LP), ACC plant | ST | A | MOV 10: power | 480 | 2.5 | 3.5 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
ST: steam turbine (HP/IP + LP), ACC plant | ST | A | MOV 11: power | 480 | 2.5 | 3.5 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
ST: steam turbine (HP/IP + LP), ACC plant | ST | A | MOV 12: power | 480 | 2.5 | 3.5 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
ST: steam turbine (HP/IP + LP), ACC plant | ST | A | MOV 13: power | 480 | 2.5 | 3.5 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
ST: steam turbine (HP/IP + LP), ACC plant | ST | A | MOV 14: power | 480 | 2.5 | 3.5 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
ST: steam turbine (HP/IP + LP), ACC plant | ST | A | MOV 15: power | 480 | 2.5 | 3.5 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
ST: steam turbine (HP/IP + LP), ACC plant | ST | A | MOV 16: power | 480 | 2.5 | 3.5 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
ST: steam turbine (HP/IP + LP), ACC plant | ST | A | MOV 17: power | 480 | 2.5 | 3.5 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
ST: steam turbine (HP/IP + LP), ACC plant | ST | A | MOV 18: power | 480 | 2.5 | 3.5 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
ST: steam turbine (HP/IP + LP), ACC plant | ST | A | MOV 19: power | 480 | 2.5 | 3.5 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
ST: steam turbine (HP/IP + LP), ACC plant | ST | A | MOV 20: power | 480 | 2.5 | 3.5 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
ST: steam turbine (HP/IP + LP), ACC plant | ST | A | LV power feeder | 480 | 15 | 21.2 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
ST: steam turbine (HP/IP + LP), ACC plant | ST | A | 480 V welding receptacle 1 | 480 | 60 | 76 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 2 | 1
ST: steam turbine (HP/IP + LP), ACC plant | ST | A | 480 V welding receptacle 2 | 480 | 60 | 76 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 2 | 1
ST: steam turbine (HP/IP + LP), ACC plant | ST | A | 480 V welding receptacle 3 | 480 | 60 | 76 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 2 | 1
ST: steam turbine (HP/IP + LP), ACC plant | ST | A | 480 V welding receptacle 4 | 480 | 60 | 76 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 2 | 1
STG: steam-turbine generator | STG | A | Motor 1 of 4, 2 kW | 480 | 2 | 2.8 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
STG: steam-turbine generator | STG | A | Motor 2 of 4, 2 kW | 480 | 2 | 2.8 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
STG: steam-turbine generator | STG | A | Motor 3 of 4, 2 kW | 480 | 2 | 2.8 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
STG: steam-turbine generator | STG | A | Motor 4 of 4, 2 kW | 480 | 2 | 2.8 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
SWAS: steam and water analysis | SWAS | A | LV power feeder | 480 | 15 | 21.2 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
T-R2A: 13.8/0.48 kV |  | A | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
T-R2A: 13.8/0.48 kV |  | A | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
T-R2A: 13.8/0.48 kV |  | A | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
T-R2A: 13.8/0.48 kV |  | A | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
T-R2A: 13.8/0.48 kV |  | A | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
T-R2A: 13.8/0.48 kV |  | A | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
T-R2B: 13.8/0.48 kV |  | A | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
T-R2B: 13.8/0.48 kV |  | A | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
T-R2B: 13.8/0.48 kV |  | A | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
T-R2B: 13.8/0.48 kV |  | A | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
T-R2B: 13.8/0.48 kV |  | A | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
T-R2B: 13.8/0.48 kV |  | A | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
T-R2C: 13.8/0.48 kV |  | A | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
T-R2C: 13.8/0.48 kV |  | A | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
T-R2C: 13.8/0.48 kV |  | A | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
T-R2C: 13.8/0.48 kV |  | A | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
T-R2C: 13.8/0.48 kV |  | A | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
T-R2C: 13.8/0.48 kV |  | A | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
T-R3: 13.8/0.48 kV |  | A | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
T-R3: 13.8/0.48 kV |  | A | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
T-R3: 13.8/0.48 kV |  | A | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
T-R3: 13.8/0.48 kV |  | A | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
T-R3: 13.8/0.48 kV |  | A | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
T-R3: 13.8/0.48 kV |  | A | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 10 | 1
T4-A: 13.8/4.16 kV station transformer | T4-A | A | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | R1 LC-480-B (480 V switchgear) | LV 600 V | 10 | 1
T4-A: 13.8/4.16 kV station transformer | T4-A | A | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | R1 LC-480-B (480 V switchgear) | LV 600 V | 10 | 1
T4-A: 13.8/4.16 kV station transformer | T4-A | A | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | R1 LC-480-B (480 V switchgear) | LV 600 V | 10 | 1
T4-A: 13.8/4.16 kV station transformer | T4-A | A | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | R1 LC-480-B (480 V switchgear) | LV 600 V | 10 | 1
T4-A: 13.8/4.16 kV station transformer | T4-A | A | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | R1 LC-480-B (480 V switchgear) | LV 600 V | 10 | 1
T4-A: 13.8/4.16 kV station transformer | T4-A | A | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | R1 LC-480-B (480 V switchgear) | LV 600 V | 10 | 1
T4-B: 13.8/4.16 kV station transformer | T4-B | A | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | R1 LC-480-B (480 V switchgear) | LV 600 V | 10 | 1
T4-B: 13.8/4.16 kV station transformer | T4-B | A | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | R1 LC-480-B (480 V switchgear) | LV 600 V | 10 | 1
T4-B: 13.8/4.16 kV station transformer | T4-B | A | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | R1 LC-480-B (480 V switchgear) | LV 600 V | 10 | 1
T4-B: 13.8/4.16 kV station transformer | T4-B | A | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | R1 LC-480-B (480 V switchgear) | LV 600 V | 10 | 1
T4-B: 13.8/4.16 kV station transformer | T4-B | A | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | R1 LC-480-B (480 V switchgear) | LV 600 V | 10 | 1
T4-B: 13.8/4.16 kV station transformer | T4-B | A | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | R1 LC-480-B (480 V switchgear) | LV 600 V | 10 | 1
TCP-1: GT1 turbine control and protection cabinets | TCP-1 | A | LV power feeder | 480 | 15 | 21.2 | R1 MCC-GT1 | LV 600 V | 8 | 1
TCP-2: GT2 turbine control and protection cabinets | TCP-2 | A | LV power feeder | 480 | 15 | 21.2 | R1 MCC-GT2 | LV 600 V | 6 | 1
TCP-3: GT3 turbine control and protection cabinets | TCP-3 | A | LV power feeder | 480 | 15 | 21.2 | R1 MCC-GT3 | LV 600 V | 4 | 1
TCP-ST: ST turbine control and protection cabinets | TCP-ST | A | LV power feeder | 480 | 15 | 21.2 | R3: ST auxiliary electrical e-house (40 x 65 ft) | LV 600 V | 6 | 1
Turbine hall exterior electrical: MC-cable risers, roof exhausters, wa |  | A | Turbine hall roof exhausters / louvres / exterior lighting panel | 480 | 120 | 151.9 | R1 LC-480-A (480 V switchgear) | LV 600 V | 3/0 | 1
UAT-1: 21/13.8 kV unit auxiliary transformer | UAT-1 | A | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
UAT-1: 21/13.8 kV unit auxiliary transformer | UAT-1 | A | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
UAT-1: 21/13.8 kV unit auxiliary transformer | UAT-1 | A | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
UAT-1: 21/13.8 kV unit auxiliary transformer | UAT-1 | A | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
UAT-1: 21/13.8 kV unit auxiliary transformer | UAT-1 | A | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
UAT-1: 21/13.8 kV unit auxiliary transformer | UAT-1 | A | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | R2A: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
UAT-2: 21/13.8 kV unit auxiliary transformer | UAT-2 | A | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
UAT-2: 21/13.8 kV unit auxiliary transformer | UAT-2 | A | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
UAT-2: 21/13.8 kV unit auxiliary transformer | UAT-2 | A | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
UAT-2: 21/13.8 kV unit auxiliary transformer | UAT-2 | A | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
UAT-2: 21/13.8 kV unit auxiliary transformer | UAT-2 | A | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
UAT-2: 21/13.8 kV unit auxiliary transformer | UAT-2 | A | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | R2B: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
UAT-3: 21/13.8 kV unit auxiliary transformer | UAT-3 | A | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
UAT-3: 21/13.8 kV unit auxiliary transformer | UAT-3 | A | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
UAT-3: 21/13.8 kV unit auxiliary transformer | UAT-3 | A | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
UAT-3: 21/13.8 kV unit auxiliary transformer | UAT-3 | A | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
UAT-3: 21/13.8 kV unit auxiliary transformer | UAT-3 | A | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
UAT-3: 21/13.8 kV unit auxiliary transformer | UAT-3 | A | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | R2C: unit / HRSG electrical e-house (32 x 40 ft) | LV 600 V | 10 | 1
WASH-GT1: compressor water-wash skid | WASH-GT1 | A | Motor 1 of 2, 22 kW | 480 | 22 | 31.1 | R1 MCC-GT1 | LV 600 V | 6 | 1
WASH-GT1: compressor water-wash skid | WASH-GT1 | A | Motor 2 of 2, 22 kW | 480 | 22 | 31.1 | R1 MCC-GT1 | LV 600 V | 6 | 1
WASH-GT2: compressor water-wash skid | WASH-GT2 | A | Motor 1 of 2, 22 kW | 480 | 22 | 31.1 | R1 MCC-GT2 | LV 600 V | 4 | 1
WASH-GT2: compressor water-wash skid | WASH-GT2 | A | Motor 2 of 2, 22 kW | 480 | 22 | 31.1 | R1 MCC-GT2 | LV 600 V | 4 | 1
WASH-GT3: compressor water-wash skid | WASH-GT3 | A | Motor 1 of 2, 22 kW | 480 | 22 | 31.1 | R1 MCC-GT3 | LV 600 V | 4 | 1
WASH-GT3: compressor water-wash skid | WASH-GT3 | A | Motor 2 of 2, 22 kW | 480 | 22 | 31.1 | R1 MCC-GT3 | LV 600 V | 4 | 1
BFP-1A/B: boiler feed pumps (13.8 kV DOL) | BFP-1 | A | Boiler feed pump BFP-1A / 1B | 13800 | 5000 | 232 | R1 SWGR-13.8-1 (11 x 36 in cubicles, 15 kV metal-clad) | MV 15 kV | 250 kcmil | 1
BFP-1A/B: boiler feed pumps (13.8 kV DOL) | BFP-1 | A | Boiler feed pump BFP-1A / 1B | 13800 | 5000 | 232 | R1 SWGR-13.8-1 (11 x 36 in cubicles, 15 kV metal-clad) | MV 15 kV | 250 kcmil | 1
BFP-2A/B: boiler feed pumps (13.8 kV DOL) | BFP-2 | A | Boiler feed pump BFP-2A / 2B | 13800 | 5000 | 232 | R1 SWGR-13.8-2 (11 x 36 in cubicles, 15 kV metal-clad) | MV 15 kV | 250 kcmil | 1
BFP-2A/B: boiler feed pumps (13.8 kV DOL) | BFP-2 | A | Boiler feed pump BFP-2A / 2B | 13800 | 5000 | 232 | R1 SWGR-13.8-2 (11 x 36 in cubicles, 15 kV metal-clad) | MV 15 kV | 250 kcmil | 1
BFP-3A/B: boiler feed pumps (13.8 kV DOL) | BFP-3 | A | Boiler feed pump BFP-3A / 3B | 13800 | 5000 | 232 | R1 SWGR-13.8-3 (11 x 36 in cubicles, 15 kV metal-clad) | MV 15 kV | 250 kcmil | 1
BFP-3A/B: boiler feed pumps (13.8 kV DOL) | BFP-3 | A | Boiler feed pump BFP-3A / 3B | 13800 | 5000 | 232 | R1 SWGR-13.8-3 (11 x 36 in cubicles, 15 kV metal-clad) | MV 15 kV | 250 kcmil | 1
LCT-A: 13.8/0.48 kV load-centre transformer | LCT-A | A | LCT-A unit / load-centre transformer primary | 13800 | 3000 | 126 | R1 SWGR-13.8-1 (11 x 36 in cubicles, 15 kV metal-clad) | MV 15 kV | 1/0 | 1
LCT-B: 13.8/0.48 kV load-centre transformer | LCT-B | A | LCT-B unit / load-centre transformer primary | 13800 | 3000 | 126 | R1 SWGR-13.8-3 (11 x 36 in cubicles, 15 kV metal-clad) | MV 15 kV | 1/0 | 1
R1 SWGR-13.8-1 (11 x 36 in cubicles, 15 kV metal-clad) | SWGR-13.8-1 | A | UAT-1 secondary to SWGR-13.8-1 incomer | 13800 | 40000 | 1674 | UAT-1: 21/13.8 kV unit auxiliary transformer | MV 15 kV | 750 kcmil | 4
R1 SWGR-13.8-2 (11 x 36 in cubicles, 15 kV metal-clad) | SWGR-13.8-2 | A | UAT-2 secondary to SWGR-13.8-2 incomer | 13800 | 40000 | 1674 | UAT-2: 21/13.8 kV unit auxiliary transformer | MV 15 kV | 750 kcmil | 4
R1 SWGR-13.8-3 (11 x 36 in cubicles, 15 kV metal-clad) | SWGR-13.8-3 | A | UAT-3 secondary to SWGR-13.8-3 incomer | 13800 | 40000 | 1674 | UAT-3: 21/13.8 kV unit auxiliary transformer | MV 15 kV | 750 kcmil | 4
R1 TX-LCI-1 dry-type input transformer | TX-LCI-1 | A | Static starter LCI-1 input transformer | 13800 | 9000 | 377 | R1 SWGR-13.8-1 (11 x 36 in cubicles, 15 kV metal-clad) | MV 15 kV | 750 kcmil | 1
R1 TX-LCI-2 dry-type input transformer | TX-LCI-2 | A | Static starter LCI-2 input transformer | 13800 | 9000 | 377 | R1 SWGR-13.8-2 (11 x 36 in cubicles, 15 kV metal-clad) | MV 15 kV | 750 kcmil | 1
R1 TX-LCI-3 dry-type input transformer | TX-LCI-3 | A | Static starter LCI-3 input transformer | 13800 | 9000 | 377 | R1 SWGR-13.8-3 (11 x 36 in cubicles, 15 kV metal-clad) | MV 15 kV | 750 kcmil | 1
T-R2A: 13.8/0.48 kV |  | A | T-R2A unit / load-centre transformer primary | 13800 | 2500 | 105 | R1 SWGR-13.8-1 (11 x 36 in cubicles, 15 kV metal-clad) | MV 15 kV | 2 | 1
T-R2B: 13.8/0.48 kV |  | A | T-R2B unit / load-centre transformer primary | 13800 | 2500 | 105 | R1 SWGR-13.8-2 (11 x 36 in cubicles, 15 kV metal-clad) | MV 15 kV | 2 | 1
T-R2C: 13.8/0.48 kV |  | A | T-R2C unit / load-centre transformer primary | 13800 | 2500 | 105 | R1 SWGR-13.8-3 (11 x 36 in cubicles, 15 kV metal-clad) | MV 15 kV | 2 | 1
T-R3: 13.8/0.48 kV |  | A | T-R3 unit / load-centre transformer primary | 13800 | 3000 | 126 | R1 SWGR-13.8-2 (11 x 36 in cubicles, 15 kV metal-clad) | MV 15 kV | 1/0 | 1
T4-A: 13.8/4.16 kV station transformer | T4-A | A | T4-A station transformer primary | 13800 | 10000 | 418 | R1 SWGR-13.8-1 (11 x 36 in cubicles, 15 kV metal-clad) | MV 15 kV | 750 kcmil | 1
T4-B: 13.8/4.16 kV station transformer | T4-B | A | T4-B station transformer primary | 13800 | 10000 | 418 | R1 SWGR-13.8-3 (11 x 36 in cubicles, 15 kV metal-clad) | MV 15 kV | 750 kcmil | 1
ET-1: excitation transformer (dry type, GTG-1 terminals) | ET-1 | A | Excitation transformer ET-1 from the IPB tap | 21000 | 3000 | 82 | GSU-1: 21/230 kV generator step-up transformer | MV 25 kV | 2 | 1
ET-2: excitation transformer (dry type, GTG-2 terminals) | ET-2 | A | Excitation transformer ET-2 from the IPB tap | 21000 | 3000 | 82 | GSU-2: 21/230 kV generator step-up transformer | MV 25 kV | 2 | 1
ET-3: excitation transformer (dry type, GTG-3 terminals) | ET-3 | A | Excitation transformer ET-3 from the IPB tap | 21000 | 3000 | 82 | GSU-3: 21/230 kV generator step-up transformer | MV 25 kV | 2 | 1
R1 SWGR-4.16-A (9 x 36 in cubicles, 5 kV metal-clad) | SWGR-4.16-A | A | T4-A secondary to SWGR-4.16-A incomer | 4160 | 10000 | 1388 | T4-A: 13.8/4.16 kV station transformer | MV 5 kV | 1000 kcmil | 3
R1 SWGR-4.16-B (5 kV metal-clad) | SWGR-4.16-B | A | T4-B secondary to SWGR-4.16-B incomer | 4160 | 10000 | 1388 | T4-B: 13.8/4.16 kV station transformer | MV 5 kV | 1000 kcmil | 3
ACC fan motor F01 | ACC-F01 | B | ACC fan F01 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F02 | ACC-F02 | B | ACC fan F02 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F03 | ACC-F03 | B | ACC fan F03 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F04 | ACC-F04 | B | ACC fan F04 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F05 | ACC-F05 | B | ACC fan F05 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F06 | ACC-F06 | B | ACC fan F06 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F07 | ACC-F07 | B | ACC fan F07 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F08 | ACC-F08 | B | ACC fan F08 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F09 | ACC-F09 | B | ACC fan F09 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F10 | ACC-F10 | B | ACC fan F10 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F11 | ACC-F11 | B | ACC fan F11 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F12 | ACC-F12 | B | ACC fan F12 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F13 | ACC-F13 | B | ACC fan F13 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F14 | ACC-F14 | B | ACC fan F14 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F15 | ACC-F15 | B | ACC fan F15 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F16 | ACC-F16 | B | ACC fan F16 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F17 | ACC-F17 | B | ACC fan F17 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F18 | ACC-F18 | B | ACC fan F18 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F19 | ACC-F19 | B | ACC fan F19 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F20 | ACC-F20 | B | ACC fan F20 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F21 | ACC-F21 | B | ACC fan F21 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F22 | ACC-F22 | B | ACC fan F22 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F23 | ACC-F23 | B | ACC fan F23 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F24 | ACC-F24 | B | ACC fan F24 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F25 | ACC-F25 | B | ACC fan F25 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F26 | ACC-F26 | B | ACC fan F26 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F27 | ACC-F27 | B | ACC fan F27 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F28 | ACC-F28 | B | ACC fan F28 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F29 | ACC-F29 | B | ACC fan F29 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F30 | ACC-F30 | B | ACC fan F30 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F31 | ACC-F31 | B | ACC fan F31 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F32 | ACC-F32 | B | ACC fan F32 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F33 | ACC-F33 | B | ACC fan F33 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F34 | ACC-F34 | B | ACC fan F34 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F35 | ACC-F35 | B | ACC fan F35 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F36 | ACC-F36 | B | ACC fan F36 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F37 | ACC-F37 | B | ACC fan F37 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F38 | ACC-F38 | B | ACC fan F38 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F39 | ACC-F39 | B | ACC fan F39 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F40 | ACC-F40 | B | ACC fan F40 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F41 | ACC-F41 | B | ACC fan F41 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F42 | ACC-F42 | B | ACC fan F42 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F43 | ACC-F43 | B | ACC fan F43 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F44 | ACC-F44 | B | ACC fan F44 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F45 | ACC-F45 | B | ACC fan F45 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F46 | ACC-F46 | B | ACC fan F46 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F47 | ACC-F47 | B | ACC fan F47 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F48 | ACC-F48 | B | ACC fan F48 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F49 | ACC-F49 | B | ACC fan F49 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F50 | ACC-F50 | B | ACC fan F50 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F51 | ACC-F51 | B | ACC fan F51 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F52 | ACC-F52 | B | ACC fan F52 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F53 | ACC-F53 | B | ACC fan F53 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F54 | ACC-F54 | B | ACC fan F54 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F55 | ACC-F55 | B | ACC fan F55 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F56 | ACC-F56 | B | ACC fan F56 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F57 | ACC-F57 | B | ACC fan F57 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F58 | ACC-F58 | B | ACC fan F58 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F59 | ACC-F59 | B | ACC fan F59 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F60 | ACC-F60 | B | ACC fan F60 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F61 | ACC-F61 | B | ACC fan F61 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F62 | ACC-F62 | B | ACC fan F62 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F63 | ACC-F63 | B | ACC fan F63 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F64 | ACC-F64 | B | ACC fan F64 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F65 | ACC-F65 | B | ACC fan F65 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F66 | ACC-F66 | B | ACC fan F66 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F67 | ACC-F67 | B | ACC fan F67 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F68 | ACC-F68 | B | ACC fan F68 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F69 | ACC-F69 | B | ACC fan F69 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F70 | ACC-F70 | B | ACC fan F70 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F71 | ACC-F71 | B | ACC fan F71 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F72 | ACC-F72 | B | ACC fan F72 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F73 | ACC-F73 | B | ACC fan F73 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F74 | ACC-F74 | B | ACC fan F74 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F75 | ACC-F75 | B | ACC fan F75 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F76 | ACC-F76 | B | ACC fan F76 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F77 | ACC-F77 | B | ACC fan F77 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F78 | ACC-F78 | B | ACC fan F78 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F79 | ACC-F79 | B | ACC fan F79 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
ACC fan motor F80 | ACC-F80 | B | ACC fan F80 motor (VFD output) | 480 | 150 | 212 | R4: ACC electrical (VFD) e-house (60 x 120 ft) | LV 600 V | 350 kcmil | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | MOV 1: power | 480 | 2.5 | 3.5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | MOV 2: power | 480 | 2.5 | 3.5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | MOV 3: power | 480 | 2.5 | 3.5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | MOV 4: power | 480 | 2.5 | 3.5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | MOV 5: power | 480 | 2.5 | 3.5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | MOV 6: power | 480 | 2.5 | 3.5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | MOV 7: power | 480 | 2.5 | 3.5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | MOV 8: power | 480 | 2.5 | 3.5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | MOV 9: power | 480 | 2.5 | 3.5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | MOV 10: power | 480 | 2.5 | 3.5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | MOV 11: power | 480 | 2.5 | 3.5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | MOV 12: power | 480 | 2.5 | 3.5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | MOV 13: power | 480 | 2.5 | 3.5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | MOV 14: power | 480 | 2.5 | 3.5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | MOV 15: power | 480 | 2.5 | 3.5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | MOV 16: power | 480 | 2.5 | 3.5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | MOV 17: power | 480 | 2.5 | 3.5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | MOV 18: power | 480 | 2.5 | 3.5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | MOV 19: power | 480 | 2.5 | 3.5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | MOV 20: power | 480 | 2.5 | 3.5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | MOV 21: power | 480 | 2.5 | 3.5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | MOV 22: power | 480 | 2.5 | 3.5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | MOV 23: power | 480 | 2.5 | 3.5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | MOV 24: power | 480 | 2.5 | 3.5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | MOV 25: power | 480 | 2.5 | 3.5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | MOV 26: power | 480 | 2.5 | 3.5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | MOV 27: power | 480 | 2.5 | 3.5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | MOV 28: power | 480 | 2.5 | 3.5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | MOV 29: power | 480 | 2.5 | 3.5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | MOV 30: power | 480 | 2.5 | 3.5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | Area / platform lighting circuit 1 (12 fixtures) | 480 | 3 | 5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | Area / platform lighting circuit 2 (12 fixtures) | 480 | 3 | 5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | Area / platform lighting circuit 3 (12 fixtures) | 480 | 3 | 5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | Area / platform lighting circuit 4 (12 fixtures) | 480 | 3 | 5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | Area / platform lighting circuit 5 (12 fixtures) | 480 | 3 | 5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | Area / platform lighting circuit 6 (12 fixtures) | 480 | 3 | 5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | Area / platform lighting circuit 7 (8 fixtures) | 480 | 3 | 5 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | 480 V welding receptacle 1 | 480 | 60 | 76 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 2 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | 480 V welding receptacle 2 | 480 | 60 | 76 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 2 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | 480 V welding receptacle 3 | 480 | 60 | 76 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 2 | 1
Air-cooled condenser, 80 cells (steam-cycle heat rejection) | ACC | B | 480 V welding receptacle 4 | 480 | 60 | 76 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 2 | 1
Aux dry coolers AUXC-F01..12 (closed cooling water) | AUXC | B | Motor 1 of 12, 22 kW (VFD output) | 480 | 22 | 31 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 2 | 1
Aux dry coolers AUXC-F01..12 (closed cooling water) | AUXC | B | Motor 2 of 12, 22 kW (VFD output) | 480 | 22 | 31 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 2 | 1
Aux dry coolers AUXC-F01..12 (closed cooling water) | AUXC | B | Motor 3 of 12, 22 kW (VFD output) | 480 | 22 | 31 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 2 | 1
Aux dry coolers AUXC-F01..12 (closed cooling water) | AUXC | B | Motor 4 of 12, 22 kW (VFD output) | 480 | 22 | 31 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 2 | 1
Aux dry coolers AUXC-F01..12 (closed cooling water) | AUXC | B | Motor 5 of 12, 22 kW (VFD output) | 480 | 22 | 31 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 2 | 1
Aux dry coolers AUXC-F01..12 (closed cooling water) | AUXC | B | Motor 6 of 12, 22 kW (VFD output) | 480 | 22 | 31 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 2 | 1
Aux dry coolers AUXC-F01..12 (closed cooling water) | AUXC | B | Motor 7 of 12, 22 kW (VFD output) | 480 | 22 | 31 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 2 | 1
Aux dry coolers AUXC-F01..12 (closed cooling water) | AUXC | B | Motor 8 of 12, 22 kW (VFD output) | 480 | 22 | 31 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 2 | 1
Aux dry coolers AUXC-F01..12 (closed cooling water) | AUXC | B | Motor 9 of 12, 22 kW (VFD output) | 480 | 22 | 31 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 2 | 1
Aux dry coolers AUXC-F01..12 (closed cooling water) | AUXC | B | Motor 10 of 12, 22 kW (VFD output) | 480 | 22 | 31 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 2 | 1
Aux dry coolers AUXC-F01..12 (closed cooling water) | AUXC | B | Motor 11 of 12, 22 kW (VFD output) | 480 | 22 | 31 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 2 | 1
Aux dry coolers AUXC-F01..12 (closed cooling water) | AUXC | B | Motor 12 of 12, 22 kW (VFD output) | 480 | 22 | 31 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 2 | 1
CCW-A/B: closed cooling water pumps | CCW-A/B | B | Motor 1 of 2, 150 kW | 480 | 150 | 212.3 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 350 kcmil | 1
CCW-A/B: closed cooling water pumps | CCW-A/B | B | Motor 2 of 2, 150 kW | 480 | 150 | 212.3 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 350 kcmil | 1
Condensate storage tank |  | B | LV power feeder | 480 | 10 | 14.2 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 8 | 1
R4: ACC electrical (VFD) e-house (60 x 120 ft) | R4 | B | LV panel / distribution feeder | 480 | 86 | 121.7 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 2/0 | 1
T-R4-1: 13.8/0.48 kV |  | B | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
T-R4-1: 13.8/0.48 kV |  | B | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
T-R4-1: 13.8/0.48 kV |  | B | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
T-R4-1: 13.8/0.48 kV |  | B | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
T-R4-1: 13.8/0.48 kV |  | B | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
T-R4-1: 13.8/0.48 kV |  | B | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
T-R4-2: 13.8/0.48 kV |  | B | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
T-R4-2: 13.8/0.48 kV |  | B | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
T-R4-2: 13.8/0.48 kV |  | B | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
T-R4-2: 13.8/0.48 kV |  | B | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
T-R4-2: 13.8/0.48 kV |  | B | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
T-R4-2: 13.8/0.48 kV |  | B | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
T-R4-3: 13.8/0.48 kV |  | B | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
T-R4-3: 13.8/0.48 kV |  | B | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
T-R4-3: 13.8/0.48 kV |  | B | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
T-R4-3: 13.8/0.48 kV |  | B | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
T-R4-3: 13.8/0.48 kV |  | B | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
T-R4-3: 13.8/0.48 kV |  | B | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
T-R4-4: 13.8/0.48 kV |  | B | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
T-R4-4: 13.8/0.48 kV |  | B | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
T-R4-4: 13.8/0.48 kV |  | B | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
T-R4-4: 13.8/0.48 kV |  | B | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
T-R4-4: 13.8/0.48 kV |  | B | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
T-R4-4: 13.8/0.48 kV |  | B | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 10 | 1
VAC-A/B: ACC air-removal vacuum pumps | VAC-A/B | B | Motor 1 of 2, 75 kW | 480 | 75 | 106.1 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 2/0 | 1
VAC-A/B: ACC air-removal vacuum pumps | VAC-A/B | B | Motor 2 of 2, 75 kW | 480 | 75 | 106.1 | R4 480 V switchgear + vacuum-pump MCC | LV 600 V | 2/0 | 1
T-R4-1: 13.8/0.48 kV |  | B | T-R4-1 ACC VFD transformer primary | 13800 | 3750 | 157 | R1 SWGR-13.8-1 (11 x 36 in cubicles, 15 kV metal-clad) | MV 15 kV | 2/0 | 1
T-R4-2: 13.8/0.48 kV |  | B | T-R4-2 ACC VFD transformer primary | 13800 | 3750 | 157 | R1 SWGR-13.8-2 (11 x 36 in cubicles, 15 kV metal-clad) | MV 15 kV | 2/0 | 1
T-R4-3: 13.8/0.48 kV |  | B | T-R4-3 ACC VFD transformer primary | 13800 | 3750 | 157 | R1 SWGR-13.8-3 (11 x 36 in cubicles, 15 kV metal-clad) | MV 15 kV | 2/0 | 1
T-R4-4: 13.8/0.48 kV |  | B | T-R4-4 ACC VFD transformer primary | 13800 | 3750 | 157 | R1 SWGR-13.8-1 (11 x 36 in cubicles, 15 kV metal-clad) | MV 15 kV | 2/0 | 1
CP-A/B/C: condensate pumps (4.16 kV) | CP-A/B/C | B | Condensate pump CP-A | 4160 | 900 | 139 | R1 SWGR-4.16-A (9 x 36 in cubicles, 5 kV metal-clad) | MV 5 kV | 1/0 | 1
CP-A/B/C: condensate pumps (4.16 kV) | CP-A/B/C | B | Condensate pump CP-B | 4160 | 900 | 139 | R1 SWGR-4.16-B (5 kV metal-clad) | MV 5 kV | 1/0 | 1
CP-A/B/C: condensate pumps (4.16 kV) | CP-A/B/C | B | Condensate pump CP-C | 4160 | 900 | 139 | R1 SWGR-4.16-A (9 x 36 in cubicles, 5 kV metal-clad) | MV 5 kV | 1/0 | 1
230 kV switchyard (gravel) |  | C | Yard lighting circuit 1 (10 floodlights) | 480 | 4 | 6 | RH: switchyard relay / control house (52 x 70 ft) | LV 600 V | 8 | 1
230 kV switchyard (gravel) |  | C | Yard lighting circuit 2 (10 floodlights) | 480 | 4 | 6 | RH: switchyard relay / control house (52 x 70 ft) | LV 600 V | 8 | 1
230 kV switchyard (gravel) |  | C | Yard lighting circuit 3 (10 floodlights) | 480 | 4 | 6 | RH: switchyard relay / control house (52 x 70 ft) | LV 600 V | 8 | 1
230 kV switchyard (gravel) |  | C | Yard lighting circuit 4 (10 floodlights) | 480 | 4 | 6 | RH: switchyard relay / control house (52 x 70 ft) | LV 600 V | 8 | 1
RH: switchyard relay / control house (52 x 70 ft) | RH | C | LV panel / distribution feeder | 480 | 44 | 62.3 | RH: switchyard relay / control house (52 x 70 ft) | LV 600 V | 4 | 1
CONDITIONAL: ULSD backup fuel-oil tank |  | D | LV power feeder | 480 | 10 | 14.2 | R1 MCC-C1 | LV 600 V | 2 | 1
CONDITIONAL: ULSD truck unloading station (canopy, spill containment) |  | D | LV power feeder | 480 | 15 | 21.2 | R1 MCC-C1 | LV 600 V | 1 | 1
CONDITIONAL: ULSD unloading and forwarding pumps, duplex filters |  | D | LV power feeder | 480 | 110 | 155.7 | R1 MCC-C1 | LV 600 V | 350 kcmil | 2
CONDITIONAL: backup fuel oil (ULSD) unloading and forwarding area |  | D | LV power feeder | 480 | 15 | 21.2 | R1 MCC-C1 | LV 600 V | 1 | 1
CONDITIONAL: fuel-gas compressors |  | D | Motor 1 of 6, 15 kW | 480 | 15 | 21.2 | R1 MCC-C1 | LV 600 V | 1/0 | 1
CONDITIONAL: fuel-gas compressors |  | D | Motor 2 of 6, 15 kW | 480 | 15 | 21.2 | R1 MCC-C1 | LV 600 V | 1/0 | 1
CONDITIONAL: fuel-gas compressors |  | D | Motor 3 of 6, 15 kW | 480 | 15 | 21.2 | R1 MCC-C1 | LV 600 V | 1/0 | 1
CONDITIONAL: fuel-gas compressors |  | D | Motor 4 of 6, 15 kW | 480 | 15 | 21.2 | R1 MCC-C1 | LV 600 V | 1/0 | 1
CONDITIONAL: fuel-gas compressors |  | D | Motor 5 of 6, 15 kW | 480 | 15 | 21.2 | R1 MCC-C1 | LV 600 V | 1/0 | 1
CONDITIONAL: fuel-gas compressors |  | D | Motor 6 of 6, 15 kW | 480 | 15 | 21.2 | R1 MCC-C1 | LV 600 V | 1/0 | 1
CPR-1: cathodic-protection rectifier | CPR-1 | D | Cathodic-protection rectifier supply | 480 | 10 | 12.7 | R1 MCC-C1 | LV 600 V | 2 | 1
Fuel-gas performance heater |  | D | LV power feeder | 480 | 60 | 84.9 | R1 MCC-C1 | LV 600 V | 350 kcmil | 1
Gas metering skid |  | D | LV power feeder | 480 | 10 | 14.2 | R1 MCC-C1 | LV 600 V | 2 | 1
Gas pressure regulation skid |  | D | LV power feeder | 480 | 10 | 14.2 | R1 MCC-C1 | LV 600 V | 2 | 1
Gas yard filter-separators |  | D | LV power feeder | 480 | 10 | 14.2 | R1 MCC-C1 | LV 600 V | 2 | 1
Gas yard inlet: ESD valve, block valve and insulating joint |  | D | LV power feeder | 480 | 10 | 14.2 | R1 MCC-C1 | LV 600 V | 2 | 1
Gas yard local control enclosure |  | D | LV power feeder | 480 | 15 | 21.2 | R1 MCC-C1 | LV 600 V | 1 | 1
HTP-4: heat-trace panel (gas) | HTP-4 | D | LV power feeder | 480 | 120 | 169.8 | R1 MCC-C1 | LV 600 V | 350 kcmil | 2
HTP-4: heat-trace panel (gas) | HTP-4 | D | Heat-trace circuit 1 (power to the trace junction box) | 480 | 4 | 6 | HTP-4: heat-trace panel (gas) | LV 600 V | 10 | 1
HTP-4: heat-trace panel (gas) | HTP-4 | D | Heat-trace circuit 2 (power to the trace junction box) | 480 | 4 | 6 | HTP-4: heat-trace panel (gas) | LV 600 V | 10 | 1
HTP-4: heat-trace panel (gas) | HTP-4 | D | Heat-trace circuit 3 (power to the trace junction box) | 480 | 4 | 6 | HTP-4: heat-trace panel (gas) | LV 600 V | 10 | 1
HTP-4: heat-trace panel (gas) | HTP-4 | D | Heat-trace circuit 4 (power to the trace junction box) | 480 | 4 | 6 | HTP-4: heat-trace panel (gas) | LV 600 V | 10 | 1
HTP-4: heat-trace panel (gas) | HTP-4 | D | Heat-trace circuit 5 (power to the trace junction box) | 480 | 4 | 6 | HTP-4: heat-trace panel (gas) | LV 600 V | 10 | 1
HTP-4: heat-trace panel (gas) | HTP-4 | D | Heat-trace circuit 6 (power to the trace junction box) | 480 | 4 | 6 | HTP-4: heat-trace panel (gas) | LV 600 V | 10 | 1
HTP-4: heat-trace panel (gas) | HTP-4 | D | Heat-trace circuit 7 (power to the trace junction box) | 480 | 4 | 6 | HTP-4: heat-trace panel (gas) | LV 600 V | 10 | 1
HTP-4: heat-trace panel (gas) | HTP-4 | D | Heat-trace circuit 8 (power to the trace junction box) | 480 | 4 | 6 | HTP-4: heat-trace panel (gas) | LV 600 V | 10 | 1
HTP-4: heat-trace panel (gas) | HTP-4 | D | Heat-trace circuit 9 (power to the trace junction box) | 480 | 4 | 6 | HTP-4: heat-trace panel (gas) | LV 600 V | 10 | 1
HTP-4: heat-trace panel (gas) | HTP-4 | D | Heat-trace circuit 10 (power to the trace junction box) | 480 | 4 | 6 | HTP-4: heat-trace panel (gas) | LV 600 V | 10 | 1
HTP-4: heat-trace panel (gas) | HTP-4 | D | Heat-trace circuit 11 (power to the trace junction box) | 480 | 4 | 6 | HTP-4: heat-trace panel (gas) | LV 600 V | 10 | 1
HTP-4: heat-trace panel (gas) | HTP-4 | D | Heat-trace circuit 12 (power to the trace junction box) | 480 | 4 | 6 | HTP-4: heat-trace panel (gas) | LV 600 V | 10 | 1
HTP-4: heat-trace panel (gas) | HTP-4 | D | Heat-trace circuit 13 (power to the trace junction box) | 480 | 4 | 6 | HTP-4: heat-trace panel (gas) | LV 600 V | 10 | 1
HTP-4: heat-trace panel (gas) | HTP-4 | D | Heat-trace circuit 14 (power to the trace junction box) | 480 | 4 | 6 | HTP-4: heat-trace panel (gas) | LV 600 V | 10 | 1
HTP-4: heat-trace panel (gas) | HTP-4 | D | Heat-trace circuit 15 (power to the trace junction box) | 480 | 4 | 6 | HTP-4: heat-trace panel (gas) | LV 600 V | 10 | 1
HTP-4: heat-trace panel (gas) | HTP-4 | D | Heat-trace circuit 16 (power to the trace junction box) | 480 | 4 | 6 | HTP-4: heat-trace panel (gas) | LV 600 V | 10 | 1
HTP-4: heat-trace panel (gas) | HTP-4 | D | Heat-trace circuit 17 (power to the trace junction box) | 480 | 4 | 6 | HTP-4: heat-trace panel (gas) | LV 600 V | 10 | 1
HTP-4: heat-trace panel (gas) | HTP-4 | D | Heat-trace circuit 18 (power to the trace junction box) | 480 | 4 | 6 | HTP-4: heat-trace panel (gas) | LV 600 V | 10 | 1
HTP-4: heat-trace panel (gas) | HTP-4 | D | Heat-trace circuit 19 (power to the trace junction box) | 480 | 4 | 6 | HTP-4: heat-trace panel (gas) | LV 600 V | 10 | 1
HTP-4: heat-trace panel (gas) | HTP-4 | D | Heat-trace circuit 20 (power to the trace junction box) | 480 | 4 | 6 | HTP-4: heat-trace panel (gas) | LV 600 V | 10 | 1
HTP-4: heat-trace panel (gas) | HTP-4 | D | Heat-trace circuit 21 (power to the trace junction box) | 480 | 4 | 6 | HTP-4: heat-trace panel (gas) | LV 600 V | 10 | 1
HTP-4: heat-trace panel (gas) | HTP-4 | D | Heat-trace circuit 22 (power to the trace junction box) | 480 | 4 | 6 | HTP-4: heat-trace panel (gas) | LV 600 V | 10 | 1
HTP-4: heat-trace panel (gas) | HTP-4 | D | Heat-trace circuit 23 (power to the trace junction box) | 480 | 4 | 6 | HTP-4: heat-trace panel (gas) | LV 600 V | 10 | 1
HTP-4: heat-trace panel (gas) | HTP-4 | D | Heat-trace circuit 24 (power to the trace junction box) | 480 | 4 | 6 | HTP-4: heat-trace panel (gas) | LV 600 V | 10 | 1
CONDITIONAL: fuel-gas compressors |  | D | Fuel-gas compressor (conditional) | 13800 | 3000 | 139 | R1 SWGR-13.8-3 (11 x 36 in cubicles, 15 kV metal-clad) | MV 15 kV | 1/0 | 1
CONDITIONAL: fuel-gas compressors |  | D | Fuel-gas compressor (conditional) | 13800 | 3000 | 139 | R1 SWGR-13.8-3 (11 x 36 in cubicles, 15 kV metal-clad) | MV 15 kV | 1/0 | 1
CONDITIONAL: fuel-gas compressors |  | D | Fuel-gas compressor (conditional) | 13800 | 3000 | 139 | R1 SWGR-13.8-3 (11 x 36 in cubicles, 15 kV metal-clad) | MV 15 kV | 1/0 | 1
Ammonia storage (aqueous, SCR reagent) |  | E | Motor 1 of 2, 7 kW | 480 | 7 | 9.9 | R1 MCC-C2 | LV 600 V | 4 | 1
Ammonia storage (aqueous, SCR reagent) |  | E | Motor 2 of 2, 7 kW | 480 | 7 | 9.9 | R1 MCC-C2 | LV 600 V | 4 | 1
Auxiliary boiler |  | E | Motor 1 of 3, 30 kW | 480 | 30 | 42.5 | R1 MCC-C2 | LV 600 V | 3/0 | 1
Auxiliary boiler |  | E | Motor 2 of 3, 30 kW | 480 | 30 | 42.5 | R1 MCC-C2 | LV 600 V | 3/0 | 1
Auxiliary boiler |  | E | Motor 3 of 3, 30 kW | 480 | 30 | 42.5 | R1 MCC-C2 | LV 600 V | 3/0 | 1
CPR-2: cathodic-protection rectifier | CPR-2 | E | Cathodic-protection rectifier supply | 480 | 10 | 12.7 | R1 MCC-C2 | LV 600 V | 2 | 1
Demineralised water tank |  | E | LV power feeder | 480 | 10 | 14.2 | R1 MCC-C2 | LV 600 V | 2 | 1
Fire / service water tank |  | E | LV power feeder | 480 | 10 | 14.2 | R1 MCC-C2 | LV 600 V | 2 | 1
Fire pump house |  | E | Motor 1 of 1, 250 kW | 480 | 250 | 353.8 | R1 MCC-C2 | LV 600 V | 500 kcmil | 3
Fire pump house |  | E | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | R1 MCC-C2 | LV 600 V | 1 | 1
H2 / CO2 storage (generator gas) |  | E | LV power feeder | 480 | 15 | 21.2 | R1 MCC-C2 | LV 600 V | 1/0 | 1
HTP-2: heat-trace panel (NH3) | HTP-2 | E | LV power feeder | 480 | 120 | 169.8 | R1 MCC-C2 | LV 600 V | 350 kcmil | 2
HTP-2: heat-trace panel (NH3) | HTP-2 | E | Heat-trace circuit 1 (power to the trace junction box) | 480 | 4 | 6 | HTP-2: heat-trace panel (NH3) | LV 600 V | 10 | 1
HTP-2: heat-trace panel (NH3) | HTP-2 | E | Heat-trace circuit 2 (power to the trace junction box) | 480 | 4 | 6 | HTP-2: heat-trace panel (NH3) | LV 600 V | 10 | 1
HTP-2: heat-trace panel (NH3) | HTP-2 | E | Heat-trace circuit 3 (power to the trace junction box) | 480 | 4 | 6 | HTP-2: heat-trace panel (NH3) | LV 600 V | 10 | 1
HTP-2: heat-trace panel (NH3) | HTP-2 | E | Heat-trace circuit 4 (power to the trace junction box) | 480 | 4 | 6 | HTP-2: heat-trace panel (NH3) | LV 600 V | 10 | 1
HTP-2: heat-trace panel (NH3) | HTP-2 | E | Heat-trace circuit 5 (power to the trace junction box) | 480 | 4 | 6 | HTP-2: heat-trace panel (NH3) | LV 600 V | 10 | 1
HTP-2: heat-trace panel (NH3) | HTP-2 | E | Heat-trace circuit 6 (power to the trace junction box) | 480 | 4 | 6 | HTP-2: heat-trace panel (NH3) | LV 600 V | 10 | 1
HTP-2: heat-trace panel (NH3) | HTP-2 | E | Heat-trace circuit 7 (power to the trace junction box) | 480 | 4 | 6 | HTP-2: heat-trace panel (NH3) | LV 600 V | 10 | 1
HTP-2: heat-trace panel (NH3) | HTP-2 | E | Heat-trace circuit 8 (power to the trace junction box) | 480 | 4 | 6 | HTP-2: heat-trace panel (NH3) | LV 600 V | 10 | 1
HTP-2: heat-trace panel (NH3) | HTP-2 | E | Heat-trace circuit 9 (power to the trace junction box) | 480 | 4 | 6 | HTP-2: heat-trace panel (NH3) | LV 600 V | 10 | 1
HTP-2: heat-trace panel (NH3) | HTP-2 | E | Heat-trace circuit 10 (power to the trace junction box) | 480 | 4 | 6 | HTP-2: heat-trace panel (NH3) | LV 600 V | 10 | 1
HTP-2: heat-trace panel (NH3) | HTP-2 | E | Heat-trace circuit 11 (power to the trace junction box) | 480 | 4 | 6 | HTP-2: heat-trace panel (NH3) | LV 600 V | 10 | 1
HTP-2: heat-trace panel (NH3) | HTP-2 | E | Heat-trace circuit 12 (power to the trace junction box) | 480 | 4 | 6 | HTP-2: heat-trace panel (NH3) | LV 600 V | 10 | 1
HTP-2: heat-trace panel (NH3) | HTP-2 | E | Heat-trace circuit 13 (power to the trace junction box) | 480 | 4 | 6 | HTP-2: heat-trace panel (NH3) | LV 600 V | 10 | 1
HTP-2: heat-trace panel (NH3) | HTP-2 | E | Heat-trace circuit 14 (power to the trace junction box) | 480 | 4 | 6 | HTP-2: heat-trace panel (NH3) | LV 600 V | 10 | 1
HTP-2: heat-trace panel (NH3) | HTP-2 | E | Heat-trace circuit 15 (power to the trace junction box) | 480 | 4 | 6 | HTP-2: heat-trace panel (NH3) | LV 600 V | 10 | 1
HTP-2: heat-trace panel (NH3) | HTP-2 | E | Heat-trace circuit 16 (power to the trace junction box) | 480 | 4 | 6 | HTP-2: heat-trace panel (NH3) | LV 600 V | 10 | 1
HTP-2: heat-trace panel (NH3) | HTP-2 | E | Heat-trace circuit 17 (power to the trace junction box) | 480 | 4 | 6 | HTP-2: heat-trace panel (NH3) | LV 600 V | 10 | 1
HTP-2: heat-trace panel (NH3) | HTP-2 | E | Heat-trace circuit 18 (power to the trace junction box) | 480 | 4 | 6 | HTP-2: heat-trace panel (NH3) | LV 600 V | 10 | 1
HTP-2: heat-trace panel (NH3) | HTP-2 | E | Heat-trace circuit 19 (power to the trace junction box) | 480 | 4 | 6 | HTP-2: heat-trace panel (NH3) | LV 600 V | 10 | 1
HTP-2: heat-trace panel (NH3) | HTP-2 | E | Heat-trace circuit 20 (power to the trace junction box) | 480 | 4 | 6 | HTP-2: heat-trace panel (NH3) | LV 600 V | 10 | 1
HTP-2: heat-trace panel (NH3) | HTP-2 | E | Heat-trace circuit 21 (power to the trace junction box) | 480 | 4 | 6 | HTP-2: heat-trace panel (NH3) | LV 600 V | 10 | 1
HTP-2: heat-trace panel (NH3) | HTP-2 | E | Heat-trace circuit 22 (power to the trace junction box) | 480 | 4 | 6 | HTP-2: heat-trace panel (NH3) | LV 600 V | 10 | 1
HTP-2: heat-trace panel (NH3) | HTP-2 | E | Heat-trace circuit 23 (power to the trace junction box) | 480 | 4 | 6 | HTP-2: heat-trace panel (NH3) | LV 600 V | 10 | 1
HTP-2: heat-trace panel (NH3) | HTP-2 | E | Heat-trace circuit 24 (power to the trace junction box) | 480 | 4 | 6 | HTP-2: heat-trace panel (NH3) | LV 600 V | 10 | 1
HTP-3: heat-trace panel (tanks) | HTP-3 | E | LV power feeder | 480 | 10 | 14.2 | R1 MCC-C2 | LV 600 V | 2 | 1
HTP-3: heat-trace panel (tanks) | HTP-3 | E | Heat-trace circuit 1 (power to the trace junction box) | 480 | 4 | 6 | HTP-3: heat-trace panel (tanks) | LV 600 V | 10 | 1
HTP-3: heat-trace panel (tanks) | HTP-3 | E | Heat-trace circuit 2 (power to the trace junction box) | 480 | 4 | 6 | HTP-3: heat-trace panel (tanks) | LV 600 V | 10 | 1
HTP-3: heat-trace panel (tanks) | HTP-3 | E | Heat-trace circuit 3 (power to the trace junction box) | 480 | 4 | 6 | HTP-3: heat-trace panel (tanks) | LV 600 V | 10 | 1
HTP-3: heat-trace panel (tanks) | HTP-3 | E | Heat-trace circuit 4 (power to the trace junction box) | 480 | 4 | 6 | HTP-3: heat-trace panel (tanks) | LV 600 V | 10 | 1
HTP-3: heat-trace panel (tanks) | HTP-3 | E | Heat-trace circuit 5 (power to the trace junction box) | 480 | 4 | 6 | HTP-3: heat-trace panel (tanks) | LV 600 V | 10 | 1
HTP-3: heat-trace panel (tanks) | HTP-3 | E | Heat-trace circuit 6 (power to the trace junction box) | 480 | 4 | 6 | HTP-3: heat-trace panel (tanks) | LV 600 V | 10 | 1
HTP-3: heat-trace panel (tanks) | HTP-3 | E | Heat-trace circuit 7 (power to the trace junction box) | 480 | 4 | 6 | HTP-3: heat-trace panel (tanks) | LV 600 V | 10 | 1
HTP-3: heat-trace panel (tanks) | HTP-3 | E | Heat-trace circuit 8 (power to the trace junction box) | 480 | 4 | 6 | HTP-3: heat-trace panel (tanks) | LV 600 V | 10 | 1
HTP-3: heat-trace panel (tanks) | HTP-3 | E | Heat-trace circuit 9 (power to the trace junction box) | 480 | 4 | 6 | HTP-3: heat-trace panel (tanks) | LV 600 V | 10 | 1
HTP-3: heat-trace panel (tanks) | HTP-3 | E | Heat-trace circuit 10 (power to the trace junction box) | 480 | 4 | 6 | HTP-3: heat-trace panel (tanks) | LV 600 V | 10 | 1
HTP-3: heat-trace panel (tanks) | HTP-3 | E | Heat-trace circuit 11 (power to the trace junction box) | 480 | 4 | 6 | HTP-3: heat-trace panel (tanks) | LV 600 V | 10 | 1
HTP-3: heat-trace panel (tanks) | HTP-3 | E | Heat-trace circuit 12 (power to the trace junction box) | 480 | 4 | 6 | HTP-3: heat-trace panel (tanks) | LV 600 V | 10 | 1
HTP-3: heat-trace panel (tanks) | HTP-3 | E | Heat-trace circuit 13 (power to the trace junction box) | 480 | 4 | 6 | HTP-3: heat-trace panel (tanks) | LV 600 V | 10 | 1
HTP-3: heat-trace panel (tanks) | HTP-3 | E | Heat-trace circuit 14 (power to the trace junction box) | 480 | 4 | 6 | HTP-3: heat-trace panel (tanks) | LV 600 V | 10 | 1
HTP-3: heat-trace panel (tanks) | HTP-3 | E | Heat-trace circuit 15 (power to the trace junction box) | 480 | 4 | 6 | HTP-3: heat-trace panel (tanks) | LV 600 V | 10 | 1
HTP-3: heat-trace panel (tanks) | HTP-3 | E | Heat-trace circuit 16 (power to the trace junction box) | 480 | 4 | 6 | HTP-3: heat-trace panel (tanks) | LV 600 V | 10 | 1
HTP-3: heat-trace panel (tanks) | HTP-3 | E | Heat-trace circuit 17 (power to the trace junction box) | 480 | 4 | 6 | HTP-3: heat-trace panel (tanks) | LV 600 V | 10 | 1
HTP-3: heat-trace panel (tanks) | HTP-3 | E | Heat-trace circuit 18 (power to the trace junction box) | 480 | 4 | 6 | HTP-3: heat-trace panel (tanks) | LV 600 V | 10 | 1
HTP-3: heat-trace panel (tanks) | HTP-3 | E | Heat-trace circuit 19 (power to the trace junction box) | 480 | 4 | 6 | HTP-3: heat-trace panel (tanks) | LV 600 V | 10 | 1
HTP-3: heat-trace panel (tanks) | HTP-3 | E | Heat-trace circuit 20 (power to the trace junction box) | 480 | 4 | 6 | HTP-3: heat-trace panel (tanks) | LV 600 V | 10 | 1
HTP-3: heat-trace panel (tanks) | HTP-3 | E | Heat-trace circuit 21 (power to the trace junction box) | 480 | 4 | 6 | HTP-3: heat-trace panel (tanks) | LV 600 V | 10 | 1
HTP-3: heat-trace panel (tanks) | HTP-3 | E | Heat-trace circuit 22 (power to the trace junction box) | 480 | 4 | 6 | HTP-3: heat-trace panel (tanks) | LV 600 V | 10 | 1
HTP-3: heat-trace panel (tanks) | HTP-3 | E | Heat-trace circuit 23 (power to the trace junction box) | 480 | 4 | 6 | HTP-3: heat-trace panel (tanks) | LV 600 V | 10 | 1
HTP-3: heat-trace panel (tanks) | HTP-3 | E | Heat-trace circuit 24 (power to the trace junction box) | 480 | 4 | 6 | HTP-3: heat-trace panel (tanks) | LV 600 V | 10 | 1
Oil-water separator |  | E | Motor 1 of 2, 7 kW | 480 | 7 | 9.9 | R1 MCC-C2 | LV 600 V | 4 | 1
Oil-water separator |  | E | Motor 2 of 2, 7 kW | 480 | 7 | 9.9 | R1 MCC-C2 | LV 600 V | 4 | 1
Raw water tank |  | E | LV power feeder | 480 | 10 | 14.2 | R1 MCC-C2 | LV 600 V | 2 | 1
Wastewater treatment |  | E | Motor 1 of 8, 15 kW | 480 | 15 | 21.2 | R1 MCC-C2 | LV 600 V | 1 | 1
Wastewater treatment |  | E | Motor 2 of 8, 15 kW | 480 | 15 | 21.2 | R1 MCC-C2 | LV 600 V | 1 | 1
Wastewater treatment |  | E | Motor 3 of 8, 15 kW | 480 | 15 | 21.2 | R1 MCC-C2 | LV 600 V | 1 | 1
Wastewater treatment |  | E | Motor 4 of 8, 15 kW | 480 | 15 | 21.2 | R1 MCC-C2 | LV 600 V | 1 | 1
Wastewater treatment |  | E | Motor 5 of 8, 15 kW | 480 | 15 | 21.2 | R1 MCC-C2 | LV 600 V | 1 | 1
Wastewater treatment |  | E | Motor 6 of 8, 15 kW | 480 | 15 | 21.2 | R1 MCC-C2 | LV 600 V | 1 | 1
Wastewater treatment |  | E | Motor 7 of 8, 15 kW | 480 | 15 | 21.2 | R1 MCC-C2 | LV 600 V | 1 | 1
Wastewater treatment |  | E | Motor 8 of 8, 15 kW | 480 | 15 | 21.2 | R1 MCC-C2 | LV 600 V | 1 | 1
Water treatment building (incl. R-WT electrical room) | R-WT | E | Motor 1 of 20, 15 kW | 480 | 15 | 21.2 | R1 MCC-C2 | LV 600 V | 2 | 1
Water treatment building (incl. R-WT electrical room) | R-WT | E | Motor 2 of 20, 15 kW | 480 | 15 | 21.2 | R1 MCC-C2 | LV 600 V | 2 | 1
Water treatment building (incl. R-WT electrical room) | R-WT | E | Motor 3 of 20, 15 kW | 480 | 15 | 21.2 | R1 MCC-C2 | LV 600 V | 2 | 1
Water treatment building (incl. R-WT electrical room) | R-WT | E | Motor 4 of 20, 15 kW | 480 | 15 | 21.2 | R1 MCC-C2 | LV 600 V | 2 | 1
Water treatment building (incl. R-WT electrical room) | R-WT | E | Motor 5 of 20, 15 kW | 480 | 15 | 21.2 | R1 MCC-C2 | LV 600 V | 2 | 1
Water treatment building (incl. R-WT electrical room) | R-WT | E | Motor 6 of 20, 15 kW | 480 | 15 | 21.2 | R1 MCC-C2 | LV 600 V | 2 | 1
Water treatment building (incl. R-WT electrical room) | R-WT | E | Motor 7 of 20, 15 kW | 480 | 15 | 21.2 | R1 MCC-C2 | LV 600 V | 2 | 1
Water treatment building (incl. R-WT electrical room) | R-WT | E | Motor 8 of 20, 15 kW | 480 | 15 | 21.2 | R1 MCC-C2 | LV 600 V | 2 | 1
Water treatment building (incl. R-WT electrical room) | R-WT | E | Motor 9 of 20, 15 kW | 480 | 15 | 21.2 | R1 MCC-C2 | LV 600 V | 2 | 1
Water treatment building (incl. R-WT electrical room) | R-WT | E | Motor 10 of 20, 15 kW | 480 | 15 | 21.2 | R1 MCC-C2 | LV 600 V | 2 | 1
Water treatment building (incl. R-WT electrical room) | R-WT | E | Motor 11 of 20, 15 kW | 480 | 15 | 21.2 | R1 MCC-C2 | LV 600 V | 2 | 1
Water treatment building (incl. R-WT electrical room) | R-WT | E | Motor 12 of 20, 15 kW | 480 | 15 | 21.2 | R1 MCC-C2 | LV 600 V | 2 | 1
Water treatment building (incl. R-WT electrical room) | R-WT | E | Motor 13 of 20, 15 kW | 480 | 15 | 21.2 | R1 MCC-C2 | LV 600 V | 2 | 1
Water treatment building (incl. R-WT electrical room) | R-WT | E | Motor 14 of 20, 15 kW | 480 | 15 | 21.2 | R1 MCC-C2 | LV 600 V | 2 | 1
Water treatment building (incl. R-WT electrical room) | R-WT | E | Motor 15 of 20, 15 kW | 480 | 15 | 21.2 | R1 MCC-C2 | LV 600 V | 2 | 1
Water treatment building (incl. R-WT electrical room) | R-WT | E | Motor 16 of 20, 15 kW | 480 | 15 | 21.2 | R1 MCC-C2 | LV 600 V | 2 | 1
Water treatment building (incl. R-WT electrical room) | R-WT | E | Motor 17 of 20, 15 kW | 480 | 15 | 21.2 | R1 MCC-C2 | LV 600 V | 2 | 1
Water treatment building (incl. R-WT electrical room) | R-WT | E | Motor 18 of 20, 15 kW | 480 | 15 | 21.2 | R1 MCC-C2 | LV 600 V | 2 | 1
Water treatment building (incl. R-WT electrical room) | R-WT | E | Motor 19 of 20, 15 kW | 480 | 15 | 21.2 | R1 MCC-C2 | LV 600 V | 2 | 1
Water treatment building (incl. R-WT electrical room) | R-WT | E | Motor 20 of 20, 15 kW | 480 | 15 | 21.2 | R1 MCC-C2 | LV 600 V | 2 | 1
Comms tower (lattice) | COMMS | F | LV power feeder | 480 | 10 | 14.2 | R1 MCC-C2 | LV 600 V | 4 | 1
Control / admin building (main control room) | CR | F | LV panel / distribution feeder | 480 | 145 | 205.2 | R1 MCC-C2 | LV 600 V | 500 kcmil | 1
EDG-1: 3 MW emergency diesel generator (480 V) | EDG-1 | F | LV power feeder | 480 | 15 | 21.2 | R1 MCC-C2 | LV 600 V | 4 | 1
EDG-2: 3 MW emergency diesel generator (480 V) | EDG-2 | F | LV power feeder | 480 | 15 | 21.2 | R1 MCC-C2 | LV 600 V | 2 | 1
Gatehouse |  | F | LV panel / distribution feeder | 480 | 30 | 42.5 | R1 MCC-C2 | LV 600 V | 1/0 | 1
LS-1: sanitary lift station (packaged duplex) | LS-1 | F | Motor 1 of 2, 7 kW | 480 | 7 | 9.9 | R1 MCC-C2 | LV 600 V | 8 | 1
LS-1: sanitary lift station (packaged duplex) | LS-1 | F | Motor 2 of 2, 7 kW | 480 | 7 | 9.9 | R1 MCC-C2 | LV 600 V | 8 | 1
Maintenance building / workshop |  | F | LV panel / distribution feeder | 480 | 60 | 84.9 | R1 MCC-C2 | LV 600 V | 2/0 | 1
Stormwater pump station (2 x 100% submersible pumps) |  | F | Motor 1 of 2, 75 kW | 480 | 75 | 106.1 | R1 MCC-C2 | LV 600 V | 500 kcmil | 1
Stormwater pump station (2 x 100% submersible pumps) |  | F | Motor 2 of 2, 75 kW | 480 | 75 | 106.1 | R1 MCC-C2 | LV 600 V | 500 kcmil | 1
Warehouse |  | F | LV panel / distribution feeder | 480 | 204 | 288.7 | R1 MCC-C2 | LV 600 V | 500 kcmil | 1
Absorber A (62 ft dia x 262 ft, stack to 313 ft) | ABS-A | G | MOV 1: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber A (62 ft dia x 262 ft, stack to 313 ft) | ABS-A | G | MOV 2: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber A (62 ft dia x 262 ft, stack to 313 ft) | ABS-A | G | MOV 3: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber A (62 ft dia x 262 ft, stack to 313 ft) | ABS-A | G | MOV 4: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber A (62 ft dia x 262 ft, stack to 313 ft) | ABS-A | G | MOV 5: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber A (62 ft dia x 262 ft, stack to 313 ft) | ABS-A | G | MOV 6: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber A (62 ft dia x 262 ft, stack to 313 ft) | ABS-A | G | MOV 7: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber A (62 ft dia x 262 ft, stack to 313 ft) | ABS-A | G | MOV 8: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber A (62 ft dia x 262 ft, stack to 313 ft) | ABS-A | G | MOV 9: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber A (62 ft dia x 262 ft, stack to 313 ft) | ABS-A | G | MOV 10: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber A (62 ft dia x 262 ft, stack to 313 ft) | ABS-A | G | LV power feeder | 480 | 40 | 56.6 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
Absorber A (62 ft dia x 262 ft, stack to 313 ft) | ABS-A | G | Area / platform lighting circuit 1 (12 fixtures) | 480 | 3 | 5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber A (62 ft dia x 262 ft, stack to 313 ft) | ABS-A | G | Area / platform lighting circuit 2 (12 fixtures) | 480 | 3 | 5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber A (62 ft dia x 262 ft, stack to 313 ft) | ABS-A | G | Area / platform lighting circuit 3 (6 fixtures) | 480 | 3 | 5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber A (62 ft dia x 262 ft, stack to 313 ft) | ABS-A | G | 480 V welding receptacle 1 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 1/0 | 1
Absorber A (62 ft dia x 262 ft, stack to 313 ft) | ABS-A | G | 480 V welding receptacle 2 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 1/0 | 1
Absorber A (62 ft dia x 262 ft, stack to 313 ft) | ABS-A | G | 480 V welding receptacle 3 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 1/0 | 1
Absorber A (62 ft dia x 262 ft, stack to 313 ft) | ABS-A | G | 480 V welding receptacle 4 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 1/0 | 1
Absorber A intercooler (pumps + plate exchanger) |  | G | Motor 1 of 2, 150 kW | 480 | 150 | 212.3 | CCS MV switchgear building (VFDs) | LV 600 V | 350 kcmil | 1
Absorber A intercooler (pumps + plate exchanger) |  | G | Motor 2 of 2, 150 kW | 480 | 150 | 212.3 | CCS MV switchgear building (VFDs) | LV 600 V | 350 kcmil | 1
Absorber B (62 ft dia x 262 ft, stack to 313 ft) | ABS-B | G | MOV 1: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber B (62 ft dia x 262 ft, stack to 313 ft) | ABS-B | G | MOV 2: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber B (62 ft dia x 262 ft, stack to 313 ft) | ABS-B | G | MOV 3: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber B (62 ft dia x 262 ft, stack to 313 ft) | ABS-B | G | MOV 4: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber B (62 ft dia x 262 ft, stack to 313 ft) | ABS-B | G | MOV 5: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber B (62 ft dia x 262 ft, stack to 313 ft) | ABS-B | G | MOV 6: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber B (62 ft dia x 262 ft, stack to 313 ft) | ABS-B | G | MOV 7: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber B (62 ft dia x 262 ft, stack to 313 ft) | ABS-B | G | MOV 8: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber B (62 ft dia x 262 ft, stack to 313 ft) | ABS-B | G | MOV 9: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber B (62 ft dia x 262 ft, stack to 313 ft) | ABS-B | G | MOV 10: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber B (62 ft dia x 262 ft, stack to 313 ft) | ABS-B | G | LV power feeder | 480 | 40 | 56.6 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
Absorber B (62 ft dia x 262 ft, stack to 313 ft) | ABS-B | G | Area / platform lighting circuit 1 (12 fixtures) | 480 | 3 | 5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber B (62 ft dia x 262 ft, stack to 313 ft) | ABS-B | G | Area / platform lighting circuit 2 (12 fixtures) | 480 | 3 | 5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber B (62 ft dia x 262 ft, stack to 313 ft) | ABS-B | G | Area / platform lighting circuit 3 (6 fixtures) | 480 | 3 | 5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber B (62 ft dia x 262 ft, stack to 313 ft) | ABS-B | G | 480 V welding receptacle 1 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
Absorber B (62 ft dia x 262 ft, stack to 313 ft) | ABS-B | G | 480 V welding receptacle 2 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
Absorber B (62 ft dia x 262 ft, stack to 313 ft) | ABS-B | G | 480 V welding receptacle 3 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
Absorber B (62 ft dia x 262 ft, stack to 313 ft) | ABS-B | G | 480 V welding receptacle 4 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
Absorber B intercooler (pumps + plate exchanger) |  | G | Motor 1 of 2, 150 kW | 480 | 150 | 212.3 | CCS MV switchgear building (VFDs) | LV 600 V | 350 kcmil | 1
Absorber B intercooler (pumps + plate exchanger) |  | G | Motor 2 of 2, 150 kW | 480 | 150 | 212.3 | CCS MV switchgear building (VFDs) | LV 600 V | 350 kcmil | 1
Absorber C (62 ft dia x 262 ft, stack to 313 ft) | ABS-C | G | MOV 1: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber C (62 ft dia x 262 ft, stack to 313 ft) | ABS-C | G | MOV 2: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber C (62 ft dia x 262 ft, stack to 313 ft) | ABS-C | G | MOV 3: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber C (62 ft dia x 262 ft, stack to 313 ft) | ABS-C | G | MOV 4: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber C (62 ft dia x 262 ft, stack to 313 ft) | ABS-C | G | MOV 5: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber C (62 ft dia x 262 ft, stack to 313 ft) | ABS-C | G | MOV 6: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber C (62 ft dia x 262 ft, stack to 313 ft) | ABS-C | G | MOV 7: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber C (62 ft dia x 262 ft, stack to 313 ft) | ABS-C | G | MOV 8: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber C (62 ft dia x 262 ft, stack to 313 ft) | ABS-C | G | MOV 9: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber C (62 ft dia x 262 ft, stack to 313 ft) | ABS-C | G | MOV 10: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber C (62 ft dia x 262 ft, stack to 313 ft) | ABS-C | G | LV power feeder | 480 | 40 | 56.6 | CCS MV switchgear building (VFDs) | LV 600 V | 4 | 1
Absorber C (62 ft dia x 262 ft, stack to 313 ft) | ABS-C | G | Area / platform lighting circuit 1 (12 fixtures) | 480 | 3 | 5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber C (62 ft dia x 262 ft, stack to 313 ft) | ABS-C | G | Area / platform lighting circuit 2 (12 fixtures) | 480 | 3 | 5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber C (62 ft dia x 262 ft, stack to 313 ft) | ABS-C | G | Area / platform lighting circuit 3 (6 fixtures) | 480 | 3 | 5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Absorber C (62 ft dia x 262 ft, stack to 313 ft) | ABS-C | G | 480 V welding receptacle 1 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
Absorber C (62 ft dia x 262 ft, stack to 313 ft) | ABS-C | G | 480 V welding receptacle 2 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
Absorber C (62 ft dia x 262 ft, stack to 313 ft) | ABS-C | G | 480 V welding receptacle 3 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
Absorber C (62 ft dia x 262 ft, stack to 313 ft) | ABS-C | G | 480 V welding receptacle 4 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
Absorber C intercooler (pumps + plate exchanger) |  | G | Motor 1 of 2, 150 kW | 480 | 150 | 212.3 | CCS MV switchgear building (VFDs) | LV 600 V | 350 kcmil | 1
Absorber C intercooler (pumps + plate exchanger) |  | G | Motor 2 of 2, 150 kW | 480 | 150 | 212.3 | CCS MV switchgear building (VFDs) | LV 600 V | 350 kcmil | 1
Activated-carbon filter |  | G | LV power feeder | 480 | 15 | 21.2 | CCS MV switchgear building (VFDs) | LV 600 V | 8 | 1
BF-A: booster fan (~16 MW) | BF-A | G | Motor 1 of 4, 15 kW | 480 | 15 | 21.2 | CCS MV switchgear building (VFDs) | LV 600 V | 6 | 1
BF-A: booster fan (~16 MW) | BF-A | G | Motor 2 of 4, 15 kW | 480 | 15 | 21.2 | CCS MV switchgear building (VFDs) | LV 600 V | 6 | 1
BF-A: booster fan (~16 MW) | BF-A | G | Motor 3 of 4, 15 kW | 480 | 15 | 21.2 | CCS MV switchgear building (VFDs) | LV 600 V | 6 | 1
BF-A: booster fan (~16 MW) | BF-A | G | Motor 4 of 4, 15 kW | 480 | 15 | 21.2 | CCS MV switchgear building (VFDs) | LV 600 V | 6 | 1
BF-A: booster fan (~16 MW) | BF-A | G | 480 V welding receptacle 1 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
BF-A: booster fan (~16 MW) | BF-A | G | 480 V welding receptacle 2 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
BF-A: booster fan (~16 MW) | BF-A | G | 480 V welding receptacle 3 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
BF-A: booster fan (~16 MW) | BF-A | G | 480 V welding receptacle 4 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
BF-B: booster fan (~16 MW) | BF-B | G | Motor 1 of 4, 15 kW | 480 | 15 | 21.2 | CCS MV switchgear building (VFDs) | LV 600 V | 8 | 1
BF-B: booster fan (~16 MW) | BF-B | G | Motor 2 of 4, 15 kW | 480 | 15 | 21.2 | CCS MV switchgear building (VFDs) | LV 600 V | 8 | 1
BF-B: booster fan (~16 MW) | BF-B | G | Motor 3 of 4, 15 kW | 480 | 15 | 21.2 | CCS MV switchgear building (VFDs) | LV 600 V | 8 | 1
BF-B: booster fan (~16 MW) | BF-B | G | Motor 4 of 4, 15 kW | 480 | 15 | 21.2 | CCS MV switchgear building (VFDs) | LV 600 V | 8 | 1
BF-B: booster fan (~16 MW) | BF-B | G | 480 V welding receptacle 1 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
BF-B: booster fan (~16 MW) | BF-B | G | 480 V welding receptacle 2 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
BF-B: booster fan (~16 MW) | BF-B | G | 480 V welding receptacle 3 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
BF-B: booster fan (~16 MW) | BF-B | G | 480 V welding receptacle 4 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
BF-C: booster fan (~16 MW) | BF-C | G | Motor 1 of 4, 15 kW | 480 | 15 | 21.2 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
BF-C: booster fan (~16 MW) | BF-C | G | Motor 2 of 4, 15 kW | 480 | 15 | 21.2 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
BF-C: booster fan (~16 MW) | BF-C | G | Motor 3 of 4, 15 kW | 480 | 15 | 21.2 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
BF-C: booster fan (~16 MW) | BF-C | G | Motor 4 of 4, 15 kW | 480 | 15 | 21.2 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
BF-C: booster fan (~16 MW) | BF-C | G | 480 V welding receptacle 1 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
BF-C: booster fan (~16 MW) | BF-C | G | 480 V welding receptacle 2 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
BF-C: booster fan (~16 MW) | BF-C | G | 480 V welding receptacle 3 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
BF-C: booster fan (~16 MW) | BF-C | G | 480 V welding receptacle 4 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
CCS F&G / control |  | G | LV panel / distribution feeder | 480 | 40 | 56.6 | CCS MV switchgear building (VFDs) | LV 600 V | 4 | 1
CCS MV switchgear building (VFDs) |  | G | LV panel / distribution feeder | 480 | 109 | 154.2 | CCS MV switchgear building (VFDs) | LV 600 V | 3/0 | 1
CCS T-1: 230/13.8 kV | CCS T-1 | G | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
CCS T-1: 230/13.8 kV | CCS T-1 | G | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
CCS T-1: 230/13.8 kV | CCS T-1 | G | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
CCS T-1: 230/13.8 kV | CCS T-1 | G | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
CCS T-1: 230/13.8 kV | CCS T-1 | G | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
CCS T-1: 230/13.8 kV | CCS T-1 | G | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
CCS T-2: 230/13.8 kV | CCS T-2 | G | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
CCS T-2: 230/13.8 kV | CCS T-2 | G | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
CCS T-2: 230/13.8 kV | CCS T-2 | G | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
CCS T-2: 230/13.8 kV | CCS T-2 | G | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
CCS T-2: 230/13.8 kV | CCS T-2 | G | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
CCS T-2: 230/13.8 kV | CCS T-2 | G | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Motor 1 of 30, 110 kW (VFD output) | 480 | 110 | 156 | CT MCC / VFD e-house | LV 600 V | 3/0 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Motor 2 of 30, 110 kW (VFD output) | 480 | 110 | 156 | CT MCC / VFD e-house | LV 600 V | 3/0 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Motor 3 of 30, 110 kW (VFD output) | 480 | 110 | 156 | CT MCC / VFD e-house | LV 600 V | 3/0 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Motor 4 of 30, 110 kW (VFD output) | 480 | 110 | 156 | CT MCC / VFD e-house | LV 600 V | 3/0 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Motor 5 of 30, 110 kW (VFD output) | 480 | 110 | 156 | CT MCC / VFD e-house | LV 600 V | 3/0 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Motor 6 of 30, 110 kW (VFD output) | 480 | 110 | 156 | CT MCC / VFD e-house | LV 600 V | 3/0 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Motor 7 of 30, 110 kW (VFD output) | 480 | 110 | 156 | CT MCC / VFD e-house | LV 600 V | 3/0 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Motor 8 of 30, 110 kW (VFD output) | 480 | 110 | 156 | CT MCC / VFD e-house | LV 600 V | 3/0 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Motor 9 of 30, 110 kW (VFD output) | 480 | 110 | 156 | CT MCC / VFD e-house | LV 600 V | 3/0 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Motor 10 of 30, 110 kW (VFD output) | 480 | 110 | 156 | CT MCC / VFD e-house | LV 600 V | 3/0 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Motor 11 of 30, 110 kW (VFD output) | 480 | 110 | 156 | CT MCC / VFD e-house | LV 600 V | 3/0 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Motor 12 of 30, 110 kW (VFD output) | 480 | 110 | 156 | CT MCC / VFD e-house | LV 600 V | 3/0 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Motor 13 of 30, 110 kW (VFD output) | 480 | 110 | 156 | CT MCC / VFD e-house | LV 600 V | 3/0 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Motor 14 of 30, 110 kW (VFD output) | 480 | 110 | 156 | CT MCC / VFD e-house | LV 600 V | 3/0 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Motor 15 of 30, 110 kW (VFD output) | 480 | 110 | 156 | CT MCC / VFD e-house | LV 600 V | 3/0 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Motor 16 of 30, 110 kW (VFD output) | 480 | 110 | 156 | CT MCC / VFD e-house | LV 600 V | 3/0 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Motor 17 of 30, 110 kW (VFD output) | 480 | 110 | 156 | CT MCC / VFD e-house | LV 600 V | 3/0 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Motor 18 of 30, 110 kW (VFD output) | 480 | 110 | 156 | CT MCC / VFD e-house | LV 600 V | 3/0 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Motor 19 of 30, 110 kW (VFD output) | 480 | 110 | 156 | CT MCC / VFD e-house | LV 600 V | 3/0 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Motor 20 of 30, 110 kW (VFD output) | 480 | 110 | 156 | CT MCC / VFD e-house | LV 600 V | 3/0 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Motor 21 of 30, 110 kW (VFD output) | 480 | 110 | 156 | CT MCC / VFD e-house | LV 600 V | 3/0 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Motor 22 of 30, 110 kW (VFD output) | 480 | 110 | 156 | CT MCC / VFD e-house | LV 600 V | 3/0 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Motor 23 of 30, 110 kW (VFD output) | 480 | 110 | 156 | CT MCC / VFD e-house | LV 600 V | 3/0 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Motor 24 of 30, 110 kW (VFD output) | 480 | 110 | 156 | CT MCC / VFD e-house | LV 600 V | 3/0 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Motor 25 of 30, 110 kW (VFD output) | 480 | 110 | 156 | CT MCC / VFD e-house | LV 600 V | 3/0 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Motor 26 of 30, 110 kW (VFD output) | 480 | 110 | 156 | CT MCC / VFD e-house | LV 600 V | 3/0 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Motor 27 of 30, 110 kW (VFD output) | 480 | 110 | 156 | CT MCC / VFD e-house | LV 600 V | 3/0 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Motor 28 of 30, 110 kW (VFD output) | 480 | 110 | 156 | CT MCC / VFD e-house | LV 600 V | 3/0 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Motor 29 of 30, 110 kW (VFD output) | 480 | 110 | 156 | CT MCC / VFD e-house | LV 600 V | 3/0 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Motor 30 of 30, 110 kW (VFD output) | 480 | 110 | 156 | CT MCC / VFD e-house | LV 600 V | 3/0 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Area / platform lighting circuit 1 (12 fixtures) | 480 | 3 | 5 | CT MCC / VFD e-house | LV 600 V | 10 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Area / platform lighting circuit 2 (12 fixtures) | 480 | 3 | 5 | CT MCC / VFD e-house | LV 600 V | 10 | 1
CCS cooling tower (~30 cells): CCS process cooling only | CCS-CT | G | Area / platform lighting circuit 3 (6 fixtures) | 480 | 3 | 5 | CT MCC / VFD e-house | LV 600 V | 10 | 1
CCS instrument air |  | G | Motor 1 of 2, 250 kW | 480 | 250 | 353.8 | CCS MV switchgear building (VFDs) | LV 600 V | 4/0 | 2
CCS instrument air |  | G | Motor 2 of 2, 250 kW | 480 | 250 | 353.8 | CCS MV switchgear building (VFDs) | LV 600 V | 4/0 | 2
CCS wastewater (DCC + tower blowdown) |  | G | Motor 1 of 6, 15 kW | 480 | 15 | 21.2 | CT MCC / VFD e-house | LV 600 V | 10 | 1
CCS wastewater (DCC + tower blowdown) |  | G | Motor 2 of 6, 15 kW | 480 | 15 | 21.2 | CT MCC / VFD e-house | LV 600 V | 10 | 1
CCS wastewater (DCC + tower blowdown) |  | G | Motor 3 of 6, 15 kW | 480 | 15 | 21.2 | CT MCC / VFD e-house | LV 600 V | 10 | 1
CCS wastewater (DCC + tower blowdown) |  | G | Motor 4 of 6, 15 kW | 480 | 15 | 21.2 | CT MCC / VFD e-house | LV 600 V | 10 | 1
CCS wastewater (DCC + tower blowdown) |  | G | Motor 5 of 6, 15 kW | 480 | 15 | 21.2 | CT MCC / VFD e-house | LV 600 V | 10 | 1
CCS wastewater (DCC + tower blowdown) |  | G | Motor 6 of 6, 15 kW | 480 | 15 | 21.2 | CT MCC / VFD e-house | LV 600 V | 10 | 1
CO2 compression 3 x ~19 MW + dehydration |  | G | Motor 1 of 10, 30 kW | 480 | 30 | 42.5 | CCS MV switchgear building (VFDs) | LV 600 V | 6 | 1
CO2 compression 3 x ~19 MW + dehydration |  | G | Motor 2 of 10, 30 kW | 480 | 30 | 42.5 | CCS MV switchgear building (VFDs) | LV 600 V | 6 | 1
CO2 compression 3 x ~19 MW + dehydration |  | G | Motor 3 of 10, 30 kW | 480 | 30 | 42.5 | CCS MV switchgear building (VFDs) | LV 600 V | 6 | 1
CO2 compression 3 x ~19 MW + dehydration |  | G | Motor 4 of 10, 30 kW | 480 | 30 | 42.5 | CCS MV switchgear building (VFDs) | LV 600 V | 6 | 1
CO2 compression 3 x ~19 MW + dehydration |  | G | Motor 5 of 10, 30 kW | 480 | 30 | 42.5 | CCS MV switchgear building (VFDs) | LV 600 V | 6 | 1
CO2 compression 3 x ~19 MW + dehydration |  | G | Motor 6 of 10, 30 kW | 480 | 30 | 42.5 | CCS MV switchgear building (VFDs) | LV 600 V | 6 | 1
CO2 compression 3 x ~19 MW + dehydration |  | G | Motor 7 of 10, 30 kW | 480 | 30 | 42.5 | CCS MV switchgear building (VFDs) | LV 600 V | 6 | 1
CO2 compression 3 x ~19 MW + dehydration |  | G | Motor 8 of 10, 30 kW | 480 | 30 | 42.5 | CCS MV switchgear building (VFDs) | LV 600 V | 6 | 1
CO2 compression 3 x ~19 MW + dehydration |  | G | Motor 9 of 10, 30 kW | 480 | 30 | 42.5 | CCS MV switchgear building (VFDs) | LV 600 V | 6 | 1
CO2 compression 3 x ~19 MW + dehydration |  | G | Motor 10 of 10, 30 kW | 480 | 30 | 42.5 | CCS MV switchgear building (VFDs) | LV 600 V | 6 | 1
CO2 compression 3 x ~19 MW + dehydration |  | G | 480 V welding receptacle 1 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
CO2 compression 3 x ~19 MW + dehydration |  | G | 480 V welding receptacle 2 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
CO2 compression 3 x ~19 MW + dehydration |  | G | 480 V welding receptacle 3 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
CO2 compression 3 x ~19 MW + dehydration |  | G | 480 V welding receptacle 4 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
CO2 dehydration: molecular-sieve towers and regeneration heater |  | G | Motor 1 of 2, 20 kW | 480 | 20 | 28.3 | CCS MV switchgear building (VFDs) | LV 600 V | 6 | 1
CO2 dehydration: molecular-sieve towers and regeneration heater |  | G | Motor 2 of 2, 20 kW | 480 | 20 | 28.3 | CCS MV switchgear building (VFDs) | LV 600 V | 6 | 1
CO2 dehydration: molecular-sieve towers and regeneration heater |  | G | Motor 1 of 1, 200 kW | 480 | 200 | 283 | CCS MV switchgear building (VFDs) | LV 600 V | 500 kcmil | 1
CO2 dehydration: molecular-sieve towers and regeneration heater |  | G | MOV 1: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
CO2 dehydration: molecular-sieve towers and regeneration heater |  | G | MOV 2: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
CO2 dehydration: molecular-sieve towers and regeneration heater |  | G | MOV 3: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
CO2 dehydration: molecular-sieve towers and regeneration heater |  | G | MOV 4: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
CO2 dehydration: molecular-sieve towers and regeneration heater |  | G | MOV 5: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
CO2 dehydration: molecular-sieve towers and regeneration heater |  | G | MOV 6: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
CO2 dehydration: molecular-sieve towers and regeneration heater |  | G | MOV 7: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
CO2 dehydration: molecular-sieve towers and regeneration heater |  | G | MOV 8: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
CO2 dehydration: molecular-sieve towers and regeneration heater |  | G | MOV 9: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
CO2 dehydration: molecular-sieve towers and regeneration heater |  | G | MOV 10: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
CO2 dehydration: molecular-sieve towers and regeneration heater |  | G | MOV 11: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
CO2 dehydration: molecular-sieve towers and regeneration heater |  | G | MOV 12: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
CONDITIONAL: HP export compressor + metering |  | G | Motor 1 of 4, 30 kW | 480 | 30 | 42.5 | CCS MV switchgear building (VFDs) | LV 600 V | 6 | 1
CONDITIONAL: HP export compressor + metering |  | G | Motor 2 of 4, 30 kW | 480 | 30 | 42.5 | CCS MV switchgear building (VFDs) | LV 600 V | 6 | 1
CONDITIONAL: HP export compressor + metering |  | G | Motor 3 of 4, 30 kW | 480 | 30 | 42.5 | CCS MV switchgear building (VFDs) | LV 600 V | 6 | 1
CONDITIONAL: HP export compressor + metering |  | G | Motor 4 of 4, 30 kW | 480 | 30 | 42.5 | CCS MV switchgear building (VFDs) | LV 600 V | 6 | 1
DCC-A pumps + water filter |  | G | Motor 1 of 2, 200 kW | 480 | 200 | 283 | CCS MV switchgear building (VFDs) | LV 600 V | 500 kcmil | 1
DCC-A pumps + water filter |  | G | Motor 2 of 2, 200 kW | 480 | 200 | 283 | CCS MV switchgear building (VFDs) | LV 600 V | 500 kcmil | 1
DCC-A: direct-contact cooler (quench) | DCC-A | G | LV power feeder | 480 | 15 | 21.2 | CCS MV switchgear building (VFDs) | LV 600 V | 6 | 1
DCC-A: direct-contact cooler (quench) | DCC-A | G | Area / platform lighting circuit 1 (8 fixtures) | 480 | 3 | 5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
DCC-B pumps + water filter |  | G | Motor 1 of 2, 200 kW | 480 | 200 | 283 | CCS MV switchgear building (VFDs) | LV 600 V | 500 kcmil | 1
DCC-B pumps + water filter |  | G | Motor 2 of 2, 200 kW | 480 | 200 | 283 | CCS MV switchgear building (VFDs) | LV 600 V | 500 kcmil | 1
DCC-B: direct-contact cooler (quench) | DCC-B | G | LV power feeder | 480 | 15 | 21.2 | CCS MV switchgear building (VFDs) | LV 600 V | 8 | 1
DCC-B: direct-contact cooler (quench) | DCC-B | G | Area / platform lighting circuit 1 (8 fixtures) | 480 | 3 | 5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
DCC-C pumps + water filter |  | G | Motor 1 of 2, 200 kW | 480 | 200 | 283 | CCS MV switchgear building (VFDs) | LV 600 V | 500 kcmil | 1
DCC-C pumps + water filter |  | G | Motor 2 of 2, 200 kW | 480 | 200 | 283 | CCS MV switchgear building (VFDs) | LV 600 V | 500 kcmil | 1
DCC-C: direct-contact cooler (quench) | DCC-C | G | LV power feeder | 480 | 15 | 21.2 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
DCC-C: direct-contact cooler (quench) | DCC-C | G | Area / platform lighting circuit 1 (8 fixtures) | 480 | 3 | 5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
DMP-A: diverter / bypass damper | DMP-A | G | Motor 1 of 2, 15 kW | 480 | 15 | 21.2 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
DMP-A: diverter / bypass damper | DMP-A | G | Motor 2 of 2, 15 kW | 480 | 15 | 21.2 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
DMP-B: diverter / bypass damper | DMP-B | G | Motor 1 of 2, 15 kW | 480 | 15 | 21.2 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
DMP-B: diverter / bypass damper | DMP-B | G | Motor 2 of 2, 15 kW | 480 | 15 | 21.2 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
DMP-C: diverter / bypass damper | DMP-C | G | Motor 1 of 2, 15 kW | 480 | 15 | 21.2 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
DMP-C: diverter / bypass damper | DMP-C | G | Motor 2 of 2, 15 kW | 480 | 15 | 21.2 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
RB-A: reboiler (LP steam from ST extraction) |  | G | MOV 1: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
RB-A: reboiler (LP steam from ST extraction) |  | G | MOV 2: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
RB-A: reboiler (LP steam from ST extraction) |  | G | MOV 3: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
RB-A: reboiler (LP steam from ST extraction) |  | G | MOV 4: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
RB-A: reboiler (LP steam from ST extraction) |  | G | LV power feeder | 480 | 10 | 14.2 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
RB-B: reboiler (LP steam from ST extraction) |  | G | MOV 1: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
RB-B: reboiler (LP steam from ST extraction) |  | G | MOV 2: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
RB-B: reboiler (LP steam from ST extraction) |  | G | MOV 3: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
RB-B: reboiler (LP steam from ST extraction) |  | G | MOV 4: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
RB-B: reboiler (LP steam from ST extraction) |  | G | LV power feeder | 480 | 10 | 14.2 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
RB-C: reboiler (LP steam from ST extraction) |  | G | MOV 1: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
RB-C: reboiler (LP steam from ST extraction) |  | G | MOV 2: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
RB-C: reboiler (LP steam from ST extraction) |  | G | MOV 3: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
RB-C: reboiler (LP steam from ST extraction) |  | G | MOV 4: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
RB-C: reboiler (LP steam from ST extraction) |  | G | LV power feeder | 480 | 10 | 14.2 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Reclaimer (thermal, intermittent) |  | G | Motor 1 of 2, 15 kW | 480 | 15 | 21.2 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Reclaimer (thermal, intermittent) |  | G | Motor 2 of 2, 15 kW | 480 | 15 | 21.2 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
STR-A: stripper / regenerator (45 ft dia x 207 ft) | STR-A | G | MOV 1: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
STR-A: stripper / regenerator (45 ft dia x 207 ft) | STR-A | G | MOV 2: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
STR-A: stripper / regenerator (45 ft dia x 207 ft) | STR-A | G | MOV 3: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
STR-A: stripper / regenerator (45 ft dia x 207 ft) | STR-A | G | MOV 4: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
STR-A: stripper / regenerator (45 ft dia x 207 ft) | STR-A | G | MOV 5: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
STR-A: stripper / regenerator (45 ft dia x 207 ft) | STR-A | G | MOV 6: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
STR-A: stripper / regenerator (45 ft dia x 207 ft) | STR-A | G | LV power feeder | 480 | 30 | 42.5 | CCS MV switchgear building (VFDs) | LV 600 V | 6 | 1
STR-A: stripper / regenerator (45 ft dia x 207 ft) | STR-A | G | Area / platform lighting circuit 1 (12 fixtures) | 480 | 3 | 5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
STR-A: stripper / regenerator (45 ft dia x 207 ft) | STR-A | G | Area / platform lighting circuit 2 (8 fixtures) | 480 | 3 | 5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
STR-A: stripper / regenerator (45 ft dia x 207 ft) | STR-A | G | 480 V welding receptacle 1 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
STR-A: stripper / regenerator (45 ft dia x 207 ft) | STR-A | G | 480 V welding receptacle 2 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
STR-A: stripper / regenerator (45 ft dia x 207 ft) | STR-A | G | 480 V welding receptacle 3 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
STR-A: stripper / regenerator (45 ft dia x 207 ft) | STR-A | G | 480 V welding receptacle 4 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
STR-B: stripper / regenerator (45 ft dia x 207 ft) | STR-B | G | MOV 1: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
STR-B: stripper / regenerator (45 ft dia x 207 ft) | STR-B | G | MOV 2: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
STR-B: stripper / regenerator (45 ft dia x 207 ft) | STR-B | G | MOV 3: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
STR-B: stripper / regenerator (45 ft dia x 207 ft) | STR-B | G | MOV 4: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
STR-B: stripper / regenerator (45 ft dia x 207 ft) | STR-B | G | MOV 5: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
STR-B: stripper / regenerator (45 ft dia x 207 ft) | STR-B | G | MOV 6: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
STR-B: stripper / regenerator (45 ft dia x 207 ft) | STR-B | G | LV power feeder | 480 | 30 | 42.5 | CCS MV switchgear building (VFDs) | LV 600 V | 6 | 1
STR-B: stripper / regenerator (45 ft dia x 207 ft) | STR-B | G | Area / platform lighting circuit 1 (12 fixtures) | 480 | 3 | 5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
STR-B: stripper / regenerator (45 ft dia x 207 ft) | STR-B | G | Area / platform lighting circuit 2 (8 fixtures) | 480 | 3 | 5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
STR-B: stripper / regenerator (45 ft dia x 207 ft) | STR-B | G | 480 V welding receptacle 1 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
STR-B: stripper / regenerator (45 ft dia x 207 ft) | STR-B | G | 480 V welding receptacle 2 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
STR-B: stripper / regenerator (45 ft dia x 207 ft) | STR-B | G | 480 V welding receptacle 3 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
STR-B: stripper / regenerator (45 ft dia x 207 ft) | STR-B | G | 480 V welding receptacle 4 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
STR-C: stripper / regenerator (45 ft dia x 207 ft) | STR-C | G | MOV 1: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
STR-C: stripper / regenerator (45 ft dia x 207 ft) | STR-C | G | MOV 2: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
STR-C: stripper / regenerator (45 ft dia x 207 ft) | STR-C | G | MOV 3: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
STR-C: stripper / regenerator (45 ft dia x 207 ft) | STR-C | G | MOV 4: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
STR-C: stripper / regenerator (45 ft dia x 207 ft) | STR-C | G | MOV 5: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
STR-C: stripper / regenerator (45 ft dia x 207 ft) | STR-C | G | MOV 6: power | 480 | 2.5 | 3.5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
STR-C: stripper / regenerator (45 ft dia x 207 ft) | STR-C | G | LV power feeder | 480 | 30 | 42.5 | CCS MV switchgear building (VFDs) | LV 600 V | 6 | 1
STR-C: stripper / regenerator (45 ft dia x 207 ft) | STR-C | G | Area / platform lighting circuit 1 (12 fixtures) | 480 | 3 | 5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
STR-C: stripper / regenerator (45 ft dia x 207 ft) | STR-C | G | Area / platform lighting circuit 2 (8 fixtures) | 480 | 3 | 5 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
STR-C: stripper / regenerator (45 ft dia x 207 ft) | STR-C | G | 480 V welding receptacle 1 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
STR-C: stripper / regenerator (45 ft dia x 207 ft) | STR-C | G | 480 V welding receptacle 2 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
STR-C: stripper / regenerator (45 ft dia x 207 ft) | STR-C | G | 480 V welding receptacle 3 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
STR-C: stripper / regenerator (45 ft dia x 207 ft) | STR-C | G | 480 V welding receptacle 4 | 480 | 60 | 76 | CCS MV switchgear building (VFDs) | LV 600 V | 2 | 1
Solvent + NaOH storage |  | G | Motor 1 of 4, 15 kW | 480 | 15 | 21.2 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Solvent + NaOH storage |  | G | Motor 2 of 4, 15 kW | 480 | 15 | 21.2 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Solvent + NaOH storage |  | G | Motor 3 of 4, 15 kW | 480 | 15 | 21.2 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Solvent + NaOH storage |  | G | Motor 4 of 4, 15 kW | 480 | 15 | 21.2 | CCS MV switchgear building (VFDs) | LV 600 V | 10 | 1
Water-wash pumps A |  | G | Motor 1 of 2, 110 kW | 480 | 110 | 155.7 | CCS MV switchgear building (VFDs) | LV 600 V | 3/0 | 1
Water-wash pumps A |  | G | Motor 2 of 2, 110 kW | 480 | 110 | 155.7 | CCS MV switchgear building (VFDs) | LV 600 V | 3/0 | 1
Water-wash pumps B |  | G | Motor 1 of 2, 110 kW | 480 | 110 | 155.7 | CCS MV switchgear building (VFDs) | LV 600 V | 3/0 | 1
Water-wash pumps B |  | G | Motor 2 of 2, 110 kW | 480 | 110 | 155.7 | CCS MV switchgear building (VFDs) | LV 600 V | 3/0 | 1
Water-wash pumps C |  | G | Motor 1 of 2, 110 kW | 480 | 110 | 155.7 | CCS MV switchgear building (VFDs) | LV 600 V | 3/0 | 1
Water-wash pumps C |  | G | Motor 2 of 2, 110 kW | 480 | 110 | 155.7 | CCS MV switchgear building (VFDs) | LV 600 V | 3/0 | 1
BF-A: booster fan (~16 MW) | BF-A | G | Booster fan BF-A (MV VFD output) | 13800 | 16000 | 744 | CCS MV switchgear building (VFDs) | MV 15 kV | 750 kcmil | 2
BF-B: booster fan (~16 MW) | BF-B | G | Booster fan BF-B (MV VFD output) | 13800 | 16000 | 744 | CCS MV switchgear building (VFDs) | MV 15 kV | 750 kcmil | 2
BF-C: booster fan (~16 MW) | BF-C | G | Booster fan BF-C (MV VFD output) | 13800 | 16000 | 744 | CCS MV switchgear building (VFDs) | MV 15 kV | 750 kcmil | 2
CCS MV switchgear building (VFDs) |  | G | CCS T-1 secondary to CCS 13.8 kV switchgear | 13800 | 60000 | 2510 | CCS T-1: 230/13.8 kV | MV 15 kV | 1000 kcmil | 5
CCS MV switchgear building (VFDs) |  | G | CCS T-2 secondary to CCS 13.8 kV switchgear | 13800 | 60000 | 2510 | CCS T-2: 230/13.8 kV | MV 15 kV | 1000 kcmil | 5
CO2 compression 3 x ~19 MW + dehydration |  | G | CO2 compressor train 1 | 13800 | 19000 | 883 | CCS MV switchgear building (VFDs) | MV 15 kV | 750 kcmil | 2
CO2 compression 3 x ~19 MW + dehydration |  | G | CO2 compressor train 2 | 13800 | 19000 | 883 | CCS MV switchgear building (VFDs) | MV 15 kV | 750 kcmil | 2
CO2 compression 3 x ~19 MW + dehydration |  | G | CO2 compressor train 3 | 13800 | 19000 | 883 | CCS MV switchgear building (VFDs) | MV 15 kV | 750 kcmil | 2
CONDITIONAL: HP export compressor + metering |  | G | HP CO2 export compressor (conditional) | 13800 | 8000 | 372 | CCS MV switchgear building (VFDs) | MV 15 kV | 750 kcmil | 1
CT MCC / VFD e-house |  | G | CT MCC / VFD e-house transformer | 13800 | 3000 | 126 | CCS MV switchgear building (VFDs) | MV 15 kV | 1/0 | 1
CT MCC / VFD e-house |  | G | CT MCC / VFD e-house transformer | 13800 | 3000 | 126 | CCS MV switchgear building (VFDs) | MV 15 kV | 1/0 | 1
CCS circulating-water pumps |  | G | CCS circulating-water pump 1 | 4160 | 1200 | 185 | CCS MV switchgear building (VFDs) | MV 5 kV | 4/0 | 1
CCS circulating-water pumps |  | G | CCS circulating-water pump 2 | 4160 | 1200 | 185 | CCS MV switchgear building (VFDs) | MV 5 kV | 4/0 | 1
CCS circulating-water pumps |  | G | CCS circulating-water pump 3 | 4160 | 1200 | 185 | CCS MV switchgear building (VFDs) | MV 5 kV | 4/0 | 1
CCS circulating-water pumps |  | G | CCS circulating-water pump 4 | 4160 | 1200 | 185 | CCS MV switchgear building (VFDs) | MV 5 kV | 4/0 | 1
Rich/lean pumps, cross exchanger, lean cooler A |  | G | Rich / lean amine pumps (A) | 4160 | 450 | 69 | CCS MV switchgear building (VFDs) | MV 5 kV | 2 | 1
Rich/lean pumps, cross exchanger, lean cooler A |  | G | Rich / lean amine pumps (A) | 4160 | 450 | 69 | CCS MV switchgear building (VFDs) | MV 5 kV | 2 | 1
Rich/lean pumps, cross exchanger, lean cooler B |  | G | Rich / lean amine pumps (B) | 4160 | 450 | 69 | CCS MV switchgear building (VFDs) | MV 5 kV | 2 | 1
Rich/lean pumps, cross exchanger, lean cooler B |  | G | Rich / lean amine pumps (B) | 4160 | 450 | 69 | CCS MV switchgear building (VFDs) | MV 5 kV | 2 | 1
Rich/lean pumps, cross exchanger, lean cooler C |  | G | Rich / lean amine pumps (C) | 4160 | 450 | 69 | CCS MV switchgear building (VFDs) | MV 5 kV | 2 | 1
Rich/lean pumps, cross exchanger, lean cooler C |  | G | Rich / lean amine pumps (C) | 4160 | 450 | 69 | CCS MV switchgear building (VFDs) | MV 5 kV | 2 | 1
BESS PCS / MV skid |  | H | DC 1,500 V: container to PCS (2 x 1/C per pole pair) | 1500 | 4000 |  | BESS container (ISO 40 ft high cube) | DC 2 kV | 500 kcmil | 4
BESS PCS / MV skid |  | H | DC 1,500 V: container to PCS (2 x 1/C per pole pair) | 1500 | 4000 |  | BESS container (ISO 40 ft high cube) | DC 2 kV | 500 kcmil | 4
BESS PCS / MV skid |  | H | DC 1,500 V: container to PCS (2 x 1/C per pole pair) | 1500 | 4000 |  | BESS container (ISO 40 ft high cube) | DC 2 kV | 500 kcmil | 4
BESS PCS / MV skid |  | H | DC 1,500 V: container to PCS (2 x 1/C per pole pair) | 1500 | 4000 |  | BESS container (ISO 40 ft high cube) | DC 2 kV | 500 kcmil | 4
BESS PCS / MV skid |  | H | DC 1,500 V: container to PCS (2 x 1/C per pole pair) | 1500 | 4000 |  | BESS container (ISO 40 ft high cube) | DC 2 kV | 500 kcmil | 4
BESS PCS / MV skid |  | H | DC 1,500 V: container to PCS (2 x 1/C per pole pair) | 1500 | 4000 |  | BESS container (ISO 40 ft high cube) | DC 2 kV | 500 kcmil | 4
BESS PCS / MV skid |  | H | DC 1,500 V: container to PCS (2 x 1/C per pole pair) | 1500 | 4000 |  | BESS container (ISO 40 ft high cube) | DC 2 kV | 500 kcmil | 4
BESS PCS / MV skid |  | H | DC 1,500 V: container to PCS (2 x 1/C per pole pair) | 1500 | 4000 |  | BESS container (ISO 40 ft high cube) | DC 2 kV | 500 kcmil | 4
BESS PCS / MV skid |  | H | DC 1,500 V: container to PCS (2 x 1/C per pole pair) | 1500 | 4000 |  | BESS container (ISO 40 ft high cube) | DC 2 kV | 500 kcmil | 4
BESS PCS / MV skid |  | H | DC 1,500 V: container to PCS (2 x 1/C per pole pair) | 1500 | 4000 |  | BESS container (ISO 40 ft high cube) | DC 2 kV | 500 kcmil | 4
BESS PCS / MV skid |  | H | DC 1,500 V: container to PCS (2 x 1/C per pole pair) | 1500 | 4000 |  | BESS container (ISO 40 ft high cube) | DC 2 kV | 500 kcmil | 4
BESS PCS / MV skid |  | H | DC 1,500 V: container to PCS (2 x 1/C per pole pair) | 1500 | 4000 |  | BESS container (ISO 40 ft high cube) | DC 2 kV | 500 kcmil | 4
BESS PCS / MV skid |  | H | DC 1,500 V: container to PCS (2 x 1/C per pole pair) | 1500 | 4000 |  | BESS container (ISO 40 ft high cube) | DC 2 kV | 500 kcmil | 4
BESS PCS / MV skid |  | H | DC 1,500 V: container to PCS (2 x 1/C per pole pair) | 1500 | 4000 |  | BESS container (ISO 40 ft high cube) | DC 2 kV | 500 kcmil | 4
BESS PCS / MV skid |  | H | DC 1,500 V: container to PCS (2 x 1/C per pole pair) | 1500 | 4000 |  | BESS container (ISO 40 ft high cube) | DC 2 kV | 500 kcmil | 4
BESS PCS / MV skid |  | H | DC 1,500 V: container to PCS (2 x 1/C per pole pair) | 1500 | 4000 |  | BESS container (ISO 40 ft high cube) | DC 2 kV | 500 kcmil | 4
BESS PCS / MV skid |  | H | DC 1,500 V: container to PCS (2 x 1/C per pole pair) | 1500 | 4000 |  | BESS container (ISO 40 ft high cube) | DC 2 kV | 500 kcmil | 4
BESS PCS / MV skid |  | H | DC 1,500 V: container to PCS (2 x 1/C per pole pair) | 1500 | 4000 |  | BESS container (ISO 40 ft high cube) | DC 2 kV | 500 kcmil | 4
BESS PCS / MV skid |  | H | DC 1,500 V: container to PCS (2 x 1/C per pole pair) | 1500 | 4000 |  | BESS container (ISO 40 ft high cube) | DC 2 kV | 500 kcmil | 4
BESS PCS / MV skid |  | H | DC 1,500 V: container to PCS (2 x 1/C per pole pair) | 1500 | 4000 |  | BESS container (ISO 40 ft high cube) | DC 2 kV | 500 kcmil | 4
BESS PCS / MV skid |  | H | DC 1,500 V: container to PCS (2 x 1/C per pole pair) | 1500 | 4000 |  | BESS container (ISO 40 ft high cube) | DC 2 kV | 500 kcmil | 4
BESS PCS / MV skid |  | H | DC 1,500 V: container to PCS (2 x 1/C per pole pair) | 1500 | 4000 |  | BESS container (ISO 40 ft high cube) | DC 2 kV | 500 kcmil | 4
BESS PCS / MV skid |  | H | DC 1,500 V: container to PCS (2 x 1/C per pole pair) | 1500 | 4000 |  | BESS container (ISO 40 ft high cube) | DC 2 kV | 500 kcmil | 4
BESS PCS / MV skid |  | H | DC 1,500 V: container to PCS (2 x 1/C per pole pair) | 1500 | 4000 |  | BESS container (ISO 40 ft high cube) | DC 2 kV | 500 kcmil | 4
BESS PCS / MV skid |  | H | DC 1,500 V: container to PCS (2 x 1/C per pole pair) | 1500 | 4000 |  | BESS container (ISO 40 ft high cube) | DC 2 kV | 500 kcmil | 4
BESS PCS / MV skid |  | H | DC 1,500 V: container to PCS (2 x 1/C per pole pair) | 1500 | 4000 |  | BESS container (ISO 40 ft high cube) | DC 2 kV | 500 kcmil | 4
BESS PCS / MV skid |  | H | DC 1,500 V: container to PCS (2 x 1/C per pole pair) | 1500 | 4000 |  | BESS container (ISO 40 ft high cube) | DC 2 kV | 500 kcmil | 4
BESS PCS / MV skid |  | H | DC 1,500 V: container to PCS (2 x 1/C per pole pair) | 1500 | 4000 |  | BESS container (ISO 40 ft high cube) | DC 2 kV | 500 kcmil | 4
BESS PCS / MV skid |  | H | DC 1,500 V: container to PCS (2 x 1/C per pole pair) | 1500 | 4000 |  | BESS container (ISO 40 ft high cube) | DC 2 kV | 500 kcmil | 4
BESS PCS / MV skid |  | H | DC 1,500 V: container to PCS (2 x 1/C per pole pair) | 1500 | 4000 |  | BESS container (ISO 40 ft high cube) | DC 2 kV | 500 kcmil | 4
34.5 kV collector e-house (arc-resistant) |  | H | LV panel / distribution feeder | 480 | 30 | 42.5 | BESS auxiliary transformer | LV 600 V | 6 | 1
BESS EMS / SCADA and revenue metering |  | H | LV panel / distribution feeder | 480 | 30 | 42.5 | BESS auxiliary transformer | LV 600 V | 6 | 1
BESS PCS / MV skid |  | H | Motor 1 of 2, 7 kW | 480 | 7 | 9.9 | BESS auxiliary transformer | LV 600 V | 10 | 1
BESS PCS / MV skid |  | H | Motor 2 of 2, 7 kW | 480 | 7 | 9.9 | BESS auxiliary transformer | LV 600 V | 10 | 1
BESS PCS / MV skid |  | H | Motor 1 of 2, 7 kW | 480 | 7 | 9.9 | BESS auxiliary transformer | LV 600 V | 10 | 1
BESS PCS / MV skid |  | H | Motor 2 of 2, 7 kW | 480 | 7 | 9.9 | BESS auxiliary transformer | LV 600 V | 10 | 1
BESS PCS / MV skid |  | H | Motor 1 of 2, 7 kW | 480 | 7 | 9.9 | BESS auxiliary transformer | LV 600 V | 10 | 1
BESS PCS / MV skid |  | H | Motor 2 of 2, 7 kW | 480 | 7 | 9.9 | BESS auxiliary transformer | LV 600 V | 10 | 1
BESS PCS / MV skid |  | H | Motor 1 of 2, 7 kW | 480 | 7 | 9.9 | BESS auxiliary transformer | LV 600 V | 10 | 1
BESS PCS / MV skid |  | H | Motor 2 of 2, 7 kW | 480 | 7 | 9.9 | BESS auxiliary transformer | LV 600 V | 10 | 1
BESS PCS / MV skid |  | H | Motor 1 of 2, 7 kW | 480 | 7 | 9.9 | BESS auxiliary transformer | LV 600 V | 10 | 1
BESS PCS / MV skid |  | H | Motor 2 of 2, 7 kW | 480 | 7 | 9.9 | BESS auxiliary transformer | LV 600 V | 10 | 1
BESS PCS / MV skid |  | H | Motor 1 of 2, 7 kW | 480 | 7 | 9.9 | BESS auxiliary transformer | LV 600 V | 10 | 1
BESS PCS / MV skid |  | H | Motor 2 of 2, 7 kW | 480 | 7 | 9.9 | BESS auxiliary transformer | LV 600 V | 10 | 1
BESS PCS / MV skid |  | H | Motor 1 of 2, 7 kW | 480 | 7 | 9.9 | BESS auxiliary transformer | LV 600 V | 10 | 1
BESS PCS / MV skid |  | H | Motor 2 of 2, 7 kW | 480 | 7 | 9.9 | BESS auxiliary transformer | LV 600 V | 10 | 1
BESS PCS / MV skid |  | H | Motor 1 of 2, 7 kW | 480 | 7 | 9.9 | BESS auxiliary transformer | LV 600 V | 10 | 1
BESS PCS / MV skid |  | H | Motor 2 of 2, 7 kW | 480 | 7 | 9.9 | BESS auxiliary transformer | LV 600 V | 10 | 1
BESS PCS / MV skid |  | H | Motor 1 of 2, 7 kW | 480 | 7 | 9.9 | BESS auxiliary transformer | LV 600 V | 10 | 1
BESS PCS / MV skid |  | H | Motor 2 of 2, 7 kW | 480 | 7 | 9.9 | BESS auxiliary transformer | LV 600 V | 10 | 1
BESS PCS / MV skid |  | H | Motor 1 of 2, 7 kW | 480 | 7 | 9.9 | BESS auxiliary transformer | LV 600 V | 8 | 1
BESS PCS / MV skid |  | H | Motor 2 of 2, 7 kW | 480 | 7 | 9.9 | BESS auxiliary transformer | LV 600 V | 8 | 1
BESS PCS / MV skid |  | H | Motor 1 of 2, 7 kW | 480 | 7 | 9.9 | BESS auxiliary transformer | LV 600 V | 10 | 1
BESS PCS / MV skid |  | H | Motor 2 of 2, 7 kW | 480 | 7 | 9.9 | BESS auxiliary transformer | LV 600 V | 10 | 1
BESS PCS / MV skid |  | H | Motor 1 of 2, 7 kW | 480 | 7 | 9.9 | BESS auxiliary transformer | LV 600 V | 10 | 1
BESS PCS / MV skid |  | H | Motor 2 of 2, 7 kW | 480 | 7 | 9.9 | BESS auxiliary transformer | LV 600 V | 10 | 1
BESS PCS / MV skid |  | H | Motor 1 of 2, 7 kW | 480 | 7 | 9.9 | BESS auxiliary transformer | LV 600 V | 8 | 1
BESS PCS / MV skid |  | H | Motor 2 of 2, 7 kW | 480 | 7 | 9.9 | BESS auxiliary transformer | LV 600 V | 8 | 1
BESS PCS / MV skid |  | H | Motor 1 of 2, 7 kW | 480 | 7 | 9.9 | BESS auxiliary transformer | LV 600 V | 10 | 1
BESS PCS / MV skid |  | H | Motor 2 of 2, 7 kW | 480 | 7 | 9.9 | BESS auxiliary transformer | LV 600 V | 10 | 1
BESS PCS / MV skid |  | H | Motor 1 of 2, 7 kW | 480 | 7 | 9.9 | BESS auxiliary transformer | LV 600 V | 10 | 1
BESS PCS / MV skid |  | H | Motor 2 of 2, 7 kW | 480 | 7 | 9.9 | BESS auxiliary transformer | LV 600 V | 10 | 1
BESS container (ISO 40 ft high cube) |  | H | Container auxiliary 480 V | 480 | 60 | 85 | BESS PCS / MV skid | LV 600 V | 2 | 1
BESS container (ISO 40 ft high cube) |  | H | Container auxiliary 480 V | 480 | 60 | 85 | BESS PCS / MV skid | LV 600 V | 2 | 1
BESS container (ISO 40 ft high cube) |  | H | Container auxiliary 480 V | 480 | 60 | 85 | BESS PCS / MV skid | LV 600 V | 2 | 1
BESS container (ISO 40 ft high cube) |  | H | Container auxiliary 480 V | 480 | 60 | 85 | BESS PCS / MV skid | LV 600 V | 2 | 1
BESS container (ISO 40 ft high cube) |  | H | Container auxiliary 480 V | 480 | 60 | 85 | BESS PCS / MV skid | LV 600 V | 2 | 1
BESS container (ISO 40 ft high cube) |  | H | Container auxiliary 480 V | 480 | 60 | 85 | BESS PCS / MV skid | LV 600 V | 2 | 1
BESS container (ISO 40 ft high cube) |  | H | Container auxiliary 480 V | 480 | 60 | 85 | BESS PCS / MV skid | LV 600 V | 2 | 1
BESS container (ISO 40 ft high cube) |  | H | Container auxiliary 480 V | 480 | 60 | 85 | BESS PCS / MV skid | LV 600 V | 2 | 1
BESS container (ISO 40 ft high cube) |  | H | Container auxiliary 480 V | 480 | 60 | 85 | BESS PCS / MV skid | LV 600 V | 2 | 1
BESS container (ISO 40 ft high cube) |  | H | Container auxiliary 480 V | 480 | 60 | 85 | BESS PCS / MV skid | LV 600 V | 2 | 1
BESS container (ISO 40 ft high cube) |  | H | Container auxiliary 480 V | 480 | 60 | 85 | BESS PCS / MV skid | LV 600 V | 2 | 1
BESS container (ISO 40 ft high cube) |  | H | Container auxiliary 480 V | 480 | 60 | 85 | BESS PCS / MV skid | LV 600 V | 2 | 1
BESS container (ISO 40 ft high cube) |  | H | Container auxiliary 480 V | 480 | 60 | 85 | BESS PCS / MV skid | LV 600 V | 2 | 1
BESS container (ISO 40 ft high cube) |  | H | Container auxiliary 480 V | 480 | 60 | 85 | BESS PCS / MV skid | LV 600 V | 2 | 1
BESS container (ISO 40 ft high cube) |  | H | Container auxiliary 480 V | 480 | 60 | 85 | BESS PCS / MV skid | LV 600 V | 2 | 1
BESS container (ISO 40 ft high cube) |  | H | Container auxiliary 480 V | 480 | 60 | 85 | BESS PCS / MV skid | LV 600 V | 2 | 1
BESS container (ISO 40 ft high cube) |  | H | Container auxiliary 480 V | 480 | 60 | 85 | BESS PCS / MV skid | LV 600 V | 2 | 1
BESS container (ISO 40 ft high cube) |  | H | Container auxiliary 480 V | 480 | 60 | 85 | BESS PCS / MV skid | LV 600 V | 2 | 1
BESS container (ISO 40 ft high cube) |  | H | Container auxiliary 480 V | 480 | 60 | 85 | BESS PCS / MV skid | LV 600 V | 2 | 1
BESS container (ISO 40 ft high cube) |  | H | Container auxiliary 480 V | 480 | 60 | 85 | BESS PCS / MV skid | LV 600 V | 2 | 1
BESS container (ISO 40 ft high cube) |  | H | Container auxiliary 480 V | 480 | 60 | 85 | BESS PCS / MV skid | LV 600 V | 2 | 1
BESS container (ISO 40 ft high cube) |  | H | Container auxiliary 480 V | 480 | 60 | 85 | BESS PCS / MV skid | LV 600 V | 2 | 1
BESS container (ISO 40 ft high cube) |  | H | Container auxiliary 480 V | 480 | 60 | 85 | BESS PCS / MV skid | LV 600 V | 2 | 1
BESS container (ISO 40 ft high cube) |  | H | Container auxiliary 480 V | 480 | 60 | 85 | BESS PCS / MV skid | LV 600 V | 2 | 1
BESS container (ISO 40 ft high cube) |  | H | Container auxiliary 480 V | 480 | 60 | 85 | BESS PCS / MV skid | LV 600 V | 2 | 1
BESS container (ISO 40 ft high cube) |  | H | Container auxiliary 480 V | 480 | 60 | 85 | BESS PCS / MV skid | LV 600 V | 2 | 1
BESS container (ISO 40 ft high cube) |  | H | Container auxiliary 480 V | 480 | 60 | 85 | BESS PCS / MV skid | LV 600 V | 2 | 1
BESS container (ISO 40 ft high cube) |  | H | Container auxiliary 480 V | 480 | 60 | 85 | BESS PCS / MV skid | LV 600 V | 2 | 1
BESS container (ISO 40 ft high cube) |  | H | Container auxiliary 480 V | 480 | 60 | 85 | BESS PCS / MV skid | LV 600 V | 2 | 1
BESS container (ISO 40 ft high cube) |  | H | Container auxiliary 480 V | 480 | 60 | 85 | BESS PCS / MV skid | LV 600 V | 2 | 1
BESS main power transformer 34.5/230 kV (to D4 upper) | BESS MPT | H | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | BESS auxiliary transformer | LV 600 V | 10 | 1
BESS main power transformer 34.5/230 kV (to D4 upper) | BESS MPT | H | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | BESS auxiliary transformer | LV 600 V | 10 | 1
BESS main power transformer 34.5/230 kV (to D4 upper) | BESS MPT | H | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | BESS auxiliary transformer | LV 600 V | 10 | 1
BESS main power transformer 34.5/230 kV (to D4 upper) | BESS MPT | H | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | BESS auxiliary transformer | LV 600 V | 10 | 1
BESS main power transformer 34.5/230 kV (to D4 upper) | BESS MPT | H | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | BESS auxiliary transformer | LV 600 V | 10 | 1
BESS main power transformer 34.5/230 kV (to D4 upper) | BESS MPT | H | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | BESS auxiliary transformer | LV 600 V | 10 | 1
BESS yard: surfacing, fence, gate, signage, lighting |  | H | Yard lighting circuit 1 (10 floodlights) | 480 | 4 | 6 | BESS auxiliary transformer | LV 600 V | 8 | 1
BESS yard: surfacing, fence, gate, signage, lighting |  | H | Yard lighting circuit 2 (10 floodlights) | 480 | 4 | 6 | BESS auxiliary transformer | LV 600 V | 8 | 1
BESS yard: surfacing, fence, gate, signage, lighting |  | H | Yard lighting circuit 3 (4 floodlights) | 480 | 4 | 6 | BESS auxiliary transformer | LV 600 V | 8 | 1
34.5 kV collector e-house (arc-resistant) |  | H | 34.5 kV collection loop 1 | 34500 | 25000 | 418 | BESS PCS / MV skid | MV 35 kV | 350 kcmil | 2
34.5 kV collector e-house (arc-resistant) |  | H | 34.5 kV collection loop 2 | 34500 | 25000 | 418 | BESS PCS / MV skid | MV 35 kV | 350 kcmil | 2
34.5 kV collector e-house (arc-resistant) |  | H | 34.5 kV collection loop 3 | 34500 | 25000 | 418 | BESS PCS / MV skid | MV 35 kV | 350 kcmil | 2
BESS PCS / MV skid |  | H | 34.5 kV collection loop 1 | 34500 | 25000 | 418 | 34.5 kV collector e-house (arc-resistant) | MV 35 kV | 350 kcmil | 2
BESS PCS / MV skid |  | H | 34.5 kV collection loop 1 | 34500 | 25000 | 418 | BESS PCS / MV skid | MV 35 kV | 350 kcmil | 2
BESS PCS / MV skid |  | H | 34.5 kV collection loop 1 | 34500 | 25000 | 418 | BESS PCS / MV skid | MV 35 kV | 350 kcmil | 2
BESS PCS / MV skid |  | H | 34.5 kV collection loop 1 | 34500 | 25000 | 418 | BESS PCS / MV skid | MV 35 kV | 350 kcmil | 2
BESS PCS / MV skid |  | H | 34.5 kV collection loop 1 | 34500 | 25000 | 418 | BESS PCS / MV skid | MV 35 kV | 350 kcmil | 2
BESS PCS / MV skid |  | H | 34.5 kV collection loop 2 | 34500 | 25000 | 418 | 34.5 kV collector e-house (arc-resistant) | MV 35 kV | 350 kcmil | 2
BESS PCS / MV skid |  | H | 34.5 kV collection loop 2 | 34500 | 25000 | 418 | BESS PCS / MV skid | MV 35 kV | 350 kcmil | 2
BESS PCS / MV skid |  | H | 34.5 kV collection loop 2 | 34500 | 25000 | 418 | BESS PCS / MV skid | MV 35 kV | 350 kcmil | 2
BESS PCS / MV skid |  | H | 34.5 kV collection loop 2 | 34500 | 25000 | 418 | BESS PCS / MV skid | MV 35 kV | 350 kcmil | 2
BESS PCS / MV skid |  | H | 34.5 kV collection loop 2 | 34500 | 25000 | 418 | BESS PCS / MV skid | MV 35 kV | 350 kcmil | 2
BESS PCS / MV skid |  | H | 34.5 kV collection loop 3 | 34500 | 25000 | 418 | 34.5 kV collector e-house (arc-resistant) | MV 35 kV | 350 kcmil | 2
BESS PCS / MV skid |  | H | 34.5 kV collection loop 3 | 34500 | 25000 | 418 | BESS PCS / MV skid | MV 35 kV | 350 kcmil | 2
BESS PCS / MV skid |  | H | 34.5 kV collection loop 3 | 34500 | 25000 | 418 | BESS PCS / MV skid | MV 35 kV | 350 kcmil | 2
BESS PCS / MV skid |  | H | 34.5 kV collection loop 3 | 34500 | 25000 | 418 | BESS PCS / MV skid | MV 35 kV | 350 kcmil | 2
BESS PCS / MV skid |  | H | 34.5 kV collection loop 3 | 34500 | 25000 | 418 | BESS PCS / MV skid | MV 35 kV | 350 kcmil | 2
BESS main power transformer 34.5/230 kV (to D4 upper) | BESS MPT | H | BESS MPT 34.5 kV side | 34500 | 100000 | 1674 | 34.5 kV collector e-house (arc-resistant) | MV 35 kV | 750 kcmil | 5
CONDITIONAL: grounding transformer |  | H | Grounding transformer connection (34.5 kV) | 34500 | 2000 | 33 | 34.5 kV collector e-house (arc-resistant) | MV 35 kV | 2 | 1
Aqueous ammonia (SC units) |  | I | LV power feeder | 480 | 10 | 14.2 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 1/0 | 1
BS black-start switchgear |  | I | Black-start genset output | 480 | 2000 | 2532.3 | Black-start genset (proposed; requires study) | LV 600 V | 500 kcmil | 10
BS black-start switchgear |  | I | Black-start genset output | 480 | 2000 | 2532.3 | Black-start genset (proposed; requires study) | LV 600 V | 500 kcmil | 10
BS black-start switchgear |  | I | LV power feeder | 480 | 15 | 21.2 | PCM: power control module | LV 600 V | 6 | 1
CONDITIONAL: BESS black-start alternative |  | I | LV power feeder | 480 | 15 | 21.2 | PCM: power control module | LV 600 V | 6 | 1
CONDITIONAL: SC-1 inlet chiller / evaporative cooler |  | I | LV power feeder | 480 | 500 | 707.6 | PCM: power control module | LV 600 V | 350 kcmil | 3
CONDITIONAL: SC-2 inlet chiller / evaporative cooler |  | I | LV power feeder | 480 | 500 | 707.6 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 500 kcmil | 12
FC-5..12 inverter / AC cabinet / desulfurizer |  | I | FC-5 SOFC output to inverter / AC cabinet | 480 | 250 | 316.5 | FC-5: SOFC module (Bloom ES5 class, 200-300 kW) | LV 600 V | 3/0 | 2
FC-5..12 inverter / AC cabinet / desulfurizer |  | I | FC-6 SOFC output to inverter / AC cabinet | 480 | 250 | 316.5 | FC-6: SOFC module (Bloom ES5 class, 200-300 kW) | LV 600 V | 3/0 | 2
FC-5..12 inverter / AC cabinet / desulfurizer |  | I | FC-7 SOFC output to inverter / AC cabinet | 480 | 250 | 316.5 | FC-7: SOFC module (Bloom ES5 class, 200-300 kW) | LV 600 V | 3/0 | 2
FC-5..12 inverter / AC cabinet / desulfurizer |  | I | FC-8 SOFC output to inverter / AC cabinet | 480 | 250 | 316.5 | FC-8: SOFC module (Bloom ES5 class, 200-300 kW) | LV 600 V | 3/0 | 2
FC-5..12 inverter / AC cabinet / desulfurizer |  | I | FC-9 SOFC output to inverter / AC cabinet | 480 | 250 | 316.5 | FC-9: SOFC module (Bloom ES5 class, 200-300 kW) | LV 600 V | 3/0 | 2
FC-5..12 inverter / AC cabinet / desulfurizer |  | I | FC-10 SOFC output to inverter / AC cabinet | 480 | 250 | 316.5 | FC-10: SOFC module (Bloom ES5 class, 200-300 kW) | LV 600 V | 3/0 | 2
FC-5..12 inverter / AC cabinet / desulfurizer |  | I | FC-11 SOFC output to inverter / AC cabinet | 480 | 250 | 316.5 | FC-11: SOFC module (Bloom ES5 class, 200-300 kW) | LV 600 V | 3/0 | 2
FC-5..12 inverter / AC cabinet / desulfurizer |  | I | FC-12 SOFC output to inverter / AC cabinet | 480 | 250 | 316.5 | FC-12: SOFC module (Bloom ES5 class, 200-300 kW) | LV 600 V | 3/0 | 2
Fuel-cell inverter / AC cabinet / desulfurizer |  | I | FC-1 SOFC output to inverter / AC cabinet | 480 | 250 | 316.5 | FC-1: SOFC module (Bloom ES5 class, 200-300 kW) | LV 600 V | 3/0 | 2
Fuel-cell inverter / AC cabinet / desulfurizer |  | I | FC-2 SOFC output to inverter / AC cabinet | 480 | 250 | 316.5 | FC-2: SOFC module (Bloom ES5 class, 200-300 kW) | LV 600 V | 3/0 | 2
Fuel-cell inverter / AC cabinet / desulfurizer |  | I | FC-3 SOFC output to inverter / AC cabinet | 480 | 250 | 316.5 | FC-3: SOFC module (Bloom ES5 class, 200-300 kW) | LV 600 V | 3/0 | 2
Fuel-cell inverter / AC cabinet / desulfurizer |  | I | FC-4 SOFC output to inverter / AC cabinet | 480 | 250 | 316.5 | FC-4: SOFC module (Bloom ES5 class, 200-300 kW) | LV 600 V | 3/0 | 2
Fuel-gas compressors 3 x 100% electric |  | I | Motor 1 of 6, 15 kW | 480 | 15 | 21.2 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 3/0 | 1
Fuel-gas compressors 3 x 100% electric |  | I | Motor 2 of 6, 15 kW | 480 | 15 | 21.2 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 3/0 | 1
Fuel-gas compressors 3 x 100% electric |  | I | Motor 3 of 6, 15 kW | 480 | 15 | 21.2 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 3/0 | 1
Fuel-gas compressors 3 x 100% electric |  | I | Motor 4 of 6, 15 kW | 480 | 15 | 21.2 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 3/0 | 1
Fuel-gas compressors 3 x 100% electric |  | I | Motor 5 of 6, 15 kW | 480 | 15 | 21.2 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 3/0 | 1
Fuel-gas compressors 3 x 100% electric |  | I | Motor 6 of 6, 15 kW | 480 | 15 | 21.2 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 3/0 | 1
Gas conditioning skid |  | I | LV power feeder | 480 | 30 | 42.5 | PCM: power control module | LV 600 V | 6 | 1
Lube oil / starting air / oily water building |  | I | LV panel / distribution feeder | 480 | 79 | 111.8 | PCM: power control module | LV 600 V | 1/0 | 1
MOD-EH: 13.8 kV modular collector e-house | MOD-EH | I | LV panel / distribution feeder | 480 | 30 | 42.5 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 4 | 1
MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | I | Fuel-cell AC cabinet to MOD-LV | 480 | 1000 | 1266.2 | Fuel-cell inverter / AC cabinet / desulfurizer | LV 600 V | 350 kcmil | 6
MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | I | Fuel-cell AC cabinet to MOD-LV | 480 | 2000 | 2532.3 | FC-5..12 inverter / AC cabinet / desulfurizer | LV 600 V | 500 kcmil | 12
MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | I | MT-1 microturbine output | 480 | 1000 | 1266.2 | MT-1: microturbine 1 MW (Capstone C1000 class) | LV 600 V | 350 kcmil | 6
MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | I | MT-2 microturbine output | 480 | 1000 | 1266.2 | MT-2: microturbine 1 MW (Capstone C1000 class) | LV 600 V | 350 kcmil | 6
MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | I | MT-3 microturbine output | 480 | 1000 | 1266.2 | MT-3: microturbine 1 MW (Capstone C1000 class) | LV 600 V | 350 kcmil | 6
MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | I | MT-4 microturbine output | 480 | 1000 | 1266.2 | MT-4: microturbine 1 MW (Capstone C1000 class) | LV 600 V | 500 kcmil | 12
MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | I | MT-5 microturbine output | 480 | 1000 | 1266.2 | MT-5: microturbine 1 MW (Capstone C1000 class) | LV 600 V | 500 kcmil | 12
MOD-LV 480 V board + 480 V : 13.8 kV step-up |  | I | MT-6 microturbine output | 480 | 1000 | 1266.2 | MT-6: microturbine 1 MW (Capstone C1000 class) | LV 600 V | 500 kcmil | 12
PAD-TX 480 V : 13.8 kV | PAD-TX | I | PAD-LV to PAD-TX | 480 | 3000 | 3600 | PAD-LV 480 V paralleling switchboard | LV 600 V | 500 kcmil | 12
PCM: power control module |  | I | LV panel / distribution feeder | 480 | 38 | 53.8 | PCM: power control module | LV 600 V | 4 | 1
RICE 1 SCR + oxidation catalyst and stack |  | I | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | PCM: power control module | LV 600 V | 6 | 1
RICE 1 SCR + oxidation catalyst and stack |  | I | Area / platform lighting circuit 1 (6 fixtures) | 480 | 3 | 5 | PCM: power control module | LV 600 V | 10 | 1
RICE 1 radiators (5) |  | I | Motor 1 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 1 | 1
RICE 1 radiators (5) |  | I | Motor 2 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 1 | 1
RICE 1 radiators (5) |  | I | Motor 3 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 1 | 1
RICE 1 radiators (5) |  | I | Motor 4 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 1 | 1
RICE 1 radiators (5) |  | I | Motor 5 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 1 | 1
RICE 2 SCR + oxidation catalyst and stack |  | I | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | PCM: power control module | LV 600 V | 6 | 1
RICE 2 SCR + oxidation catalyst and stack |  | I | Area / platform lighting circuit 1 (6 fixtures) | 480 | 3 | 5 | PCM: power control module | LV 600 V | 10 | 1
RICE 2 radiators (5) |  | I | Motor 1 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 2 | 1
RICE 2 radiators (5) |  | I | Motor 2 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 2 | 1
RICE 2 radiators (5) |  | I | Motor 3 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 2 | 1
RICE 2 radiators (5) |  | I | Motor 4 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 2 | 1
RICE 2 radiators (5) |  | I | Motor 5 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 2 | 1
RICE 3 SCR + oxidation catalyst and stack |  | I | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | PCM: power control module | LV 600 V | 6 | 1
RICE 3 SCR + oxidation catalyst and stack |  | I | Area / platform lighting circuit 1 (6 fixtures) | 480 | 3 | 5 | PCM: power control module | LV 600 V | 10 | 1
RICE 3 radiators (5) |  | I | Motor 1 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 6 | 1
RICE 3 radiators (5) |  | I | Motor 2 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 6 | 1
RICE 3 radiators (5) |  | I | Motor 3 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 6 | 1
RICE 3 radiators (5) |  | I | Motor 4 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 6 | 1
RICE 3 radiators (5) |  | I | Motor 5 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 6 | 1
RICE 4 SCR + oxidation catalyst and stack |  | I | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | PCM: power control module | LV 600 V | 6 | 1
RICE 4 SCR + oxidation catalyst and stack |  | I | Area / platform lighting circuit 1 (6 fixtures) | 480 | 3 | 5 | PCM: power control module | LV 600 V | 10 | 1
RICE 4 radiators (5) |  | I | Motor 1 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 6 | 1
RICE 4 radiators (5) |  | I | Motor 2 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 6 | 1
RICE 4 radiators (5) |  | I | Motor 3 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 6 | 1
RICE 4 radiators (5) |  | I | Motor 4 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 6 | 1
RICE 4 radiators (5) |  | I | Motor 5 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 6 | 1
RICE 5 SCR + oxidation catalyst and stack |  | I | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | PCM: power control module | LV 600 V | 6 | 1
RICE 5 SCR + oxidation catalyst and stack |  | I | Area / platform lighting circuit 1 (6 fixtures) | 480 | 3 | 5 | PCM: power control module | LV 600 V | 10 | 1
RICE 5 radiators (5) |  | I | Motor 1 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 6 | 1
RICE 5 radiators (5) |  | I | Motor 2 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 6 | 1
RICE 5 radiators (5) |  | I | Motor 3 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 6 | 1
RICE 5 radiators (5) |  | I | Motor 4 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 6 | 1
RICE 5 radiators (5) |  | I | Motor 5 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 6 | 1
RICE 6 SCR + oxidation catalyst and stack |  | I | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | PCM: power control module | LV 600 V | 6 | 1
RICE 6 SCR + oxidation catalyst and stack |  | I | Area / platform lighting circuit 1 (6 fixtures) | 480 | 3 | 5 | PCM: power control module | LV 600 V | 10 | 1
RICE 6 radiators (5) |  | I | Motor 1 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 6 | 1
RICE 6 radiators (5) |  | I | Motor 2 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 6 | 1
RICE 6 radiators (5) |  | I | Motor 3 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 6 | 1
RICE 6 radiators (5) |  | I | Motor 4 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 6 | 1
RICE 6 radiators (5) |  | I | Motor 5 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 6 | 1
RICE 7 SCR + oxidation catalyst and stack |  | I | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | PCM: power control module | LV 600 V | 8 | 1
RICE 7 SCR + oxidation catalyst and stack |  | I | Area / platform lighting circuit 1 (6 fixtures) | 480 | 3 | 5 | PCM: power control module | LV 600 V | 10 | 1
RICE 7 radiators (5) |  | I | Motor 1 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 6 | 1
RICE 7 radiators (5) |  | I | Motor 2 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 6 | 1
RICE 7 radiators (5) |  | I | Motor 3 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 6 | 1
RICE 7 radiators (5) |  | I | Motor 4 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 6 | 1
RICE 7 radiators (5) |  | I | Motor 5 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 6 | 1
RICE 8 SCR + oxidation catalyst and stack |  | I | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | PCM: power control module | LV 600 V | 8 | 1
RICE 8 SCR + oxidation catalyst and stack |  | I | Area / platform lighting circuit 1 (6 fixtures) | 480 | 3 | 5 | PCM: power control module | LV 600 V | 10 | 1
RICE 8 radiators (5) |  | I | Motor 1 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 6 | 1
RICE 8 radiators (5) |  | I | Motor 2 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 6 | 1
RICE 8 radiators (5) |  | I | Motor 3 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 6 | 1
RICE 8 radiators (5) |  | I | Motor 4 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 6 | 1
RICE 8 radiators (5) |  | I | Motor 5 of 5, 30 kW (VFD output) | 480 | 30 | 42 | PCM: power control module | LV 600 V | 6 | 1
RICE CEMS |  | I | LV panel / distribution feeder | 480 | 30 | 42.5 | PCM: power control module | LV 600 V | 4 | 1
RICE engine hall (8 engines) | RICE | I | LV power feeder | 480 | 15 | 21.2 | PCM: power control module | LV 600 V | 8 | 1
RICE engine-generator 1 | RICE-1 | I | Motor 1 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 1 | RICE-1 | I | Motor 2 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 1 | RICE-1 | I | Motor 3 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 1 | RICE-1 | I | Motor 4 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 1 | RICE-1 | I | Motor 5 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 1 | RICE-1 | I | Motor 6 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 1 | RICE-1 | I | 480 V welding receptacle 1 | 480 | 60 | 76 | PCM: power control module | LV 600 V | 1/0 | 1
RICE engine-generator 1 | RICE-1 | I | 480 V welding receptacle 2 | 480 | 60 | 76 | PCM: power control module | LV 600 V | 1/0 | 1
RICE engine-generator 1 | RICE-1 | I | 480 V welding receptacle 3 | 480 | 60 | 76 | PCM: power control module | LV 600 V | 1/0 | 1
RICE engine-generator 1 | RICE-1 | I | 480 V welding receptacle 4 | 480 | 60 | 76 | PCM: power control module | LV 600 V | 1/0 | 1
RICE engine-generator 2 | RICE-2 | I | Motor 1 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 2 | RICE-2 | I | Motor 2 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 2 | RICE-2 | I | Motor 3 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 2 | RICE-2 | I | Motor 4 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 2 | RICE-2 | I | Motor 5 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 2 | RICE-2 | I | Motor 6 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 2 | RICE-2 | I | 480 V welding receptacle 1 | 480 | 60 | 76 | PCM: power control module | LV 600 V | 1/0 | 1
RICE engine-generator 2 | RICE-2 | I | 480 V welding receptacle 2 | 480 | 60 | 76 | PCM: power control module | LV 600 V | 1/0 | 1
RICE engine-generator 2 | RICE-2 | I | 480 V welding receptacle 3 | 480 | 60 | 76 | PCM: power control module | LV 600 V | 1/0 | 1
RICE engine-generator 2 | RICE-2 | I | 480 V welding receptacle 4 | 480 | 60 | 76 | PCM: power control module | LV 600 V | 1/0 | 1
RICE engine-generator 3 | RICE-3 | I | Motor 1 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 3 | RICE-3 | I | Motor 2 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 3 | RICE-3 | I | Motor 3 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 3 | RICE-3 | I | Motor 4 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 3 | RICE-3 | I | Motor 5 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 3 | RICE-3 | I | Motor 6 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 3 | RICE-3 | I | 480 V welding receptacle 1 | 480 | 60 | 76 | PCM: power control module | LV 600 V | 1 | 1
RICE engine-generator 3 | RICE-3 | I | 480 V welding receptacle 2 | 480 | 60 | 76 | PCM: power control module | LV 600 V | 1 | 1
RICE engine-generator 3 | RICE-3 | I | 480 V welding receptacle 3 | 480 | 60 | 76 | PCM: power control module | LV 600 V | 1 | 1
RICE engine-generator 3 | RICE-3 | I | 480 V welding receptacle 4 | 480 | 60 | 76 | PCM: power control module | LV 600 V | 1 | 1
RICE engine-generator 4 | RICE-4 | I | Motor 1 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 4 | RICE-4 | I | Motor 2 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 4 | RICE-4 | I | Motor 3 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 4 | RICE-4 | I | Motor 4 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 4 | RICE-4 | I | Motor 5 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 4 | RICE-4 | I | Motor 6 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 4 | RICE-4 | I | 480 V welding receptacle 1 | 480 | 60 | 76 | PCM: power control module | LV 600 V | 1 | 1
RICE engine-generator 4 | RICE-4 | I | 480 V welding receptacle 2 | 480 | 60 | 76 | PCM: power control module | LV 600 V | 1 | 1
RICE engine-generator 4 | RICE-4 | I | 480 V welding receptacle 3 | 480 | 60 | 76 | PCM: power control module | LV 600 V | 1 | 1
RICE engine-generator 4 | RICE-4 | I | 480 V welding receptacle 4 | 480 | 60 | 76 | PCM: power control module | LV 600 V | 1 | 1
RICE engine-generator 5 | RICE-5 | I | Motor 1 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 5 | RICE-5 | I | Motor 2 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 5 | RICE-5 | I | Motor 3 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 5 | RICE-5 | I | Motor 4 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 5 | RICE-5 | I | Motor 5 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 5 | RICE-5 | I | Motor 6 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 5 | RICE-5 | I | 480 V welding receptacle 1 | 480 | 60 | 76 | PCM: power control module | LV 600 V | 1 | 1
RICE engine-generator 5 | RICE-5 | I | 480 V welding receptacle 2 | 480 | 60 | 76 | PCM: power control module | LV 600 V | 1 | 1
RICE engine-generator 5 | RICE-5 | I | 480 V welding receptacle 3 | 480 | 60 | 76 | PCM: power control module | LV 600 V | 1 | 1
RICE engine-generator 5 | RICE-5 | I | 480 V welding receptacle 4 | 480 | 60 | 76 | PCM: power control module | LV 600 V | 1 | 1
RICE engine-generator 6 | RICE-6 | I | Motor 1 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 6 | RICE-6 | I | Motor 2 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 6 | RICE-6 | I | Motor 3 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 6 | RICE-6 | I | Motor 4 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 6 | RICE-6 | I | Motor 5 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 6 | RICE-6 | I | Motor 6 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 4 | 1
RICE engine-generator 6 | RICE-6 | I | 480 V welding receptacle 1 | 480 | 60 | 76 | PCM: power control module | LV 600 V | 1 | 1
RICE engine-generator 6 | RICE-6 | I | 480 V welding receptacle 2 | 480 | 60 | 76 | PCM: power control module | LV 600 V | 1 | 1
RICE engine-generator 6 | RICE-6 | I | 480 V welding receptacle 3 | 480 | 60 | 76 | PCM: power control module | LV 600 V | 1 | 1
RICE engine-generator 6 | RICE-6 | I | 480 V welding receptacle 4 | 480 | 60 | 76 | PCM: power control module | LV 600 V | 1 | 1
RICE engine-generator 7 | RICE-7 | I | Motor 1 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 8 | 1
RICE engine-generator 7 | RICE-7 | I | Motor 2 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 8 | 1
RICE engine-generator 7 | RICE-7 | I | Motor 3 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 8 | 1
RICE engine-generator 7 | RICE-7 | I | Motor 4 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 8 | 1
RICE engine-generator 7 | RICE-7 | I | Motor 5 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 8 | 1
RICE engine-generator 7 | RICE-7 | I | Motor 6 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 8 | 1
RICE engine-generator 7 | RICE-7 | I | 480 V welding receptacle 1 | 480 | 60 | 76 | PCM: power control module | LV 600 V | 2 | 1
RICE engine-generator 7 | RICE-7 | I | 480 V welding receptacle 2 | 480 | 60 | 76 | PCM: power control module | LV 600 V | 2 | 1
RICE engine-generator 7 | RICE-7 | I | 480 V welding receptacle 3 | 480 | 60 | 76 | PCM: power control module | LV 600 V | 2 | 1
RICE engine-generator 7 | RICE-7 | I | 480 V welding receptacle 4 | 480 | 60 | 76 | PCM: power control module | LV 600 V | 2 | 1
RICE engine-generator 8 | RICE-8 | I | Motor 1 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 8 | 1
RICE engine-generator 8 | RICE-8 | I | Motor 2 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 8 | 1
RICE engine-generator 8 | RICE-8 | I | Motor 3 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 8 | 1
RICE engine-generator 8 | RICE-8 | I | Motor 4 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 8 | 1
RICE engine-generator 8 | RICE-8 | I | Motor 5 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 8 | 1
RICE engine-generator 8 | RICE-8 | I | Motor 6 of 6, 22 kW | 480 | 22 | 31.1 | PCM: power control module | LV 600 V | 8 | 1
RICE engine-generator 8 | RICE-8 | I | 480 V welding receptacle 1 | 480 | 60 | 76 | PCM: power control module | LV 600 V | 2 | 1
RICE engine-generator 8 | RICE-8 | I | 480 V welding receptacle 2 | 480 | 60 | 76 | PCM: power control module | LV 600 V | 2 | 1
RICE engine-generator 8 | RICE-8 | I | 480 V welding receptacle 3 | 480 | 60 | 76 | PCM: power control module | LV 600 V | 2 | 1
RICE engine-generator 8 | RICE-8 | I | 480 V welding receptacle 4 | 480 | 60 | 76 | PCM: power control module | LV 600 V | 2 | 1
Reagent storage |  | I | LV power feeder | 480 | 15 | 21.2 | PCM: power control module | LV 600 V | 10 | 1
SC-1 SCR / CO catalyst |  | I | Motor 1 of 2, 30 kW | 480 | 30 | 42.5 | PCM: power control module | LV 600 V | 6 | 1
SC-1 SCR / CO catalyst |  | I | Motor 2 of 2, 30 kW | 480 | 30 | 42.5 | PCM: power control module | LV 600 V | 6 | 1
SC-1 lube-oil fin-fan cooler |  | I | Motor 1 of 4, 15 kW | 480 | 15 | 21.2 | PCM: power control module | LV 600 V | 10 | 1
SC-1 lube-oil fin-fan cooler |  | I | Motor 2 of 4, 15 kW | 480 | 15 | 21.2 | PCM: power control module | LV 600 V | 10 | 1
SC-1 lube-oil fin-fan cooler |  | I | Motor 3 of 4, 15 kW | 480 | 15 | 21.2 | PCM: power control module | LV 600 V | 10 | 1
SC-1 lube-oil fin-fan cooler |  | I | Motor 4 of 4, 15 kW | 480 | 15 | 21.2 | PCM: power control module | LV 600 V | 10 | 1
SC-1 stack (80 ft) |  | I | Area / platform lighting circuit 1 (4 fixtures) | 480 | 3 | 5 | PCM: power control module | LV 600 V | 2 | 1
SC-1: aeroderivative simple-cycle unit (LM6000 class) | SC-1 | I | Motor 1 of 10, 30 kW | 480 | 30 | 42.5 | PCM: power control module | LV 600 V | 6 | 1
SC-1: aeroderivative simple-cycle unit (LM6000 class) | SC-1 | I | Motor 2 of 10, 30 kW | 480 | 30 | 42.5 | PCM: power control module | LV 600 V | 6 | 1
SC-1: aeroderivative simple-cycle unit (LM6000 class) | SC-1 | I | Motor 3 of 10, 30 kW | 480 | 30 | 42.5 | PCM: power control module | LV 600 V | 6 | 1
SC-1: aeroderivative simple-cycle unit (LM6000 class) | SC-1 | I | Motor 4 of 10, 30 kW | 480 | 30 | 42.5 | PCM: power control module | LV 600 V | 6 | 1
SC-1: aeroderivative simple-cycle unit (LM6000 class) | SC-1 | I | Motor 5 of 10, 30 kW | 480 | 30 | 42.5 | PCM: power control module | LV 600 V | 6 | 1
SC-1: aeroderivative simple-cycle unit (LM6000 class) | SC-1 | I | Motor 6 of 10, 30 kW | 480 | 30 | 42.5 | PCM: power control module | LV 600 V | 6 | 1
SC-1: aeroderivative simple-cycle unit (LM6000 class) | SC-1 | I | Motor 7 of 10, 30 kW | 480 | 30 | 42.5 | PCM: power control module | LV 600 V | 6 | 1
SC-1: aeroderivative simple-cycle unit (LM6000 class) | SC-1 | I | Motor 8 of 10, 30 kW | 480 | 30 | 42.5 | PCM: power control module | LV 600 V | 6 | 1
SC-1: aeroderivative simple-cycle unit (LM6000 class) | SC-1 | I | Motor 9 of 10, 30 kW | 480 | 30 | 42.5 | PCM: power control module | LV 600 V | 6 | 1
SC-1: aeroderivative simple-cycle unit (LM6000 class) | SC-1 | I | Motor 10 of 10, 30 kW | 480 | 30 | 42.5 | PCM: power control module | LV 600 V | 6 | 1
SC-2 SCR / CO catalyst |  | I | Motor 1 of 2, 30 kW | 480 | 30 | 42.5 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 350 kcmil | 1
SC-2 SCR / CO catalyst |  | I | Motor 2 of 2, 30 kW | 480 | 30 | 42.5 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 350 kcmil | 1
SC-2 lube-oil fin-fan cooler |  | I | Motor 1 of 4, 15 kW | 480 | 15 | 21.2 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 3/0 | 1
SC-2 lube-oil fin-fan cooler |  | I | Motor 2 of 4, 15 kW | 480 | 15 | 21.2 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 3/0 | 1
SC-2 lube-oil fin-fan cooler |  | I | Motor 3 of 4, 15 kW | 480 | 15 | 21.2 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 3/0 | 1
SC-2 lube-oil fin-fan cooler |  | I | Motor 4 of 4, 15 kW | 480 | 15 | 21.2 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 3/0 | 1
SC-2 stack (80 ft) |  | I | Area / platform lighting circuit 1 (4 fixtures) | 480 | 3 | 5 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 4 | 1
SC-2: aeroderivative simple-cycle unit (LM6000 class) | SC-2 | I | Motor 1 of 10, 30 kW | 480 | 30 | 42.5 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 350 kcmil | 1
SC-2: aeroderivative simple-cycle unit (LM6000 class) | SC-2 | I | Motor 2 of 10, 30 kW | 480 | 30 | 42.5 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 350 kcmil | 1
SC-2: aeroderivative simple-cycle unit (LM6000 class) | SC-2 | I | Motor 3 of 10, 30 kW | 480 | 30 | 42.5 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 350 kcmil | 1
SC-2: aeroderivative simple-cycle unit (LM6000 class) | SC-2 | I | Motor 4 of 10, 30 kW | 480 | 30 | 42.5 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 350 kcmil | 1
SC-2: aeroderivative simple-cycle unit (LM6000 class) | SC-2 | I | Motor 5 of 10, 30 kW | 480 | 30 | 42.5 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 350 kcmil | 1
SC-2: aeroderivative simple-cycle unit (LM6000 class) | SC-2 | I | Motor 6 of 10, 30 kW | 480 | 30 | 42.5 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 350 kcmil | 1
SC-2: aeroderivative simple-cycle unit (LM6000 class) | SC-2 | I | Motor 7 of 10, 30 kW | 480 | 30 | 42.5 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 350 kcmil | 1
SC-2: aeroderivative simple-cycle unit (LM6000 class) | SC-2 | I | Motor 8 of 10, 30 kW | 480 | 30 | 42.5 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 350 kcmil | 1
SC-2: aeroderivative simple-cycle unit (LM6000 class) | SC-2 | I | Motor 9 of 10, 30 kW | 480 | 30 | 42.5 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 350 kcmil | 1
SC-2: aeroderivative simple-cycle unit (LM6000 class) | SC-2 | I | Motor 10 of 10, 30 kW | 480 | 30 | 42.5 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 350 kcmil | 1
T-MOD 230 kV take-off gantry with arresters |  | I | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 10 | 1
T-MOD 230 kV take-off gantry with arresters |  | I | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 10 | 1
T-MOD 230 kV take-off gantry with arresters |  | I | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 10 | 1
T-MOD 230 kV take-off gantry with arresters |  | I | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 10 | 1
T-MOD 230 kV take-off gantry with arresters |  | I | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 10 | 1
T-MOD 230 kV take-off gantry with arresters |  | I | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 10 | 1
T-MOD-1 / T-MOD-2 firewall |  | I | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 10 | 1
T-MOD-1 / T-MOD-2 firewall |  | I | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 10 | 1
T-MOD-1 / T-MOD-2 firewall |  | I | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 10 | 1
T-MOD-1 / T-MOD-2 firewall |  | I | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 10 | 1
T-MOD-1 / T-MOD-2 firewall |  | I | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 10 | 1
T-MOD-1 / T-MOD-2 firewall |  | I | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 10 | 1
T-MOD-1: 13.8/230 kV | T-MOD-1 | I | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 10 | 1
T-MOD-1: 13.8/230 kV | T-MOD-1 | I | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 10 | 1
T-MOD-1: 13.8/230 kV | T-MOD-1 | I | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 10 | 1
T-MOD-1: 13.8/230 kV | T-MOD-1 | I | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 10 | 1
T-MOD-1: 13.8/230 kV | T-MOD-1 | I | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 10 | 1
T-MOD-1: 13.8/230 kV | T-MOD-1 | I | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 10 | 1
T-MOD-2: 13.8/230 kV | T-MOD-2 | I | Motor 1 of 6, 2 kW | 480 | 2 | 2.8 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 10 | 1
T-MOD-2: 13.8/230 kV | T-MOD-2 | I | Motor 2 of 6, 2 kW | 480 | 2 | 2.8 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 10 | 1
T-MOD-2: 13.8/230 kV | T-MOD-2 | I | Motor 3 of 6, 2 kW | 480 | 2 | 2.8 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 10 | 1
T-MOD-2: 13.8/230 kV | T-MOD-2 | I | Motor 4 of 6, 2 kW | 480 | 2 | 2.8 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 10 | 1
T-MOD-2: 13.8/230 kV | T-MOD-2 | I | Motor 5 of 6, 2 kW | 480 | 2 | 2.8 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 10 | 1
T-MOD-2: 13.8/230 kV | T-MOD-2 | I | Motor 6 of 6, 2 kW | 480 | 2 | 2.8 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 10 | 1
TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | TM-1 | I | Motor 1 of 6, 22 kW | 480 | 22 | 31.1 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 4/0 | 1
TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | TM-1 | I | Motor 2 of 6, 22 kW | 480 | 22 | 31.1 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 4/0 | 1
TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | TM-1 | I | Motor 3 of 6, 22 kW | 480 | 22 | 31.1 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 4/0 | 1
TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | TM-1 | I | Motor 4 of 6, 22 kW | 480 | 22 | 31.1 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 4/0 | 1
TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | TM-1 | I | Motor 5 of 6, 22 kW | 480 | 22 | 31.1 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 4/0 | 1
TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | TM-1 | I | Motor 6 of 6, 22 kW | 480 | 22 | 31.1 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 4/0 | 1
TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | TM-2 | I | Motor 1 of 6, 22 kW | 480 | 22 | 31.1 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 4/0 | 1
TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | TM-2 | I | Motor 2 of 6, 22 kW | 480 | 22 | 31.1 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 4/0 | 1
TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | TM-2 | I | Motor 3 of 6, 22 kW | 480 | 22 | 31.1 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 4/0 | 1
TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | TM-2 | I | Motor 4 of 6, 22 kW | 480 | 22 | 31.1 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 4/0 | 1
TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | TM-2 | I | Motor 5 of 6, 22 kW | 480 | 22 | 31.1 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 4/0 | 1
TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 MW) | TM-2 | I | Motor 6 of 6, 22 kW | 480 | 22 | 31.1 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 4/0 | 1
Water-injection skid |  | I | LV power feeder | 480 | 15 | 21.2 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | LV 600 V | 3/0 | 1
Fuel-gas compressors 3 x 100% electric |  | I | Modular-yard fuel-gas compressor | 13800 | 1500 | 70 | MOD-EH: 13.8 kV modular collector e-house | MV 15 kV | 2 | 1
Fuel-gas compressors 3 x 100% electric |  | I | Modular-yard fuel-gas compressor | 13800 | 1500 | 70 | MOD-EH: 13.8 kV modular collector e-house | MV 15 kV | 2 | 1
Fuel-gas compressors 3 x 100% electric |  | I | Modular-yard fuel-gas compressor | 13800 | 1500 | 70 | MOD-EH: 13.8 kV modular collector e-house | MV 15 kV | 2 | 1
MOD-EH: 13.8 kV modular collector e-house | MOD-EH | I | SC-1 PCM to MOD-EH | 13800 | 50000 | 2092 | SC-1 PCM + 15 kV GCB | MV 15 kV | 750 kcmil | 5
MOD-EH: 13.8 kV modular collector e-house | MOD-EH | I | SC-2 PCM to MOD-EH | 13800 | 50000 | 2092 | SC-2 PCM + 15 kV GCB | MV 15 kV | 750 kcmil | 5
MOD-EH: 13.8 kV modular collector e-house | MOD-EH | I | MOD-LV step-up to MOD-EH | 13800 | 7500 | 314 | MOD-LV 480 V board + 480 V : 13.8 kV step-up | MV 15 kV | 500 kcmil | 1
PAD-EH 13.8 kV switchgear e-house | PAD-EH | I | CONT-3 13.8 kV to PAD-EH (extension section, ground tray) | 13800 | 2000 | 93 | CONT-3: containerized gas genset 13.8 kV (40 ft) | MV 15 kV | 2 | 1
PAD-EH 13.8 kV switchgear e-house | PAD-EH | I | CONT-4 13.8 kV to PAD-EH (extension section, ground tray) | 13800 | 2000 | 93 | CONT-4: containerized gas genset 13.8 kV (40 ft) | MV 15 kV | 2 | 1
PAD-EH 13.8 kV switchgear e-house | PAD-EH | I | CONT-5 13.8 kV to PAD-EH (extension section, ground tray) | 13800 | 2000 | 93 | CONT-5: containerized gas genset 13.8 kV (40 ft) | MV 15 kV | 2 | 1
PAD-EH 13.8 kV switchgear e-house | PAD-EH | I | CONT-6 13.8 kV to PAD-EH (extension section, ground tray) | 13800 | 2000 | 93 | CONT-6: containerized gas genset 13.8 kV (40 ft) | MV 15 kV | 2 | 1
PAD-EH 13.8 kV switchgear e-house | PAD-EH | I | CONT-7 13.8 kV to PAD-EH (extension section, ground tray) | 13800 | 2000 | 93 | CONT-7: containerized gas genset 13.8 kV (40 ft) | MV 15 kV | 2 | 1
PAD-EH 13.8 kV switchgear e-house | PAD-EH | I | CONT-8 13.8 kV to PAD-EH (extension section, ground tray) | 13800 | 2000 | 93 | CONT-8: containerized gas genset 13.8 kV (40 ft) | MV 15 kV | 2 | 1
PAD-EH 13.8 kV switchgear e-house | PAD-EH | I | TM-1 (TM2500) generator leads to PAD-EH | 13800 | 35000 | 1464 | TM-1: trailer-mounted aeroderivative GT (TM2500 class, ~35 M | MV 15 kV | 1000 kcmil | 3
PAD-EH 13.8 kV switchgear e-house | PAD-EH | I | TM-2 (TM2500) generator leads to PAD-EH | 13800 | 35000 | 1464 | TM-2: trailer-mounted aeroderivative GT (TM2500 class, ~35 M | MV 15 kV | 1000 kcmil | 3
PCM: power control module |  | I | RICE-1 generator leads to the PCM | 13800 | 18400 | 770 | RICE engine-generator 1 | MV 15 kV | 750 kcmil | 2
PCM: power control module |  | I | RICE-2 generator leads to the PCM | 13800 | 18400 | 770 | RICE engine-generator 2 | MV 15 kV | 750 kcmil | 2
PCM: power control module |  | I | RICE-3 generator leads to the PCM | 13800 | 18400 | 770 | RICE engine-generator 3 | MV 15 kV | 750 kcmil | 2
PCM: power control module |  | I | RICE-4 generator leads to the PCM | 13800 | 18400 | 770 | RICE engine-generator 4 | MV 15 kV | 750 kcmil | 2
PCM: power control module |  | I | RICE-5 generator leads to the PCM | 13800 | 18400 | 770 | RICE engine-generator 5 | MV 15 kV | 750 kcmil | 2
PCM: power control module |  | I | RICE-6 generator leads to the PCM | 13800 | 18400 | 770 | RICE engine-generator 6 | MV 15 kV | 750 kcmil | 2
PCM: power control module |  | I | RICE-7 generator leads to the PCM | 13800 | 18400 | 770 | RICE engine-generator 7 | MV 15 kV | 750 kcmil | 2
PCM: power control module |  | I | RICE-8 generator leads to the PCM | 13800 | 18400 | 770 | RICE engine-generator 8 | MV 15 kV | 750 kcmil | 2
SC-1 PCM + 15 kV GCB |  | I | SC-1 (LM6000 class) generator leads to its PCM / GCB | 13800 | 50000 | 2092 | SC-1: aeroderivative simple-cycle unit (LM6000 class) | MV 15 kV | 750 kcmil | 5
SC-2 PCM + 15 kV GCB |  | I | SC-2 (LM6000 class) generator leads to its PCM / GCB | 13800 | 50000 | 2092 | SC-2: aeroderivative simple-cycle unit (LM6000 class) | MV 15 kV | 750 kcmil | 5
PAD-LV 480 V paralleling switchboard | PAD-LV | I | GEN-E 480 V to PAD-LV (Type W sets, cam-lock) | 480 | 2000 | 2406 | GEN-E: enclosed industrial gas genset 2 MW | Portable LV | 4/0 | 8
PAD-LV 480 V paralleling switchboard | PAD-LV | I | GEN-O 480 V to PAD-LV (Type W sets, cam-lock) | 480 | 1000 | 1203 | GEN-O: open engine-generator skid | Portable LV | 4/0 | 4
GSP-1: generator breaker / protection | GSP-1 | I | CONT-1 13.8 kV leads to GSP-1 | 13800 | 2000 | 93 | CONT-1: containerized genset 13.8 kV (40 ft) | Portable MV | 2 | 1
GSP-2: generator breaker / protection | GSP-2 | I | CONT-2 13.8 kV leads to GSP-2 | 13800 | 2000 | 93 | CONT-2: containerized genset 13.8 kV (40 ft) | Portable MV | 2 | 1
LB: commissioning load bank (trailer) | LB | I | PIC to commissioning load bank | 13800 | 2000 | 93 | PIC: portable input cabinet | Portable MV | 2 | 1
PAD-EH 13.8 kV switchgear e-house | PAD-EH | I | GSP-1 to PAD-EH | 13800 | 2000 | 93 | GSP-1: generator breaker / protection | Portable MV | 2 | 1
PAD-EH 13.8 kV switchgear e-house | PAD-EH | I | GSP-2 to PAD-EH | 13800 | 2000 | 93 | GSP-2: generator breaker / protection | Portable MV | 2 | 1
PIC: portable input cabinet | PIC | I | MOB-1 13.8 kV to PIC through the C-L01 ramp | 13800 | 2000 | 93 | MOB-1: trailer genset | Portable MV | 2 | 1
CHW pumps |  | J | Motor 1 of 4, 150 kW | 480 | 150 | 212.3 | Inlet-chilling e-house / transformer | LV 600 V | 350 kcmil | 1
CHW pumps |  | J | Motor 2 of 4, 150 kW | 480 | 150 | 212.3 | Inlet-chilling e-house / transformer | LV 600 V | 350 kcmil | 1
CHW pumps |  | J | Motor 3 of 4, 150 kW | 480 | 150 | 212.3 | Inlet-chilling e-house / transformer | LV 600 V | 350 kcmil | 1
CHW pumps |  | J | Motor 4 of 4, 150 kW | 480 | 150 | 212.3 | Inlet-chilling e-house / transformer | LV 600 V | 350 kcmil | 1
CONDITIONAL: TES chilled-water tank |  | J | LV power feeder | 480 | 10 | 14.2 | Inlet-chilling e-house / transformer | LV 600 V | 8 | 1
Chillers x6 (water-cooled) |  | J | Motor 1 of 6, 7 kW | 480 | 7 | 9.9 | Inlet-chilling e-house / transformer | LV 600 V | 10 | 1
Chillers x6 (water-cooled) |  | J | Motor 2 of 6, 7 kW | 480 | 7 | 9.9 | Inlet-chilling e-house / transformer | LV 600 V | 10 | 1
Chillers x6 (water-cooled) |  | J | Motor 3 of 6, 7 kW | 480 | 7 | 9.9 | Inlet-chilling e-house / transformer | LV 600 V | 10 | 1
Chillers x6 (water-cooled) |  | J | Motor 4 of 6, 7 kW | 480 | 7 | 9.9 | Inlet-chilling e-house / transformer | LV 600 V | 10 | 1
Chillers x6 (water-cooled) |  | J | Motor 5 of 6, 7 kW | 480 | 7 | 9.9 | Inlet-chilling e-house / transformer | LV 600 V | 10 | 1
Chillers x6 (water-cooled) |  | J | Motor 6 of 6, 7 kW | 480 | 7 | 9.9 | Inlet-chilling e-house / transformer | LV 600 V | 10 | 1
Inlet-chilling tower (12 cells): chiller heat rejection |  | J | Motor 1 of 12, 75 kW (VFD output) | 480 | 75 | 106 | Inlet-chilling e-house / transformer | LV 600 V | 2/0 | 1
Inlet-chilling tower (12 cells): chiller heat rejection |  | J | Motor 2 of 12, 75 kW (VFD output) | 480 | 75 | 106 | Inlet-chilling e-house / transformer | LV 600 V | 2/0 | 1
Inlet-chilling tower (12 cells): chiller heat rejection |  | J | Motor 3 of 12, 75 kW (VFD output) | 480 | 75 | 106 | Inlet-chilling e-house / transformer | LV 600 V | 2/0 | 1
Inlet-chilling tower (12 cells): chiller heat rejection |  | J | Motor 4 of 12, 75 kW (VFD output) | 480 | 75 | 106 | Inlet-chilling e-house / transformer | LV 600 V | 2/0 | 1
Inlet-chilling tower (12 cells): chiller heat rejection |  | J | Motor 5 of 12, 75 kW (VFD output) | 480 | 75 | 106 | Inlet-chilling e-house / transformer | LV 600 V | 2/0 | 1
Inlet-chilling tower (12 cells): chiller heat rejection |  | J | Motor 6 of 12, 75 kW (VFD output) | 480 | 75 | 106 | Inlet-chilling e-house / transformer | LV 600 V | 2/0 | 1
Inlet-chilling tower (12 cells): chiller heat rejection |  | J | Motor 7 of 12, 75 kW (VFD output) | 480 | 75 | 106 | Inlet-chilling e-house / transformer | LV 600 V | 2/0 | 1
Inlet-chilling tower (12 cells): chiller heat rejection |  | J | Motor 8 of 12, 75 kW (VFD output) | 480 | 75 | 106 | Inlet-chilling e-house / transformer | LV 600 V | 2/0 | 1
Inlet-chilling tower (12 cells): chiller heat rejection |  | J | Motor 9 of 12, 75 kW (VFD output) | 480 | 75 | 106 | Inlet-chilling e-house / transformer | LV 600 V | 2/0 | 1
Inlet-chilling tower (12 cells): chiller heat rejection |  | J | Motor 10 of 12, 75 kW (VFD output) | 480 | 75 | 106 | Inlet-chilling e-house / transformer | LV 600 V | 2/0 | 1
Inlet-chilling tower (12 cells): chiller heat rejection |  | J | Motor 11 of 12, 75 kW (VFD output) | 480 | 75 | 106 | Inlet-chilling e-house / transformer | LV 600 V | 2/0 | 1
Inlet-chilling tower (12 cells): chiller heat rejection |  | J | Motor 12 of 12, 75 kW (VFD output) | 480 | 75 | 106 | Inlet-chilling e-house / transformer | LV 600 V | 2/0 | 1
Inlet-chilling tower (12 cells): chiller heat rejection |  | J | Area / platform lighting circuit 1 (12 fixtures) | 480 | 3 | 5 | Inlet-chilling e-house / transformer | LV 600 V | 10 | 1
Inlet-chilling e-house / transformer |  | J | Inlet-chilling e-house / transformer | 13800 | 12000 | 502 | R1 SWGR-13.8-1 (11 x 36 in cubicles, 15 kV metal-clad) | MV 15 kV | 1000 kcmil | 1
CW pumps (inlet chilling) |  | J | Inlet-chilling CW pump 1 | 4160 | 450 | 69 | Inlet-chilling e-house / transformer | MV 5 kV | 2 | 1
CW pumps (inlet chilling) |  | J | Inlet-chilling CW pump 2 | 4160 | 450 | 69 | Inlet-chilling e-house / transformer | MV 5 kV | 2 | 1
CW pumps (inlet chilling) |  | J | Inlet-chilling CW pump 3 | 4160 | 450 | 69 | Inlet-chilling e-house / transformer | MV 5 kV | 2 | 1
CW pumps (inlet chilling) |  | J | Inlet-chilling CW pump 4 | 4160 | 450 | 69 | Inlet-chilling e-house / transformer | MV 5 kV | 2 | 1
Chillers x6 (water-cooled) |  | J | Water-cooled chiller CH-1 | 4160 | 1500 | 231 | Inlet-chilling e-house / transformer | MV 5 kV | 250 kcmil | 1
Chillers x6 (water-cooled) |  | J | Water-cooled chiller CH-2 | 4160 | 1500 | 231 | Inlet-chilling e-house / transformer | MV 5 kV | 250 kcmil | 1
Chillers x6 (water-cooled) |  | J | Water-cooled chiller CH-3 | 4160 | 1500 | 231 | Inlet-chilling e-house / transformer | MV 5 kV | 250 kcmil | 1
Chillers x6 (water-cooled) |  | J | Water-cooled chiller CH-4 | 4160 | 1500 | 231 | Inlet-chilling e-house / transformer | MV 5 kV | 250 kcmil | 1
Chillers x6 (water-cooled) |  | J | Water-cooled chiller CH-5 | 4160 | 1500 | 231 | Inlet-chilling e-house / transformer | MV 5 kV | 250 kcmil | 1
Chillers x6 (water-cooled) |  | J | Water-cooled chiller CH-6 | 4160 | 1500 | 231 | Inlet-chilling e-house / transformer | MV 5 kV | 250 kcmil | 1
H2 19: T-H2 230/13.8 kV (about 40 MVA) | T-H2 | K | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | H2 20: 13.8 kV e-house | LV 600 V | 10 | 1
H2 20: 13.8 kV e-house |  | K | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | H2 20: 13.8 kV e-house | LV 600 V | 10 | 1
H2 21: rectifier transformer 1 (7 MVA) |  | K | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | H2 20: 13.8 kV e-house | LV 600 V | 8 | 1
H2 21: rectifier transformer 2 (7 MVA) |  | K | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | H2 20: 13.8 kV e-house | LV 600 V | 8 | 1
H2 21: rectifier transformer 3 (7 MVA) |  | K | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | H2 20: 13.8 kV e-house | LV 600 V | 8 | 1
H2 21: rectifier transformer 4 (7 MVA) |  | K | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | H2 20: 13.8 kV e-house | LV 600 V | 8 | 1
H2 21: rectifier transformer 5 (7 MVA) |  | K | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | H2 20: 13.8 kV e-house | LV 600 V | 10 | 1
H2 22: electrolyzer building (5 x HyLYZER-1000 + 5 rectifiers) | H2-EL | K | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | H2 20: 13.8 kV e-house | LV 600 V | 8 | 1
H2 23: dry coolers |  | K | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | H2 20: 13.8 kV e-house | LV 600 V | 10 | 1
H2 24: water purification (RO / EDI) |  | K | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | H2 20: 13.8 kV e-house | LV 600 V | 10 | 1
H2 25: H2 dryer / purification |  | K | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | H2 20: 13.8 kV e-house | LV 600 V | 10 | 1
H2 26: H2 compressor 1 (40 ft ISO) |  | K | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | H2 20: 13.8 kV e-house | LV 600 V | 10 | 1
H2 26: H2 compressor 2 (40 ft ISO) |  | K | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | H2 20: 13.8 kV e-house | LV 600 V | 10 | 1
H2 27: storage tube bank (~40 ft tubes) |  | K | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | H2 20: 13.8 kV e-house | LV 600 V | 10 | 1
H2 27: storage tube bank (~40 ft tubes) |  | K | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | H2 20: 13.8 kV e-house | LV 600 V | 10 | 1
H2 27: storage tube bank (~40 ft tubes) |  | K | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | H2 20: 13.8 kV e-house | LV 600 V | 10 | 1
H2 27: storage tube bank (~40 ft tubes) |  | K | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | H2 20: 13.8 kV e-house | LV 600 V | 10 | 1
H2 28: N2 purge supply |  | K | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | H2 20: 13.8 kV e-house | LV 600 V | 10 | 1
H2 29: vent stack |  | K | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | H2 20: 13.8 kV e-house | LV 600 V | 10 | 1
H2 30: H2 / gas blending station (plant gas yard) |  | K | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | LNG 17: LNG e-house (13.8 kV / 480 V) | LV 600 V | 4 | 1
H2 pipe track and cable trench, hall -> dryer / compressors (N2, instr |  | K | Motor 1 of 2, 250 kW | 480 | 250 | 353.8 | H2 20: 13.8 kV e-house | LV 600 V | 4/0 | 2
H2 pipe track and cable trench, hall -> dryer / compressors (N2, instr |  | K | Motor 2 of 2, 250 kW | 480 | 250 | 353.8 | H2 20: 13.8 kV e-house | LV 600 V | 4/0 | 2
H2 storage tube banks x4 | H2-ST | K | LV power feeder | 480 | 15 | 21.2 | H2 20: 13.8 kV e-house | LV 600 V | 10 | 1
H2R: hydrogen pipeline receiving station (pig receiver, filters, meter | H2R | K | LV power feeder | 480 | 15 | 21.2 | H2 20: 13.8 kV e-house | LV 600 V | 10 | 1
LNG 10: truck unloading bay 1 |  | K | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | LNG 17: LNG e-house (13.8 kV / 480 V) | LV 600 V | 8 | 1
LNG 10: truck unloading bay 2 |  | K | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | LNG 17: LNG e-house (13.8 kV / 480 V) | LV 600 V | 10 | 1
LNG 10: unloading skid |  | K | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | LNG 17: LNG e-house (13.8 kV / 480 V) | LV 600 V | 10 | 1
LNG 11: tank 1, Chart HS 50000 (51,780 gal) | LNG-T1 | K | LV power feeder | 480 | 10 | 14.2 | LNG 17: LNG e-house (13.8 kV / 480 V) | LV 600 V | 10 | 1
LNG 11: tank 2, Chart HS 50000 (51,780 gal) | LNG-T2 | K | LV power feeder | 480 | 10 | 14.2 | LNG 17: LNG e-house (13.8 kV / 480 V) | LV 600 V | 10 | 1
LNG 11: tank 3, Chart HS 50000 (51,780 gal) | LNG-T3 | K | LV power feeder | 480 | 10 | 14.2 | LNG 17: LNG e-house (13.8 kV / 480 V) | LV 600 V | 10 | 1
LNG 11: tank 4, Chart HS 50000 (51,780 gal) | LNG-T4 | K | LV power feeder | 480 | 10 | 14.2 | LNG 17: LNG e-house (13.8 kV / 480 V) | LV 600 V | 10 | 1
LNG 11: tank 5, Chart HS 50000 (51,780 gal) | LNG-T5 | K | LV power feeder | 480 | 10 | 14.2 | LNG 17: LNG e-house (13.8 kV / 480 V) | LV 600 V | 10 | 1
LNG 11: tank 6, Chart HS 50000 (51,780 gal) | LNG-T6 | K | LV power feeder | 480 | 10 | 14.2 | LNG 17: LNG e-house (13.8 kV / 480 V) | LV 600 V | 10 | 1
LNG 11: tank 7, Chart HS 50000 (51,780 gal) | LNG-T7 | K | LV power feeder | 480 | 10 | 14.2 | LNG 17: LNG e-house (13.8 kV / 480 V) | LV 600 V | 10 | 1
LNG 11: tank 8, Chart HS 50000 (51,780 gal) | LNG-T8 | K | LV power feeder | 480 | 10 | 14.2 | LNG 17: LNG e-house (13.8 kV / 480 V) | LV 600 V | 10 | 1
LNG 12: spill impoundment (NFPA 59A, to verify) |  | K | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | LNG 17: LNG e-house (13.8 kV / 480 V) | LV 600 V | 10 | 1
LNG 13: send-out pumps 2 x 100% |  | K | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | LNG 17: LNG e-house (13.8 kV / 480 V) | LV 600 V | 10 | 1
LNG 14: vaporizers + glycol heater |  | K | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | LNG 17: LNG e-house (13.8 kV / 480 V) | LV 600 V | 10 | 1
LNG 15: boil-off gas compressor |  | K | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | LNG 17: LNG e-house (13.8 kV / 480 V) | LV 600 V | 10 | 1
LNG 16: send-out metering + pressure control |  | K | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | LNG 17: LNG e-house (13.8 kV / 480 V) | LV 600 V | 10 | 1
LNG 17: LNG e-house (13.8 kV / 480 V) |  | K | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | LNG 17: LNG e-house (13.8 kV / 480 V) | LV 600 V | 10 | 1
LNG 18: vent stack |  | K | Motor 1 of 1, 15 kW | 480 | 15 | 21.2 | LNG 17: LNG e-house (13.8 kV / 480 V) | LV 600 V | 10 | 1
LNG impoundment sump pump |  | K | LV power feeder | 480 | 15 | 21.2 | LNG 17: LNG e-house (13.8 kV / 480 V) | LV 600 V | 8 | 1
M&R 2: insulating joint + ESD valve |  | K | LV power feeder | 480 | 10 | 14.2 | LNG 17: LNG e-house (13.8 kV / 480 V) | LV 600 V | 6 | 1
M&R 3: horizontal filter-separator |  | K | LV power feeder | 480 | 15 | 21.2 | LNG 17: LNG e-house (13.8 kV / 480 V) | LV 600 V | 4 | 1
M&R 4: line heater 1 (water bath) |  | K | LV power feeder | 480 | 15 | 21.2 | LNG 17: LNG e-house (13.8 kV / 480 V) | LV 600 V | 6 | 1
M&R 4: line heater 2 (water bath) |  | K | LV power feeder | 480 | 15 | 21.2 | LNG 17: LNG e-house (13.8 kV / 480 V) | LV 600 V | 6 | 1
M&R 4: line heater 3 (water bath) |  | K | LV power feeder | 480 | 15 | 21.2 | LNG 17: LNG e-house (13.8 kV / 480 V) | LV 600 V | 6 | 1
M&R 6: regulation / flow control building |  | K | LV panel / distribution feeder | 480 | 10 | 14.2 | LNG 17: LNG e-house (13.8 kV / 480 V) | LV 600 V | 8 | 1
M&R 7: gas quality + measurement building |  | K | LV panel / distribution feeder | 480 | 30 | 42.5 | LNG 17: LNG e-house (13.8 kV / 480 V) | LV 600 V | 2 | 1
M&R 8: condensate tank |  | K | LV power feeder | 480 | 10 | 14.2 | LNG 17: LNG e-house (13.8 kV / 480 V) | LV 600 V | 8 | 1
M&R 9: service panel + UPS, SCADA RTU, CP |  | K | LV power feeder | 480 | 15 | 21.2 | LNG 17: LNG e-house (13.8 kV / 480 V) | LV 600 V | 6 | 1
M&R CP test station (as drawn) |  | K | LV power feeder | 480 | 15 | 21.2 | LNG 17: LNG e-house (13.8 kV / 480 V) | LV 600 V | 6 | 1
M&R SCADA antenna mast base (as drawn) |  | K | LV power feeder | 480 | 15 | 21.2 | LNG 17: LNG e-house (13.8 kV / 480 V) | LV 600 V | 8 | 1
H2 20: 13.8 kV e-house |  | K | H2 13.8 kV e-house (electrolyzers) | 13800 | 20000 | 837 | R1 SWGR-13.8-3 (11 x 36 in cubicles, 15 kV metal-clad) | MV 15 kV | 750 kcmil | 2
LNG 17: LNG e-house (13.8 kV / 480 V) |  | K | LNG e-house | 13800 | 5000 | 209 | R1 SWGR-13.8-3 (11 x 36 in cubicles, 15 kV metal-clad) | MV 15 kV | 4/0 | 1
Small-bore piping: instrument air, service water, nitrogen, HRSG drain |  |  | Motor 1 of 2, 250 kW | 480 | 250 | 353.8 | R1 MCC-C1 | LV 600 V | 250 kcmil | 2
Small-bore piping: instrument air, service water, nitrogen, HRSG drain |  |  | Motor 2 of 2, 250 kW | 480 | 250 | 353.8 | R1 MCC-C1 | LV 600 V | 250 kcmil | 2