# Section 26 05 13 - Power Plant Wire and Cable (Combined Cycle) - Guide Specification

Oct 19, 2026 · Stephan

Guide specification for wire and cable in a gas-fired combined cycle power plant (1x1, 2x1 or 3x1), written to US practice (NEC, ICEA, IEEE, UL). Text in [brackets] is an option or value for the project editor to confirm.

## Part 1 - General

### 1.1 Summary

- This section covers furnishing, installing, terminating and testing all field wire and cable for the plant, from the generator terminals to the switchyard and from the auxiliary switchgear to every load.

- Included: 15 kV power cable, 600 V power and VFD cable, DC and UPS cable, control, instrument, fiber optic and grounding conductors, connectors, terminations and identification.

- Not included: isolated phase and nonsegregated phase bus, 600 V busway, and overhead switchyard and line conductors (specified in their own sections); cable supplied inside OEM packages, except where it connects to field cable.

### 1.2 References

Use the edition current at contract award unless noted.

| Body | Documents |
| --- | --- |
| NFPA | NFPA 70 (NEC) [2023]: Articles 110, 250, 310, 311, 330, 336, 392, 430, 445, 500-504, 725, 727, 770; Chapter 9 Tables 8 and 9 |
| ICEA / NEMA | S-93-639 (WC74) 5-46 kV shielded power cable; S-95-658 (WC70) 600 V power cable; S-73-532 (WC57) control, thermocouple extension and instrumentation cable; P-32-382 short-circuit characteristics |
| UL | 44, 1072, 1277, 1569, 1685, 2225, 2250, 1424, 486A-486B, 467 |
| IEEE | 422, 1185, 525, 835, 1202, 400, 400.2, 404, 80, 81 |
| NETA | ATS, Acceptance Testing Specifications |
| Owner | [Owner electrical design criteria]; [Transmission owner interconnection standards]; [Site hazardous area classification drawings] |

### 1.3 Definitions

- MV: medium voltage, 2.4-34.5 kV; here 13.8 kV systems on 15 kV cable.

- LV: 600 V class and below.

- MC-HL: Type MC cable listed for hazardous locations, continuous corrugated welded armor with overall jacket.

- TC-ER: tray cable listed for exposed runs.

- PLTC / ITC-HL: power-limited tray cable / instrumentation tray cable for hazardous locations.

- CI: circuit integrity (fire-rated) cable.

- IS: intrinsically safe circuit.

### 1.4 System description

| System | Nominal voltage | Grounding | Cable class |
| --- | --- | --- | --- |
| Generator | [18-24] kV | High-resistance via NGR | Phase bus (not this section); neutral cable 15 kV |
| Auxiliary MV | [13.8] kV [and 4.16 kV], 3-ph, 60 Hz | [Low-resistance, 400 A] | 15 kV MV-105, 133% |
| Auxiliary LV | 480 V, 3-ph, 3-wire | [High-resistance] | 600 V |
| DC | 125 V DC | Ungrounded | 600 V |
| UPS / instrument AC | 120/208 V | Solidly grounded | 600 V |
| Instrument | 24 V DC, 4-20 mA, thermocouple | Single-point shield ground | 300 V |

### 1.5 Submittals

- Manufacturer data sheets for each cable type: construction, OD, mass, ampacity basis, short-circuit rating, minimum bend radius, maximum pulling tension and sidewall pressure.

- Cable schedule: cable number, from/to equipment, type, size, conductors, runs, raceway route, length, design current, ampacity, voltage drop, short-circuit check, connector at each end.

- Pulling calculations for every MV cable and every LV pull longer than [150 ft] or with more than [270°] of bends.

- Certified factory test reports for each reel.

- Field test reports and as-built cable schedule.

### 1.6 Quality assurance

- Manufacturer: at least [10] years producing the cable types offered, ISO 9001 certified.

- All cable of one type from one manufacturer.

- Field testing by a NETA-accredited agency.

- Terminators of 15 kV cable certified by the termination-kit manufacturer.

### 1.7 Delivery, storage and handling

- Ship on reels with sealed ends, reel number, type, size and length marked.

- Store reels on hard ground, ends sealed, protected from sunlight and damage.

- Do not install below the manufacturer's minimum installation temperature [-10 °C / 14 °F for PVC jackets] without warming.

## Part 2 - Products

### 2.1 General requirements (all cable)

- Conductors: annealed copper, Class B compressed or Class C stranded; tinned where noted. No aluminum conductors.

- Listed and marked for the installation: tray-rated (-TC or -ER), sunlight resistant, rated for direct burial where installed in duct banks.

- Flame test: IEEE 1202 / UL 1685 FT4.

- Construction policy: [Type MC-HL with continuous corrugated welded aluminum armor (CCW) and PVC jacket throughout] OR [TC-ER in tray; MC-HL in hazardous areas, exposed drops and where mechanical protection is needed].

- Jacket: [PVC] OR [low-smoke zero-halogen in enclosed buildings and control rooms].

- Minimum temperature rating: 90 °C wet and dry; 130 °C emergency; 250 °C short circuit (600 V XLPE). MV-105: 105 °C normal.

### 2.2 15 kV medium-voltage power cable

| Item | Requirement |
| --- | --- |
| Standard | ICEA S-93-639, UL 1072, Type MV-105 |
| Conductor | Copper, Class B compressed; #2 AWG minimum |
| Insulation | EPR, 133% insulation level, 220 mil nominal |
| Shields | Extruded semiconducting conductor and insulation shields; copper tape shield, 12.5% overlap |
| Configuration | [3/C with ground] for feeders up to [750 kcmil]; [1/C triplexed] above |
| Armor and jacket | [CCW aluminum armor, MC-HL] + PVC jacket, red for MV identification |
| Hazardous locations | Listed Class I Div 1 & 2 where routed through classified areas |
| Short circuit | Conductor and shield sized for the available fault current and clearing time per ICEA P-32-382 |

### 2.3 600 V power cable

| Item | Requirement |
| --- | --- |
| Standard | ICEA S-95-658, UL 44 / UL 1569 (MC) or UL 1277 (TC) |
| Conductor | Copper; #12 AWG minimum for power |
| Insulation | XLPE, Type XHHW-2, 90 °C wet and dry |
| Configuration | 3/C + insulated or bare ground for 3-phase; 2/C + ground for single-phase and DC |
| Armor and jacket | Per 2.1 item 4 |
| Parallel runs | 1/0 AWG minimum, equal length, same type (NEC 310.10(G)) |

### 2.4 VFD cable

- Motor (output) side of every variable frequency drive.

- Construction: 3/C copper, XLPE (XHHW-2), three symmetrical ground conductors, overall shield (copper tape or foil plus braid), [1000] V rated.

- Fixed runs in tray: armored, Type MC-HL [Armor-X VFD type].

- Final drops to vibrating motors (ACC fans, cooling tower fans): flexible tinned copper, Type TC-ER, NFPA 79 [Machine Flex type]. Not permitted in Class I Div 1.

- MV drives: 15 kV shielded cable per 2.2, rated for the drive's dv/dt and common-mode voltage as confirmed by the drive manufacturer.

- Cable length from drive to motor within the drive manufacturer's limit, or provide output filters.

### 2.5 DC and UPS cable

- 600 V XHHW-2 copper, 2/C + ground, or 1/C pairs for large DC feeders; armor per 2.1 item 4.

- Emergency lube oil pumps, emergency lighting and other circuits that must run during a fire: circuit integrity cable, [2-hour] rated (UL 2196), or protected routing.

### 2.6 Control cable

| Item | Requirement |
| --- | --- |
| Standard | ICEA S-73-532 / S-95-658, UL 1277 or UL 1569 |
| Insulation | XLPE, XHHW-2, 600 V |
| Conductor size | #14 AWG minimum; #12 AWG for 120 V AC power to panels; #10 AWG for CT secondaries |
| Conductor count | Standard counts [2, 3, 4, 7, 12, 19, 25, 37]; [20%] spare conductors, minimum 2 |
| Color code | ICEA Method 1, Table E-2 (or printed numbers) |

### 2.7 Instrument and thermocouple cable

| Item | Requirement |
| --- | --- |
| Standard | ICEA S-73-532; NEC 725 (PLTC) / 727 (ITC) |
| Construction | Twisted pairs or triads, #16 AWG single pair, #18 AWG multi-pair; individual and overall aluminum-polyester shields with drain wire |
| Rating | 300 V [600 V where run with power-limited 120 V circuits] |
| Armor | [CCW armor, PLTC-ER / ITC-HL] |
| Thermocouple | Extension grade matching the element (Type KX for K, JX for J), ANSI color code |
| Intrinsically safe circuits | Light blue jacket, separate from non-IS circuits (NEC 504.30) |
| Fieldbus / serial | Cable to the protocol's specification (RS-485 120 Ω, Foundation Fieldbus Type A) |
| Spares | [20%] spare pairs on multi-pair cable |

### 2.8 Fiber optic cable

- Single-mode OS2, [24 / 48] fibers, loose tube, gel-free.

- Armored [interlocked aluminum] OFCR or OFNR; OPGW on transmission line and switchyard shield wire where specified.

- Pre-terminated or fusion-spliced; [25%] spare fibers.

### 2.9 Grounding conductors

- Ground grid: bare soft-drawn stranded copper, [4/0 AWG] minimum or as the IEEE 80 study requires.

- Equipment bonding jumpers: copper, [2/0 AWG] minimum for major equipment; green insulated where exposed.

- Connections below grade: exothermic weld or compression listed to IEEE 837.

### 2.10 Connectors, terminations and splices

- MC and MC-HL connectors: listed for the cable OD and armor type; watertight; [stainless or aluminum].

- Hazardous locations: connectors listed to UL 2225 for the Class and Division; seals per NEC 501.15 in Division 1.

- VFD cable: EMC connectors with 360° shield termination at both ends.

- 15 kV terminations: IEEE 48 Class 1, cold-shrink or heat-shrink kits, [outdoor / indoor]; shield grounding per manufacturer.

- 15 kV splices: avoid; where unavoidable, IEEE 404 rated and recorded on the as-built schedule.

- Lugs: compression, tin-plated copper, two-hole for 1/0 AWG and larger.

### 2.11 Identification

- Cable tag at both ends and at every pull point and tray entry: cable number per the cable schedule, on [stainless steel / UV-stable] tags.

- Conductor markers on every conductor at terminations: terminal number per wiring diagram.

- MV cable: phase identification tape and "DANGER - 13.8 kV" markers at accessible locations.

## Part 3 - Execution

### 3.1 Cable sizing criteria

Every power cable shall meet all four checks below; the cable schedule shows each result.

| Check | Criterion |
| --- | --- |
| Ampacity | Design current ≤ allowable ampacity. Design current = 125% of motor full-load or continuous load (NEC 430.22, 215.2); 115% of generator rating (NEC 445.13); 100% of transformer secondary. Allowable = NEC 310.16 75 °C column (600 V) or NEC 311.60 (15 kV), corrected for [40 °C] ambient and installation (NEC 392.80 for tray; IEEE 835 / Neher-McGrath, RHO [90], for duct banks). |
| Voltage drop | ≤ [3%] feeder and ≤ [5%] feeder plus branch at full load; motor terminal voltage ≥ [80%] during starting. NEC Chapter 9 Table 9 impedances at the load power factor. |
| Short circuit | Conductor and shield withstand the maximum available fault for the protective device clearing time (ICEA P-32-382). Governs most 13.8 kV feeders on multi-GT plants. |
| Minimum size | 15 kV: #2 AWG. 600 V power: #12 AWG. Control: #14 AWG. CT circuits: #10 AWG. |

### 3.2 Raceway and segregation

- Cable tray: ladder type; fill per NEC 392.22 (cables 4/0 AWG and larger in a single layer); [25%] spare capacity at turnover.

- Separate trays or tray tiers by level, top to bottom: 15 kV; 600 V power; control; instrument. Instrument tray at least [12 in] from 600 V power tray, or a solid barrier.

- Duct banks: concrete-encased, [red-dyed]; [25%] spare ducts; ampacity per IEEE 835.

- Unit separation: each generating unit (each GT/HRSG, ST) on its own tray routes where practical, so a cable fire affects one unit only. Redundant trains (A/B pumps, redundant controllers, fiber pairs) on separate routes (IEEE 422).

- Switchyard control cable in trench or duct to the relay building per IEEE 525 and transmission owner standards.

### 3.3 Installation

- Follow IEEE 1185 and the manufacturer's limits for pulling tension, sidewall pressure and minimum bending radius. Use a dynamometer on all MV pulls and record the maximum tension.

- Use pulling lubricant compatible with the jacket. Pull from reels with the cable entering the raceway without twisting.

- Secure cable in vertical tray and at changes of direction; support armored cable per NEC 330.30.

- Train cables neatly; maintain bend radius at terminations. Single-conductor MV in triplexed or trefoil groups with all phases in the same raceway.

- Seal cable ends until terminated. Fire-stop all wall and floor penetrations with a listed system.

### 3.4 Hazardous locations

- Install per NEC 501 and the site hazardous area classification drawings.

- Class I Division 1 (LNG pump and tank-top penetrations, gas metering where classified Div 1): MC-HL or ITC-HL with UL 2225 Division 1 connectors; seals within 18 in of enclosures per NEC 501.15.

- Class I Division 2 (gas metering skids, fuel gas heaters and compressors, GT enclosures, BOG compressors): MC-HL, ITC-HL, TC-ER or PLTC with listed Division 2 fittings.

- Intrinsically safe circuits: separate raceway or 2 in separation, light blue, per the control drawing.

### 3.5 Terminations

- Terminate per manufacturer instructions with calibrated tools; torque to the equipment rating and mark.

- Ground MV cable shields at [both ends] (single-point grounding only where approved for long single-conductor runs).

- Ground instrument shields at the [control system] end only; insulate the field end.

- Ground VFD cable shields and symmetrical grounds at both ends.

### 3.6 Field testing

Test every cable after installation and before energizing, per NETA ATS. Values in brackets are typical; confirm against NETA ATS and the cable manufacturer.

| Cable | Test | Acceptance |
| --- | --- | --- |
| All | Visual and mechanical: damage, bend radius, tags, connector tightness | No defects |
| 600 V power, control, DC | Insulation resistance, [1,000 V DC], 1 min, conductor to conductor and to ground | ≥ [100 MΩ], or per NETA ATS Table 100.1 |
| 600 V power, control | Continuity and point-to-point against wiring diagrams | 100% correct |
| 15 kV | Insulation resistance, [5,000 V DC], before and after withstand | Per NETA ATS; no decrease after withstand |
| 15 kV | Shield continuity | Continuous end to end |
| 15 kV, splices, terminations | VLF withstand, 0.1 Hz sinusoidal, IEEE 400.2 acceptance level [21 kV rms for 15 kV cable], [60 min] | No breakdown |
| 15 kV | VLF tan δ (IEEE 400.2) | Within IEEE 400.2 acceptance criteria for EPR; record baseline |
| VFD | Insulation resistance, continuity of symmetrical grounds and shield | As 600 V |
| Instrument | Loop check from field device to control system; shield isolation from ground at field end | 100% correct |
| Fiber | OTDR both directions and end-to-end insertion loss | Within the link loss budget |
| Grounding | Fall-of-potential grid resistance (IEEE 81); continuity of equipment bonds | ≤ [1 Ω] grid resistance or per the IEEE 80 study |

Do not use DC hi-pot on aged or service-aged 15 kV cable.

### 3.7 Records

- Maintain the cable schedule as the master record. For each cable, record reel number, date pulled, maximum pull tension (MV), date terminated at each end and test results.

- Hand over: as-built cable schedule (native spreadsheet), test reports, pulling records, termination records and manufacturer data sheets.

- A cable is complete when pulled, terminated at both ends, tested and accepted. Report status weekly by system.

## Appendix A - Cable type schedule

Every field cable in the plant shall be one of the types below. The cable schedule references these codes; add a type only by revising this appendix. Code format: class-conductors-size; suffix -A = armored (CCW, MC-HL / ITC-HL), -T = unarmored tray cable (TC-ER / PLTC-ER), applied per 2.1 item 4.

### A.1 15 kV medium-voltage power (2.2)

Common construction: Cu Class B compressed; EPR 220 mil, 133%; semiconducting shields; Cu tape shield; overall PVC jacket (red); MV-105, UL 1072, ICEA S-93-639; armored versions MC-HL listed Class I Div 1 & 2.

| Code | Conductors | Sizes (AWG / kcmil) | Typical use |
| --- | --- | --- | --- |
| MV15-1C-[size]-A | 1/C | #2 | Generator neutral to NGR |
| MV15-3C-[size]-A | 3/C + GC | #2, 1/0, 2/0, 4/0, 250, 350, 500, 750 | Motor and transformer feeders (#2 min: pumps, fans; 4/0 BFPs; 500-750 large fans, compressors, ties) |
| MV15-1C-[size]-TPX-A | 3 × 1/C triplexed | 500, 750, 1000 | Feeders above 3/C range: switchgear incomers, RICE / CCS bus ties where busduct is not used |
| MV15-3C-[size]-VFD-A | 3/C + 3 symmetrical G | 2/0 - 750 | MV drive output (e.g. CO₂ compressor), subject to drive maker's dv/dt rating |

### A.2 600 V power (2.3)

Common construction: Cu Class B; XLPE XHHW-2, 90 °C wet/dry; 3/C + insulated green ground (sized per NEC 250.122) unless noted; PVC jacket (black); UL 1569 MC-HL (-A) or UL 1277 TC-ER (-T); FT4.

| Code | Conductors | Sizes (AWG / kcmil) | Typical use |
| --- | --- | --- | --- |
| LV-3C-[size]-A/T | 3/C + G | #12, #10, #8, #6, #4, #2, 1/0, 2/0, 4/0, 250, 350, 500 | 480 V motor, heater, MCC and panel feeders |
| LV-4C-[size]-A/T | 4/C + G | #12 - 4/0 | 208Y/120 V and 480Y/277 V 4-wire feeders (lighting, small power panels) |
| LV-1C-[size]-A | 1/C | 250 - 750 | Large parallel 480 V feeders where 3/C cannot be used |
| LV-VFD-[size]-A | 3/C + 3 symmetrical G, overall shield | #12 - 500 | 480 V VFD output, fixed tray runs (Armor-X VFD type) |
| LV-MFX-[size]-T | 3/C + 3 symmetrical G, flexible tinned Cu, foil + braid shield, TPE jacket, 1000 V, TC-ER, NFPA 79 | #14 - [2/0, confirm range] | Final drop to vibrating VFD motors (ACC and cooling-tower fans); not Class I Div 1 (Machine Flex type) |

### A.3 DC and UPS power (2.5)

| Code | Construction | Sizes | Typical use |
| --- | --- | --- | --- |
| DC-2C-[size]-A | 2/C + G, XHHW-2, 600 V | #12 - 4/0 | 125 V DC distribution, trip and close supplies; 120/208 V UPS feeders |
| DC-1C-[size]-A | 1/C pairs, XHHW-2, 600 V | 250 - 500 | Battery to DC switchboard; large DC motors (emergency lube oil pumps) |
| CI-2C-[size] | 2/C + G, circuit integrity, UL 2196 [2-hour] | #12 - 4/0 | Emergency lube oil pumps, emergency lighting, fire & gas power where routed through fire zones |

### A.4 Control (2.6)

Common construction: Cu Class B (Class C / tinned optional); XLPE XHHW-2, 600 V; ICEA Method 1 color code; PVC jacket (black); -A or -T; FT4.

| Code | Conductors | Size | Typical use |
| --- | --- | --- | --- |
| CTL-[n]C-14-A/T | 2, 3, 4, 7, 12, 19, 25, 37 | #14 | General control, interlocks, status and alarm wiring |
| CTL-[n]C-12-A/T | 2, 3, 4, 7, 12 | #12 | 120 V AC control power, space heaters, solenoids, MOV controls |
| CTL-[n]C-10-A/T | 4, 7, 12 | #10 | CT secondaries, VT circuits, long DC trip circuits |
| CTL-[n]C-14-S-A | 4, 7, 12 | #14, overall shield | Control near VFDs or in high-noise areas (synchronizing, speed signals) |

### A.5 Instrument and thermocouple (2.7)

Common construction: Cu Class B; PE or FR-PVC insulation; twisted, individually and overall shielded (Al-polyester + drain); 300 V [600 V option]; PLTC-ER / ITC-ER (-T) or ITC-HL armored (-A); black jacket, light blue for IS.

| Code | Pairs / triads | Size | Typical use |
| --- | --- | --- | --- |
| INS-1P-16-A/T | 1 pair | #16 | Single 4-20 mA / HART field device home run |
| INS-1T-16-A/T | 1 triad | #16 | RTDs (3-wire), 3-wire transmitters |
| INS-[n]P-18-A/T | 4, 8, 12, 24, 36 pairs | #18 | Junction box to control system multi-pair |
| INS-[n]T-18-A/T | 4, 8, 12 triads | #18 | Multi-RTD runs (bearing, winding temperatures) |
| INS-IS-[n]P-[size] | As above | #16 / #18 | Intrinsically safe circuits, light blue jacket |
| TC-KX-[n]P-16-A/T | 1, 4, 8, 12 pairs | #16 | Type K thermocouples (GT exhaust, HRSG tubes, bearings); ANSI color code |
| TC-JX-[n]P-16-A/T | 1, 4, 8 pairs | #16 | Type J thermocouples where used |

### A.6 Communication and data

| Code | Construction | Typical use |
| --- | --- | --- |
| COM-RS485-1P-22 | 1 TSP #22-24 AWG, 120 Ω, shielded, ITC-ER / -HL | Modbus RTU: flow computers, analyzers, meters |
| COM-FF-A | Foundation Fieldbus Type A, 1 TSP #18 AWG, 100 Ω | Fieldbus segments |
| COM-PB-DP | PROFIBUS DP, 1 pair #22 AWG, 150 Ω | PROFIBUS networks (if used by OEM packages) |
| COM-CAT6A-S | Shielded Cat 6A, outdoor / tray-rated | Ethernet inside buildings and e-houses (≤ 90 m) |

### A.7 Fiber optic (2.8)

| Code | Construction | Typical use |
| --- | --- | --- |
| FO-[12/24/48]SM-A | Single-mode OS2, loose tube, gel-free, interlocked armor, OFCR | DCS backbone, protection intertrip, switchyard SCADA, CCTV / security |
| FO-[12/24]MM-A | Multimode OM4, armored | Short runs inside buildings where equipment requires multimode |
| OPGW-[24/48] | Optical ground wire | Transmission line and switchyard shield wire with teleprotection fibers |

### A.8 Grounding (2.9)

| Code | Construction | Typical use |
| --- | --- | --- |
| GND-BARE-[4/0, 500] | Bare soft-drawn stranded Cu | Buried ground grid and ring grounds per IEEE 80 study |
| GND-BARE-2/0 | Bare stranded Cu | Grid risers to structures, fences, tanks, lightning down conductors |
| GND-GRN-[#6 - 4/0] | Green insulated stranded Cu, THHN/THWN-2 or XHHW-2 | Equipment bonding jumpers above grade, panel and tray bonding |
| GND-TRAY-[#4/0 bare or 2/0 insulated] | Cu | Tray ground conductor run full length of power tray where used as EGC path |

Size ranges are typical. Confirm each type's available sizes, OD, mass and ratings against the selected manufacturer's data sheets before procurement.

## Editor's notes

Fill every bracketed value from the inputs below before issue. Owner and utility requirements override this guide.

- ☐ Plant configuration (1x1, 2x1, 3x1) and one-line diagram: sets step-up transformers, switchyard bays and unit separation (3.2 item 4).

- ☐ Owner electrical design criteria: construction policy (2.1 item 4), jacket type, insulation, spare conductors and spare tray / duct capacity.

- ☐ Auxiliary system grounding (1.4) and short-circuit study: fault levels and clearing times for 3.1.

- ☐ Transmission owner standards: switchyard control cable, CT/VT wiring, fiber and OPGW (2.8, 3.2 item 5).

- ☐ Site hazardous area classification drawings (3.4).

- ☐ OEM interface lists for GT, ST, HRSG, CCS and drives: scope split between vendor and field cable; drive cable limits (2.4).

- ☐ Load list: motor ratings, starting method (across-the-line or VFD), duty.

- ☐ Test acceptance values: confirm NETA ATS edition and IEEE 400.2 levels (3.6).

Basis of this guide. It follows the NEC, ICEA, UL and IEEE documents in 1.2, and the structure of UFGS 26 05 13 (Medium-Voltage Cables) and UFGS 26 05 19.00 10 (Insulated Wire and Cable). Product requirements align with published listings for armored MC-HL power, control and VFD cable, 15 kV MV-105 cable and flexible TC-ER VFD cable. These sources were identified by search but not read in full; bracketed values are typical practice. See the Gas & Combined Cycle Plant Cable Requirements reference for the source list.