## Cover
CABLE SCHEDULE
Combined Cycle Power Plant with Post-Combustion CCS, Gas Metering / LNG and Modular RICE Plant
Document No. | CCPP-E-CS-0001
Revision | C (Preliminary - issued for review, NOT FOR CONSTRUCTION). Rev B: converted to US NEC practice - 13.8 kV / 480 V, AWG/kcmil, Type MC-HL armored cable. Rev C: CO2 compressor VFD line/output split; ACC fan local disconnects with flexible Machine Flex type VFD final drops.
Date | 2026-10-18
Basis of layout | Equipment positions from the 3D line-art model examples/powerplant.go (repo shardt87/ln, branch claude/powerplant-example). Coordinates in metres, site grid: X east, Y north, Z up. Lengths reported in metres and feet.
Basis of ratings | Representative ratings for a ~1x1 F-class CCGT (GT ~290 MVA, ST ~175 MVA), amine CCS train, 8 x 2.5 MVA containerised gas engines, 230 kV switchyard. Ratings are typical values, NOT taken from a specific project. See 'Design Basis'.
Cable construction | Power, VFD and control: 600 V and 15 kV Type MC-HL, Cu, XHHW-2 / EPR (MV-105) insulation, continuous corrugated welded aluminum armor (CCW) with PVC jacket - e.g. Southwire Armor-X (product named as an example of the construction only). Final drops to vibrating VFD-driven motors (ACC fans): flexible shielded VFD cable Type TC-ER with 3 symmetrical grounds - e.g. Southwire Machine Flex. Instrument: armored PLTC / ITC-HL. All tray-rated (-TC/-ER), sunlight resistant, UL 1685 / IEEE 1202 FT4. MC-HL with listed fittings is suitable for Class I Div 1 & 2 areas (gas metering, LNG, BOG) per NEC 501.10.
Sheets
Design Basis | Global inputs: route slack, termination allowance, sag allowance, wastage, voltage drop limits, standards.
Equipment | Equipment / termination point list with site coordinates (from the 3D model).
Cable Types | Cable / conductor / busduct library: OD, ampacity, mV/A/m, mass, reel length.
Raceways | Trays, trenches, duct banks, busducts, OHL - elevation, correction factor and fill check.
Cable Schedule | One row per circuit. Route length, total length, running and design current, loading, voltage drop and check are all formulas.
BOQ Summary | Quantities by cable type (with wastage, reels, mass) and by system.
References | Public documents identified as references for typical arrangements, and cable product data.
Legend
Blue text | Hard-coded input - edit these
Black text | Formula - do not overwrite
Green text | Lookup from another sheet
Yellow fill | Key assumption to be verified against vendor / project data
Route length method | M = Manhattan route along raceway: (¦dX¦+¦dY¦ + rise from each end to raceway elevation) x (1+slack) + 2 x termination allowance. D = direct span (overhead conductors): 3D distance x (1+sag allowance). A value in 'Length Override' replaces the calculation (used for earth grids / bonds).
Sizing | Design current = running current x sizing factor: 1.25 for motors (NEC 430.22) and continuous loads (NEC 210.19 / 215.2), 1.15 for generator conductors (NEC 445.13), 1.00 for transformer secondaries / busduct. Allowable ampacity = base ampacity (NEC 310.16 75 C column for 600 V; NEC 311.60 for 15 kV) x raceway correction factor. Voltage drop uses NEC Ch. 9 Table 9 effective Z at 0.85 PF (AC) or Table 8 DC resistance.
Limitations | Preliminary sizing only. Short-circuit withstand (ICEA P-32-382), motor starting voltage dip, ground fault return path, detailed tray fill per NEC 392.22 and ampacity per NEC 392.80 / IEEE 835 (Neher-McGrath for duct banks) must be verified at detailed design. Raceway fill counts each cable on its primary raceway only.

## Design Basis
DESIGN BASIS - GLOBAL INPUTS
Parameter |  | Value | Note
Route slack / snaking allowance |  | 10% | Typical 5-15% on tray routes for bends, drops and snaking.
Termination allowance per end (m) |  | 3 | Gland / connector, tail and dressing inside panel / terminal box.
Overhead conductor sag allowance |  | 3% | Conductor length over chord for strung bus and line spans.
Procurement wastage allowance |  | 5% | Applied in BOQ only.
Ambient air design temperature (deg C) |  | 40 | Information - included in raceway correction factors (NEC 310.15(B) 0.88 for 75 C at 40 C).
Earth thermal resistivity (RHO) |  | 90 | Information - included in duct bank factors (IEEE 835 / NEC 311.60, RHO 90).
Feet per metre |  | 3.2808 | Unit conversion.
System | Nominal voltage | Max steady-state voltage drop | Note
HV Overhead | 230 kV |  | Strung bus / OHL - checked for ampacity only.
Busduct | 18 / 19 kV IPB, 480 V LV busway |  | Checked for ampacity only.
MV Power | 13.8 kV | 3% | Feeder volt drop, full load running.
LV Power | 480 V, 3-ph 3-wire + ground | 3% | NEC 215.2 / 210.19 informational notes: 3% feeder or branch, 5% total.
DC Power | 125 V DC / 120-208 V UPS | 3% | Battery / UPS to load.
Control | 120 V AC / 125 V DC |  | Size by CT burden / voltage at coil - not checked here.
Instrument | 24 V DC / 4-20 mA / TC |  | Not checked here.
Fibre Optic | - |  | -
Earthing | - |  | Size per IEEE 80 fault study.
Design standards (reference)
NFPA 70 (NEC) 2023: 310.16 / 311.60 ampacity, 330 Type MC, 392 cable tray, 430.22 motors, 445.13 generators, 501.10 Class I wiring, 725 PLTC, 727 ITC
NEC Chapter 9 Tables 8 and 9: conductor DC resistance and AC effective impedance (voltage drop)
UL 1569 Metal-Clad Cables; UL 2225 cables and fittings for hazardous locations (MC-HL)
ICEA S-95-658 (NEMA WC70) 600 V cables; ICEA S-93-639 (NEMA WC74) 5-46 kV shielded power cables; ICEA S-73-532 control & instrument
IEEE 835: Power cable ampacity tables; IEEE 525: Cable design and installation in substations
IEEE 1202 / UL 1685: Vertical tray flame test (FT4)
IEEE 738: Bare overhead conductor ampacity; IEEE C37.23: Metal-enclosed (isolated phase) bus
IEEE 80: AC substation grounding

## Equipment
Tag | Description | Area | X (m) | Y (m) | Z term. (m) | Location in 3D model / basis
SWY-B1 | 230 kV bay 1 - RICE transformer bay (gantry dead-end) | 10 | 20 | 137.5 | 12.5 | Gantry x=20
SWY-B2 | 230 kV bay 2 - bus coupler (gantry dead-end) | 10 | 40 | 137.5 | 12.5 | Gantry x=40
SWY-B3 | 230 kV bay 3 - GT generator bay (gantry dead-end) | 10 | 60 | 137.5 | 12.5 | Gantry x=60
SWY-B4 | 230 kV bay 4 - ST generator bay / line exit (gantry dead-end) | 10 | 80 | 137.5 | 12.5 | Gantry x=80
TWR-01 | 230 kV transmission tower 1 (terminal) | 10 | 130 | 137.5 | 31.5 | Tower x=130
TWR-02 | 230 kV transmission tower 2 (suspension) | 10 | 200 | 152.5 | 31.5 | Tower x=200
TWR-03 | 230 kV transmission tower 3 (suspension) | 10 | 270 | 167.5 | 31.5 | Tower x=270
SWY-RB | Switchyard relay & control building | 10 | 95 | 128 | 0.5 | Not drawn - assumed
RICE-TX-HV | RICE step-up transformer 13.8/230 kV 22 MVA - HV bushings | 50 | 19 | 107.5 | 8 | Transformer at (14-20,105-110)
RICE-TX-LV | RICE step-up transformer 13.8/230 kV 22 MVA - LV cable box | 50 | 14.5 | 107.5 | 2 | Transformer at (14-20,105-110)
GEN-GT | Gas turbine generator ~290 MVA, 19 kV - line terminals | 20 | 58 | 18 | 4 | GT generator box (52-64,10-18)
GEN-ST | Steam turbine generator ~175 MVA, 18 kV - line terminals | 20 | 60 | 46 | 6 | ST hall north wall
GSU-GT-HV | GT step-up transformer 19/230 kV 290 MVA - HV bushings | 20 | 54 | 65.5 | 10 | Transformer(50,60)
GSU-GT-LV | GT step-up transformer - LV bushings / marshalling box | 20 | 54 | 60 | 4.5 | Transformer(50,60)
GSU-ST-HV | ST step-up transformer 18/230 kV 175 MVA - HV bushings | 20 | 74 | 65.5 | 10 | Transformer(70,60)
GSU-ST-LV | ST step-up transformer - LV bushings / marshalling box | 20 | 74 | 60 | 4.5 | Transformer(70,60)
UAT-1 | Unit auxiliary transformer 1, 19/13.8 kV 45 MVA | 20 | 44 | 64 | 3 | Not drawn - west of GSU-GT
UAT-2 | Unit auxiliary transformer 2, 18/13.8 kV 30 MVA (feeds CCS) | 20 | 86 | 64 | 3 | Not drawn - east of GSU-ST
NGR-GT | GT generator neutral grounding transformer cubicle | 20 | 62 | 18 | 1 | Assumed
NGR-ST | ST generator neutral grounding transformer cubicle | 20 | 64 | 46 | 1 | Assumed
LCI-TX | GT static starter (LCI) isolation transformer 8 MVA | 20 | 40 | -6 | 0.5 | GT PEECC - assumed
LCI-GT | GT static starter (LCI) cubicle | 20 | 44 | -6 | 0.5 | GT PEECC - assumed
GTCP | GT control panel (in PEECC) | 20 | 46 | -6 | 0.5 | GT PEECC - assumed
MCC-GT | GT auxiliary MCC 480 V (in PEECC) | 20 | 48 | -6 | 0.5 | GT PEECC - assumed
M-GT-LOP | GT AC lube oil pump motor 75 kW | 20 | 60 | -5 | 0.5 | GT enclosure (42-70,-3..7)
M-GT-ELOP | GT DC emergency lube oil pump motor 15 kW | 20 | 61 | -5 | 0.5 | GT enclosure
M-GT-VNT-A | GT enclosure ventilation fan A 45 kW | 20 | 52 | 6.5 | 11 | Roof vent package (46-66,-2.5..6.5)
M-GT-VNT-B | GT enclosure ventilation fan B 45 kW | 20 | 60 | 6.5 | 11 | Roof vent package
JB-GT-TC | GT exhaust thermocouple junction box | 20 | 72 | 2 | 6 | Exhaust diffuser (70-76)
JB-FG-GT | F&G junction box - GT enclosure | 20 | 60 | -3 | 1 | GT enclosure
MCC-HRSG | HRSG auxiliary MCC 480 V | 20 | 80 | -9 | 0.5 | Assumed south of HRSG
M-BFP-A | HP/IP boiler feed pump A motor 3.2 MW, 13.8 kV | 20 | 86 | -9 | 0.5 | South of HRSG
M-BFP-B | HP/IP boiler feed pump B motor 3.2 MW, 13.8 kV | 20 | 90 | -9 | 0.5 | South of HRSG
M-HRSG-RCP | HRSG preheater recirculation pump motor 55 kW | 20 | 100 | -8 | 0.5 | South of HRSG
JB-HRSG-01 | HRSG drum platform instrument junction box | 20 | 97 | -6 | 30 | HP drum z=30
STK | HRSG stack (lightning down conductor) | 20 | 117 | 3 | 55 | Stack r=3.5, h=55
AE-STK | CEMS probe at stack sample port | 20 | 117 | -0.5 | 40 | Stack
CEMS-SH | CEMS analyser shelter | 20 | 122 | -8 | 0.5 | Assumed
TCP-ST | ST control panel | 20 | 85 | 40 | 0.5 | ST hall (52-92,28-46)
MCC-ST | ST auxiliary MCC 480 V | 20 | 88 | 30 | 0.5 | ST hall
M-ST-TG | ST turning gear motor 37 kW | 20 | 66 | 36 | 6 | ST at (60-72,32-40)
M-ST-LOP | ST AC lube oil pump motor 55 kW | 20 | 70 | 30 | 0.5 | ST hall
M-ST-ELOP | ST DC emergency lube oil pump motor 22 kW | 20 | 72 | 30 | 0.5 | ST hall
M-CEP-A | Condensate extraction pump A motor 500 kW, 13.8 kV | 20 | 88 | 44 | 0.5 | ST hall
M-CEP-B | Condensate extraction pump B motor 500 kW, 13.8 kV | 20 | 88 | 41 | 0.5 | ST hall
RIO-PB | DCS remote I/O cabinet - power block | 20 | 68 | 22 | 0.5 | Assumed
EG-PB | Power block main earth grid (nearest riser) | 20 | 75 | 20 | -0.8 | Buried
LVT-ACC | ACC fan transformer 13.8/0.48 kV 3 MVA | 30 | 146 | 40 | 0.5 | East of ACC (98-142,26-60)
MCC-ACC | ACC fan VFD switchroom 480 V | 30 | 146 | 46 | 0.5 | East of ACC
JB-ACC | ACC instrument junction box | 30 | 142 | 30 | 0.5 | ACC
M-ACC-01 | ACC fan motor 01, 150 kW 480 V (VFD) | 30 | 104 | 32 | 20.5 | Fan ring (104,32) on deck z=20
DS-ACC-01 | ACC fan 01 local disconnect switch (in sight of motor, NEC 430.102) | 30 | 108 | 32 | 20.5 | Fan bridge beside ring (104,32)
M-ACC-02 | ACC fan motor 02, 150 kW 480 V (VFD) | 30 | 104 | 43 | 20.5 | Fan ring (104,43) on deck z=20
DS-ACC-02 | ACC fan 02 local disconnect switch (in sight of motor, NEC 430.102) | 30 | 108 | 43 | 20.5 | Fan bridge beside ring (104,43)
M-ACC-03 | ACC fan motor 03, 150 kW 480 V (VFD) | 30 | 104 | 54 | 20.5 | Fan ring (104,54) on deck z=20
DS-ACC-03 | ACC fan 03 local disconnect switch (in sight of motor, NEC 430.102) | 30 | 108 | 54 | 20.5 | Fan bridge beside ring (104,54)
M-ACC-04 | ACC fan motor 04, 150 kW 480 V (VFD) | 30 | 112 | 32 | 20.5 | Fan ring (112,32) on deck z=20
DS-ACC-04 | ACC fan 04 local disconnect switch (in sight of motor, NEC 430.102) | 30 | 116 | 32 | 20.5 | Fan bridge beside ring (112,32)
M-ACC-05 | ACC fan motor 05, 150 kW 480 V (VFD) | 30 | 112 | 43 | 20.5 | Fan ring (112,43) on deck z=20
DS-ACC-05 | ACC fan 05 local disconnect switch (in sight of motor, NEC 430.102) | 30 | 116 | 43 | 20.5 | Fan bridge beside ring (112,43)
M-ACC-06 | ACC fan motor 06, 150 kW 480 V (VFD) | 30 | 112 | 54 | 20.5 | Fan ring (112,54) on deck z=20
DS-ACC-06 | ACC fan 06 local disconnect switch (in sight of motor, NEC 430.102) | 30 | 116 | 54 | 20.5 | Fan bridge beside ring (112,54)
M-ACC-07 | ACC fan motor 07, 150 kW 480 V (VFD) | 30 | 120 | 32 | 20.5 | Fan ring (120,32) on deck z=20
DS-ACC-07 | ACC fan 07 local disconnect switch (in sight of motor, NEC 430.102) | 30 | 124 | 32 | 20.5 | Fan bridge beside ring (120,32)
M-ACC-08 | ACC fan motor 08, 150 kW 480 V (VFD) | 30 | 120 | 43 | 20.5 | Fan ring (120,43) on deck z=20
DS-ACC-08 | ACC fan 08 local disconnect switch (in sight of motor, NEC 430.102) | 30 | 124 | 43 | 20.5 | Fan bridge beside ring (120,43)
M-ACC-09 | ACC fan motor 09, 150 kW 480 V (VFD) | 30 | 120 | 54 | 20.5 | Fan ring (120,54) on deck z=20
DS-ACC-09 | ACC fan 09 local disconnect switch (in sight of motor, NEC 430.102) | 30 | 124 | 54 | 20.5 | Fan bridge beside ring (120,54)
M-ACC-10 | ACC fan motor 10, 150 kW 480 V (VFD) | 30 | 128 | 32 | 20.5 | Fan ring (128,32) on deck z=20
DS-ACC-10 | ACC fan 10 local disconnect switch (in sight of motor, NEC 430.102) | 30 | 132 | 32 | 20.5 | Fan bridge beside ring (128,32)
M-ACC-11 | ACC fan motor 11, 150 kW 480 V (VFD) | 30 | 128 | 43 | 20.5 | Fan ring (128,43) on deck z=20
DS-ACC-11 | ACC fan 11 local disconnect switch (in sight of motor, NEC 430.102) | 30 | 132 | 43 | 20.5 | Fan bridge beside ring (128,43)
M-ACC-12 | ACC fan motor 12, 150 kW 480 V (VFD) | 30 | 128 | 54 | 20.5 | Fan ring (128,54) on deck z=20
DS-ACC-12 | ACC fan 12 local disconnect switch (in sight of motor, NEC 430.102) | 30 | 132 | 54 | 20.5 | Fan bridge beside ring (128,54)
M-ACC-13 | ACC fan motor 13, 150 kW 480 V (VFD) | 30 | 136 | 32 | 20.5 | Fan ring (136,32) on deck z=20
DS-ACC-13 | ACC fan 13 local disconnect switch (in sight of motor, NEC 430.102) | 30 | 140 | 32 | 20.5 | Fan bridge beside ring (136,32)
M-ACC-14 | ACC fan motor 14, 150 kW 480 V (VFD) | 30 | 136 | 43 | 20.5 | Fan ring (136,43) on deck z=20
DS-ACC-14 | ACC fan 14 local disconnect switch (in sight of motor, NEC 430.102) | 30 | 140 | 43 | 20.5 | Fan bridge beside ring (136,43)
M-ACC-15 | ACC fan motor 15, 150 kW 480 V (VFD) | 30 | 136 | 54 | 20.5 | Fan ring (136,54) on deck z=20
DS-ACC-15 | ACC fan 15 local disconnect switch (in sight of motor, NEC 430.102) | 30 | 140 | 54 | 20.5 | Fan bridge beside ring (136,54)
MVS-CCS | CCS 13.8 kV switchboard (CCS substation) | 40 | 178 | 58 | 0.5 | Tray TR-02 end (180,64)
LVT-CCS | CCS LV transformer 13.8/0.48 kV 2.5 MVA | 40 | 182 | 60 | 0.5 | CCS substation
PMCC-CCS | CCS power / motor control centre 480 V | 40 | 176 | 60 | 0.5 | CCS substation
RIO-CCS | DCS remote I/O cabinet - CCS | 40 | 174 | 58 | 0.5 | CCS substation
M-BF | Flue gas booster fan motor 6.5 MW, 13.8 kV | 40 | 150 | -4 | 0.5 | Booster fan (145-155,-8..0)
M-DCC-A | Direct contact cooler circulation pump A 400 kW, 13.8 kV | 40 | 146 | 6 | 0.5 | DCC r=5 at (150,3)
M-DCC-B | Direct contact cooler circulation pump B 400 kW, 13.8 kV | 40 | 146 | 9 | 0.5 | DCC
M-RAP-A | Rich amine pump A 700 kW, 13.8 kV | 40 | 174 | 16 | 0.5 | Absorber r=8 at (170,6)
M-RAP-B | Rich amine pump B 700 kW, 13.8 kV | 40 | 177 | 16 | 0.5 | Absorber
M-LAP-A | Lean amine pump A 800 kW, 13.8 kV | 40 | 186 | 12 | 0.5 | Stripper r=4 at (190,20)
M-LAP-B | Lean amine pump B 800 kW, 13.8 kV | 40 | 186 | 15 | 0.5 | Stripper
M-RBC-A | Reboiler condensate pump A 110 kW, 480 V | 40 | 200 | 24 | 0.5 | Reboiler at (198,20)
M-CO2C | CO2 compressor motor 14 MW, 13.8 kV (VFD) | 40 | 195 | 39 | 0.5 | Compressor bldg (180-210,32-46)
UCP-CO2 | CO2 compressor unit control panel | 40 | 192 | 34 | 0.5 | Compressor bldg
VFD-CO2 | CO2 compressor MV variable frequency drive, 13.8 kV in / out | 40 | 186 | 40 | 0.5 | Compressor bldg - assumed
PKG-DEH | CO2 dehydration package (TEG) 250 kVA | 40 | 214 | 39 | 0.5 | Dehydration (210-218,34-44)
FC-CO2 | CO2 export fiscal meter skid / flow computer | 40 | 242 | 39 | 1 | Meter skid (240-244,37-41)
JB-ABS-01 | Absorber instrument junction box (mid-height) | 40 | 170 | -2.5 | 30 | Absorber
JB-STR-01 | Stripper instrument junction box | 40 | 190 | 15.5 | 20 | Stripper
JB-FG-CCS | F&G junction box - CCS area | 40 | 172 | -3 | 1 | CCS
C-ABS | Absorber column shell (lightning / bonding) | 40 | 170 | 6 | 0 | Absorber
EG-CCS | CCS area earth grid (nearest riser) | 40 | 190 | 25 | -0.8 | Buried
MVS-RICE | RICE 13.8 kV collector switchgear e-house | 50 | 12 | 99 | 0.5 | E-house (6-18,96-102)
LVT-RICE | RICE auxiliary transformer 13.8/0.48 kV 1 MVA | 50 | 10 | 104 | 0.5 | Assumed
MCC-RICE | RICE auxiliary MCC 480 V | 50 | 16 | 99 | 0.5 | E-house
RPC | RICE plant controller | 50 | 8 | 99 | 0.5 | E-house
EG-RICE | RICE area earth grid (nearest riser) | 50 | -4 | 85 | -0.8 | Buried
GEN-R01 | Gas engine genset 1 (40 ft container) 2.5 MVA, 13.8 kV - terminal box | 50 | 2.2 | 71.45 | 1.5 | Container y=70.0
GEN-R02 | Gas engine genset 2 (40 ft container) 2.5 MVA, 13.8 kV - terminal box | 50 | 2.2 | 75.65 | 1.5 | Container y=74.2
GEN-R03 | Gas engine genset 3 (40 ft container) 2.5 MVA, 13.8 kV - terminal box | 50 | 2.2 | 79.85 | 1.5 | Container y=78.4
GEN-R04 | Gas engine genset 4 (40 ft container) 2.5 MVA, 13.8 kV - terminal box | 50 | 2.2 | 84.05 | 1.5 | Container y=82.6
GEN-R05 | Gas engine genset 5 (40 ft container) 2.5 MVA, 13.8 kV - terminal box | 50 | 2.2 | 88.25 | 1.5 | Container y=86.8
GEN-R06 | Gas engine genset 6 (40 ft container) 2.5 MVA, 13.8 kV - terminal box | 50 | 2.2 | 92.45 | 1.5 | Container y=91.0
GEN-R07 | Gas engine genset 7 (40 ft container) 2.5 MVA, 13.8 kV - terminal box | 50 | 2.2 | 96.65 | 1.5 | Container y=95.2
GEN-R08 | Gas engine genset 8 (40 ft container) 2.5 MVA, 13.8 kV - terminal box | 50 | 2.2 | 100.85 | 1.5 | Container y=99.4
AUX-R01 | Genset 1 auxiliary panel (radiator fans, pre-lube, jacket heater) | 50 | -4 | 71.45 | 1 | Container y=70.0
AUX-R02 | Genset 2 auxiliary panel (radiator fans, pre-lube, jacket heater) | 50 | -4 | 75.65 | 1 | Container y=74.2
AUX-R03 | Genset 3 auxiliary panel (radiator fans, pre-lube, jacket heater) | 50 | -4 | 79.85 | 1 | Container y=78.4
AUX-R04 | Genset 4 auxiliary panel (radiator fans, pre-lube, jacket heater) | 50 | -4 | 84.05 | 1 | Container y=82.6
AUX-R05 | Genset 5 auxiliary panel (radiator fans, pre-lube, jacket heater) | 50 | -4 | 88.25 | 1 | Container y=86.8
AUX-R06 | Genset 6 auxiliary panel (radiator fans, pre-lube, jacket heater) | 50 | -4 | 92.45 | 1 | Container y=91.0
AUX-R07 | Genset 7 auxiliary panel (radiator fans, pre-lube, jacket heater) | 50 | -4 | 96.65 | 1 | Container y=95.2
AUX-R08 | Genset 8 auxiliary panel (radiator fans, pre-lube, jacket heater) | 50 | -4 | 100.85 | 1 | Container y=99.4
TK-LNG | LNG full-containment tank (bonding) | 60 | -60 | 10 | 0 | Tank r=16 at (-60,10)
M-LNG-P1 | LNG in-tank send-out pump 1, 250 kW 480 V (top penetration) | 60 | -60 | 10 | 24 | Tank roof z=24
M-LNG-P2 | LNG in-tank send-out pump 2, 250 kW 480 V (top penetration) | 60 | -58 | 12 | 24 | Tank roof z=24
LT-LNG | LNG tank level / temperature gauging head | 60 | -60 | -6 | 24 | Tank roof
C-BOG | Boil-off gas compressor motor 900 kW, 13.8 kV | 60 | -45 | 25 | 0.5 | Assumed north of vaporizers
JB-LNG | LNG area instrument junction box | 60 | -44 | 8 | 0.5 | Pipe to station y=10
HTP-LNG | Heat tracing / lighting panel - LNG area | 60 | -42 | 4 | 0.5 | Assumed
XV-001 | Station inlet ESD valve (electro-hydraulic actuator) | 60 | -24 | 10 | 4 | Inlet pipe (-44..-25, y=10, z=4)
LVT-GAS | Gas station transformer 13.8/0.48 kV 1.6 MVA | 60 | -12 | 16 | 0.5 | Assumed north of skid
MCC-GAS | Gas station MCC 480 V (shelter) | 60 | -20 | 12 | 0.5 | Shelter (-25..-15,10-14)
RIO-GAS | DCS remote I/O cabinet - gas station (shelter) | 60 | -18 | 12 | 0.5 | Shelter
FC-GAS | Fiscal gas flow computer / metering panel (shelter) | 60 | -17 | 12 | 0.5 | Shelter
AT-GC | Gas chromatograph (shelter) | 60 | -22 | 12 | 0.5 | Shelter
FT-101A | Ultrasonic gas meter run A | 60 | -7.25 | -3 | 2.2 | Meter body run y=-3
FT-101B | Ultrasonic gas meter run B | 60 | -7.25 | 0 | 2.2 | Meter body run y=0
FT-101C | Ultrasonic gas meter run C (spare / check) | 60 | -7.25 | 3 | 2.2 | Meter body run y=3
PCV-101 | Pressure reducing / regulating valve skid | 60 | 1.5 | 1.5 | 2.5 | Regulator box (0-3,0-3)
H-101 | Fuel gas electric heater 400 kW | 60 | 2 | 7 | 1.5 | Heater (0-4, y=7)
JB-GAS | Gas station instrument junction box | 60 | -10 | 8 | 0.5 | Skid
EG-GAS | Gas / LNG area earth grid (nearest riser) | 60 | -30 | 5 | -0.8 | Buried
MVS-1 | Main 13.8 kV switchboard (main electrical building) | 70 | 36 | 52 | 0.5 | E-house (34-46,50-56)
PMCC-1 | Main power / motor control centre 480 V | 70 | 44 | 52 | 0.5 | E-house
LVT-1 | Main LV transformer 13.8/0.48 kV 2.5 MVA | 70 | 34 | 57 | 0.5 | North of e-house
DCS-CCR | DCS servers / central control room | 70 | 40 | 55 | 0.5 | E-house
GPP | Generator & transformer protection panels | 70 | 38 | 55 | 0.5 | E-house
DCB-1 | 125 V DC battery and chargers | 70 | 42 | 55 | 0.5 | E-house
UPS-1 | 230 V AC UPS | 70 | 43 | 55 | 0.5 | E-house
FGP-1 | Fire & gas panel | 70 | 39 | 55.5 | 0.5 | E-house
EG-SWY | Switchyard earth grid (nearest riser) | 10 | 50 | 137.5 | -0.8 | Buried

## Cable Types
Code | Description | Category | Conductors / cables per run | OD (mm) | Base ampacity per run (A) | mV/A/m (3-ph line, or 1-ph/DC loop) | Mass (kg/m per conductor) | Std reel length (m) | Basis
ACSR-DRAKE | ACSR 795 kcmil 'Drake' 26/7, 1 per phase | HV Overhead | 3 | 28.1 | 900 |  | 1.628 | 2000 | IEEE 738 typical (40 C ambient, 75 C conductor, 2 ft/s wind)
ACSR-DRAKE-2B | ACSR 795 kcmil 'Drake' 26/7, twin bundle per phase | HV Overhead | 6 | 28.1 | 1800 |  | 1.628 | 2000 | IEEE 738 typical (40 C ambient, 75 C conductor, 2 ft/s wind)
SW-7/16-EHS | Shield wire 7/16" EHS galvanized steel | HV Overhead | 1 | 11.1 |  |  | 0.595 | 3000 | IEEE 738 typical (40 C ambient, 75 C conductor, 2 ft/s wind)
OPGW-24 | OPGW 24-fiber shield wire | HV Overhead | 1 | 14 |  |  | 0.62 | 4000 | IEEE 738 typical (40 C ambient, 75 C conductor, 2 ft/s wind)
IPB-10K | Isolated phase bus 24 kV, 10 kA (per phase metre) | Busduct | 3 |  | 10000 |  | 160 |  | Vendor nominal rating (IEEE C37.23 / UL 857)
IPB-7K | Isolated phase bus 24 kV, 7 kA (per phase metre) | Busduct | 3 |  | 7000 |  | 120 |  | Vendor nominal rating (IEEE C37.23 / UL 857)
IPB-3K | Isolated phase tap bus 24 kV, 3 kA (per phase metre) | Busduct | 3 |  | 3000 |  | 70 |  | Vendor nominal rating (IEEE C37.23 / UL 857)
LVBD-4000 | 600 V busway 4000 A, Cu, 3-ph + ground, outdoor feeder | Busduct | 1 |  | 4000 |  | 45 |  | Vendor nominal rating (IEEE C37.23 / UL 857)
LVBD-2500 | 600 V busway 2500 A, Cu, 3-ph + ground, outdoor feeder | Busduct | 1 |  | 2500 |  | 30 |  | Vendor nominal rating (IEEE C37.23 / UL 857)
MV-1C-2-NGR | 15 kV MV-105 1/C #2 AWG Cu EPR 133% shielded, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | MV Power | 1 | 33 | 195 |  | 1.6 | 300 | NEC 311.60(C) 15 kV Cu 90 C in air, 40 C ambient (approx.); VD from R cos + X sin at 0.85 PF
MV-3C-2 | 15 kV MV-105 3/C #2 AWG Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | MV Power | 1 | 61 | 165 | 1.068 | 4 | 300 | NEC 311.60(C) 15 kV Cu 90 C in air, 40 C ambient (approx.); VD from R cos + X sin at 0.85 PF
MV-3C-1/0 | 15 kV MV-105 3/C 1/0 AWG Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | MV Power | 1 | 66 | 215 | 0.716 | 5.3 | 300 | NEC 311.60(C) 15 kV Cu 90 C in air, 40 C ambient (approx.); VD from R cos + X sin at 0.85 PF
MV-3C-4/0 | 15 kV MV-105 3/C 4/0 AWG Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | MV Power | 1 | 76 | 310 | 0.426 | 8 | 300 | NEC 311.60(C) 15 kV Cu 90 C in air, 40 C ambient (approx.); VD from R cos + X sin at 0.85 PF
MV-3C-500 | 15 kV MV-105 3/C 500 kcmil Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | MV Power | 1 | 94 | 515 | 0.256 | 15.5 | 300 | NEC 311.60(C) 15 kV Cu 90 C in air, 40 C ambient (approx.); VD from R cos + X sin at 0.85 PF
MV-1C-500-TPX | 15 kV MV-105 1/C 500 kcmil Cu EPR 133% shielded, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt, triplexed set | MV Power | 3 | 41 | 585 | 0.256 | 4.4 | 300 | NEC 311.60(C) 15 kV Cu 90 C in air, 40 C ambient (approx.); VD from R cos + X sin at 0.85 PF
MV-1C-750-TPX | 15 kV MV-105 1/C 750 kcmil Cu EPR 133% shielded, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt, triplexed set | MV Power | 3 | 46 | 740 | 0.21 | 6.2 | 300 | NEC 311.60(C) 15 kV Cu 90 C in air, 40 C ambient (approx.); VD from R cos + X sin at 0.85 PF
MV-1C-1000-TPX | 15 kV MV-105 1/C 1000 kcmil Cu EPR 133% shielded, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt, triplexed set | MV Power | 3 | 51 | 860 | 0.188 | 7.9 | 300 | NEC 311.60(C) 15 kV Cu 90 C in air, 40 C ambient (approx.); VD from R cos + X sin at 0.85 PF
LV-3C-10 | 600 V 3/C #10 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | LV Power | 1 | 20 | 35 | 6.251 | 0.6 | 600 | NEC 310.16 Cu 75 C column (termination limit); NEC 392.80(A)(1); VD NEC Ch.9 Table 9, 0.85 PF
LV-3C-6 | 600 V 3/C #6 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | LV Power | 1 | 24 | 65 | 2.557 | 0.95 | 600 | NEC 310.16 Cu 75 C column (termination limit); NEC 392.80(A)(1); VD NEC Ch.9 Table 9, 0.85 PF
LV-3C-2 | 600 V 3/C #2 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | LV Power | 1 | 31 | 115 | 1.08 | 1.8 | 600 | NEC 310.16 Cu 75 C column (termination limit); NEC 392.80(A)(1); VD NEC Ch.9 Table 9, 0.85 PF
LV-3C-1/0 | 600 V 3/C 1/0 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | LV Power | 1 | 37 | 150 | 0.682 | 2.6 | 300 | NEC 310.16 Cu 75 C column (termination limit); NEC 392.80(A)(1); VD NEC Ch.9 Table 9, 0.85 PF
LV-3C-4/0 | 600 V 3/C 4/0 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | LV Power | 1 | 47 | 230 | 0.392 | 4.6 | 300 | NEC 310.16 Cu 75 C column (termination limit); NEC 392.80(A)(1); VD NEC Ch.9 Table 9, 0.85 PF
LV-3C-350 | 600 V 3/C 350 kcmil + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | LV Power | 1 | 57 | 310 | 0.273 | 7.2 | 300 | NEC 310.16 Cu 75 C column (termination limit); NEC 392.80(A)(1); VD NEC Ch.9 Table 9, 0.85 PF
LV-3C-500 | 600 V 3/C 500 kcmil + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | LV Power | 1 | 66 | 380 | 0.222 | 9.8 | 300 | NEC 310.16 Cu 75 C column (termination limit); NEC 392.80(A)(1); VD NEC Ch.9 Table 9, 0.85 PF
LV-VFD-500 | 600/1000 V VFD 3/C 500 kcmil + 3 symmetrical G, Cu XLPE, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | LV Power | 1 | 70 | 380 | 0.222 | 11 | 300 | NEC 310.16 Cu 75 C column (termination limit); NEC 392.80(A)(1); VD NEC Ch.9 Table 9, 0.85 PF
LV-MFX-2/0 | 1000 V 3/C 2/0 AWG + 3 symmetrical G, flexible tinned Cu XHHW-2, foil + braid shield, TPE jkt, Type TC-ER, NFPA 79 (Machine Flex type) | LV Power | 1 | 38 | 175 | 0.568 | 2.6 | 300 | NEC 310.16 Cu 75 C column (termination limit); NEC 392.80(A)(1); VD NEC Ch.9 Table 9, 0.85 PF
LV-2C-10 | 600 V 2/C #10 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | DC Power | 1 | 18 | 35 | 8.137 | 0.5 | 600 | NEC 310.16 75 C (1/C in tray: 392.80(A)(2), 75% of 310.17); VD NEC Ch.9 Table 8 DC loop
LV-2C-6 | 600 V 2/C #6 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | DC Power | 1 | 22 | 65 | 3.222 | 0.8 | 600 | NEC 310.16 75 C (1/C in tray: 392.80(A)(2), 75% of 310.17); VD NEC Ch.9 Table 8 DC loop
LV-2C-2 | 600 V 2/C #2 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | DC Power | 1 | 28 | 115 | 1.273 | 1.4 | 600 | NEC 310.16 75 C (1/C in tray: 392.80(A)(2), 75% of 310.17); VD NEC Ch.9 Table 8 DC loop
LV-1C-500 | 600 V 1/C 500 kcmil Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt (+/- pair) | DC Power | 2 | 34 | 465 | 0.169 | 3.3 | 300 | NEC 310.16 75 C (1/C in tray: 392.80(A)(2), 75% of 310.17); VD NEC Ch.9 Table 8 DC loop
CTL-7C-12 | 600 V 7/C #12 AWG Cu XHHW-2 control, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | Control | 1 | 19 |  |  | 0.6 | 600 | Not current-rated here
CTL-12C-14 | 600 V 12/C #14 AWG Cu XHHW-2 control, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | Control | 1 | 21 |  |  | 0.7 | 600 | Not current-rated here
CTL-25C-14 | 600 V 25/C #14 AWG Cu XHHW-2 control, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | Control | 1 | 27 |  |  | 1.1 | 600 | Not current-rated here
CTL-12C-10 | 600 V 12/C #10 AWG Cu XHHW-2 control (CT circuits), Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | Control | 1 | 27 |  |  | 1.2 | 600 | Not current-rated here
INS-1TSP-16 | 300 V 1 TSP #16 AWG, PLTC/ITC-HL, CCW armor, PVC jkt (IS blue) | Instrument | 1 | 13 |  |  | 0.25 | 600 | Not current-rated here
INS-2TSP-16 | 300 V 2 TSP #16 AWG, PLTC/ITC-HL, CCW armor, PVC jkt (IS blue) | Instrument | 1 | 16 |  |  | 0.35 | 600 | Not current-rated here
INS-12TSP-18 | 300 V 12 TSP #18 AWG indiv. + overall shield, PLTC/ITC-HL, CCW armor | Instrument | 1 | 30 |  |  | 0.9 | 600 | Not current-rated here
INS-24TSP-18 | 300 V 24 TSP #18 AWG indiv. + overall shield, PLTC/ITC-HL, CCW armor | Instrument | 1 | 38 |  |  | 1.4 | 600 | Not current-rated here
INS-TC-12P-KX | 300 V 12 pair #16 AWG type KX thermocouple extension, ITC-HL, CCW armor | Instrument | 1 | 30 |  |  | 0.8 | 600 | Not current-rated here
INS-RS485 | 300 V 1 TSP #22 AWG 120 ohm RS-485, ITC-HL, CCW armor | Instrument | 1 | 12 |  |  | 0.2 | 600 | Not current-rated here
FO-24SM | 24-fiber single-mode OFCR, interlocked Al armor | Fibre Optic | 1 | 19 |  |  | 0.3 | 2000 | -
FO-48SM | 48-fiber single-mode OFCR, interlocked Al armor | Fibre Optic | 1 | 21 |  |  | 0.36 | 2000 | -
EG-CU-4/0 | Bare stranded Cu 4/0 AWG ground grid conductor (buried) | Earthing | 1 | 13.3 |  |  | 0.97 | 300 | Size per IEEE 80 fault study
EB-CU-2/0 | Green insulated Cu 2/0 AWG bonding jumper | Earthing | 1 | 15 |  |  | 0.62 | 300 | Size per IEEE 80 fault study

## Cable Schedule
CABLE SCHEDULE - CCPP-E-CS-0001 Rev C (PRELIMINARY) - US NEC practice, Type MC-HL armored cable | [32 empty] | Calculation helpers (lookups - do not edit)
Cable No. | Area | System | Service / Function | From Tag | From Equipment | To Tag | To Equipment | Cable Type | Cable Description | Parallel Runs | Raceway | Route Method | Length Override (m) | Route Length / Run (m) | Route Length / Run (ft) | Total Conductor Length (m) | Total Conductor Length (ft) | System Voltage (V) | Phases | Load (kW / kVA) | PF x Eff. | Running Current (A) | Sizing Factor | Design Current (A) | Allowable Ampacity / Run (A) | Total Capacity (A) | Loading (%) | Volt Drop (%) | VD Limit (%) | Check | Cable Area (mm2) | Notes | X from | Y from | Z from | X to | Y to | Z to | Raceway Elev. | Correction | Cond. / Run | OD (mm) | Base Ampacity (A) | mV/A/m
10-HV-001 | 10 | HV Overhead | GT GSU 230 kV to bay 3 (strung) | GSU-GT-HV | GT step-up transformer 19/230 kV 290 MVA - HV bushings | SWY-B3 | 230 kV bay 3 - GT generator bay (gantry dead-end) | ACSR-DRAKE | ACSR 795 kcmil 'Drake' 26/7, 1 per phase | 1 | OHL | D |  | 75 | 246 | 225 | 738 | 230000 | 3 | 290000 | 1 | 727.9634 | 1 | 727.9634 | 900 | 900 | 80.88% |  |  | OK | 1860.4747 | Load in kVA | 54 | 65.5 | 10 | 60 | 137.5 | 12.5 | 0 | 1 | 3 | 28.1 | 900
10-HV-002 | 10 | HV Overhead | ST GSU 230 kV to bay 4 (strung) | GSU-ST-HV | ST step-up transformer 18/230 kV 175 MVA - HV bushings | SWY-B4 | 230 kV bay 4 - ST generator bay / line exit (gantry dead-end) | ACSR-DRAKE | ACSR 795 kcmil 'Drake' 26/7, 1 per phase | 1 | OHL | D |  | 75 | 246 | 225 | 738 | 230000 | 3 | 175000 | 1 | 439.2882 | 1 | 439.2882 | 900 | 900 | 48.81% |  |  | OK | 1860.4747 | Load in kVA | 74 | 65.5 | 10 | 80 | 137.5 | 12.5 | 0 | 1 | 3 | 28.1 | 900
10-HV-003 | 10 | HV Overhead | RICE transformer 230 kV to bay 1 (strung) | RICE-TX-HV | RICE step-up transformer 13.8/230 kV 22 MVA - HV bushings | SWY-B1 | 230 kV bay 1 - RICE transformer bay (gantry dead-end) | ACSR-DRAKE | ACSR 795 kcmil 'Drake' 26/7, 1 per phase | 1 | OHL | D |  | 32 | 105 | 96 | 315 | 230000 | 3 | 22000 | 1 | 55.2248 | 1 | 55.2248 | 900 | 900 | 6.136% |  |  | OK | 1860.4747 | Load in kVA | 19 | 107.5 | 8 | 20 | 137.5 | 12.5 | 0 | 1 | 3 | 28.1 | 900
10-HV-004 | 10 | HV Overhead | Strung main bus bay 1 - bay 2 | SWY-B1 | 230 kV bay 1 - RICE transformer bay (gantry dead-end) | SWY-B2 | 230 kV bay 2 - bus coupler (gantry dead-end) | ACSR-DRAKE-2B | ACSR 795 kcmil 'Drake' 26/7, twin bundle per phase | 1 | OHL | D |  | 21 | 69 | 126 | 413 | 230000 | 3 | 487000 | 1 | 1222.4764 | 1 | 1222.4764 | 1800 | 1800 | 67.92% |  |  | OK | 3720.9495 | Rated for total plant export | 20 | 137.5 | 12.5 | 40 | 137.5 | 12.5 | 0 | 1 | 6 | 28.1 | 1800
10-HV-005 | 10 | HV Overhead | Strung main bus bay 2 - bay 3 | SWY-B2 | 230 kV bay 2 - bus coupler (gantry dead-end) | SWY-B3 | 230 kV bay 3 - GT generator bay (gantry dead-end) | ACSR-DRAKE-2B | ACSR 795 kcmil 'Drake' 26/7, twin bundle per phase | 1 | OHL | D |  | 21 | 69 | 126 | 413 | 230000 | 3 | 487000 | 1 | 1222.4764 | 1 | 1222.4764 | 1800 | 1800 | 67.92% |  |  | OK | 3720.9495 |  | 40 | 137.5 | 12.5 | 60 | 137.5 | 12.5 | 0 | 1 | 6 | 28.1 | 1800
10-HV-006 | 10 | HV Overhead | Strung main bus bay 3 - bay 4 | SWY-B3 | 230 kV bay 3 - GT generator bay (gantry dead-end) | SWY-B4 | 230 kV bay 4 - ST generator bay / line exit (gantry dead-end) | ACSR-DRAKE-2B | ACSR 795 kcmil 'Drake' 26/7, twin bundle per phase | 1 | OHL | D |  | 21 | 69 | 126 | 413 | 230000 | 3 | 487000 | 1 | 1222.4764 | 1 | 1222.4764 | 1800 | 1800 | 67.92% |  |  | OK | 3720.9495 |  | 60 | 137.5 | 12.5 | 80 | 137.5 | 12.5 | 0 | 1 | 6 | 28.1 | 1800
10-HV-007 | 10 | HV Overhead | Outgoing 230 kV line: bay 4 to terminal tower T1 | SWY-B4 | 230 kV bay 4 - ST generator bay / line exit (gantry dead-end) | TWR-01 | 230 kV transmission tower 1 (terminal) | ACSR-DRAKE-2B | ACSR 795 kcmil 'Drake' 26/7, twin bundle per phase | 1 | OHL | D |  | 56 | 184 | 336 | 1102 | 230000 | 3 | 487000 | 1 | 1222.4764 | 1 | 1222.4764 | 1800 | 1800 | 67.92% |  |  | OK | 3720.9495 |  | 80 | 137.5 | 12.5 | 130 | 137.5 | 31.5 | 0 | 1 | 6 | 28.1 | 1800
10-HV-008 | 10 | HV Overhead | Outgoing 230 kV line span T1 - T2 | TWR-01 | 230 kV transmission tower 1 (terminal) | TWR-02 | 230 kV transmission tower 2 (suspension) | ACSR-DRAKE-2B | ACSR 795 kcmil 'Drake' 26/7, twin bundle per phase | 1 | OHL | D |  | 74 | 243 | 444 | 1457 | 230000 | 3 | 487000 | 1 | 1222.4764 | 1 | 1222.4764 | 1800 | 1800 | 67.92% |  |  | OK | 3720.9495 |  | 130 | 137.5 | 31.5 | 200 | 152.5 | 31.5 | 0 | 1 | 6 | 28.1 | 1800
10-HV-009 | 10 | HV Overhead | Outgoing 230 kV line span T2 - T3 | TWR-02 | 230 kV transmission tower 2 (suspension) | TWR-03 | 230 kV transmission tower 3 (suspension) | ACSR-DRAKE-2B | ACSR 795 kcmil 'Drake' 26/7, twin bundle per phase | 1 | OHL | D |  | 74 | 243 | 444 | 1457 | 230000 | 3 | 487000 | 1 | 1222.4764 | 1 | 1222.4764 | 1800 | 1800 | 67.92% |  |  | OK | 3720.9495 |  | 200 | 152.5 | 31.5 | 270 | 167.5 | 31.5 | 0 | 1 | 6 | 28.1 | 1800
10-HV-010 | 10 | HV Overhead | Switchyard shield wires (2 off) bay 1 - bay 4 | SWY-B1 | 230 kV bay 1 - RICE transformer bay (gantry dead-end) | SWY-B4 | 230 kV bay 4 - ST generator bay / line exit (gantry dead-end) | SW-7/16-EHS | Shield wire 7/16" EHS galvanized steel | 2 | OHL | D |  | 62 | 203 | 124 | 407 | [12 empty] | n/a | 193.5378 | Lightning shielding over gantries | 20 | 137.5 | 12.5 | 80 | 137.5 | 12.5 | 0 | 1 | 1 | 11.1
10-HV-011 | 10 | HV Overhead | Line OPGW: bay 4 to T3 (teleprotection / SCADA) | SWY-B4 | 230 kV bay 4 - ST generator bay / line exit (gantry dead-end) | TWR-03 | 230 kV transmission tower 3 (suspension) | OPGW-24 | OPGW 24-fiber shield wire | 1 | OHL | D |  | 200 | 656 | 200 | 656 | [12 empty] | n/a | 153.938 | Chord length bay 4 -> T3; refine per tower spotting | 80 | 137.5 | 12.5 | 270 | 167.5 | 31.5 | 0 | 1 | 1 | 14
20-IPB-001 | 20 | Busduct | GT generator main IPB to GSU-GT LV | GEN-GT | Gas turbine generator ~290 MVA, 19 kV - line terminals | GSU-GT-LV | GT step-up transformer - LV bushings / marshalling box | IPB-10K | Isolated phase bus 24 kV, 10 kA (per phase metre) | 1 | IPB-GT | M |  | 58 | 190 | 174 | 571 | 19000 | 3 | 290000 | 1 | 8812.1883 | 1 | 8812.1883 | 10000 | 10000 | 88.12% |  |  | OK |  | Includes GCB if fitted | 58 | 18 | 4 | 54 | 60 | 4.5 | 4 | 1 | 3 |  | 10000
20-IPB-002 | 20 | Busduct | GT IPB tap to UAT-1 | GEN-GT | Gas turbine generator ~290 MVA, 19 kV - line terminals | UAT-1 | Unit auxiliary transformer 1, 19/13.8 kV 45 MVA | IPB-3K | Isolated phase tap bus 24 kV, 3 kA (per phase metre) | 1 | IPB-GT | M |  | 74 | 243 | 222 | 728 | 19000 | 3 | 45000 | 1 | 1367.4085 | 1 | 1367.4085 | 3000 | 3000 | 45.58% |  |  | OK |  |  | 58 | 18 | 4 | 44 | 64 | 3 | 4 | 1 | 3 |  | 3000
20-IPB-003 | 20 | Busduct | ST generator main IPB to GSU-ST LV | GEN-ST | Steam turbine generator ~175 MVA, 18 kV - line terminals | GSU-ST-LV | ST step-up transformer - LV bushings / marshalling box | IPB-7K | Isolated phase bus 24 kV, 7 kA (per phase metre) | 1 | IPB-ST | M |  | 40 | 131 | 120 | 394 | 18000 | 3 | 175000 | 1 | 5613.1276 | 1 | 5613.1276 | 7000 | 7000 | 80.19% |  |  | OK |  |  | 60 | 46 | 6 | 74 | 60 | 4.5 | 4 | 1 | 3 |  | 7000
20-IPB-004 | 20 | Busduct | ST IPB tap to UAT-2 | GEN-ST | Steam turbine generator ~175 MVA, 18 kV - line terminals | UAT-2 | Unit auxiliary transformer 2, 18/13.8 kV 30 MVA (feeds CCS) | IPB-3K | Isolated phase tap bus 24 kV, 3 kA (per phase metre) | 1 | IPB-ST | M |  | 58 | 190 | 174 | 571 | 18000 | 3 | 30000 | 1 | 962.2504 | 1 | 962.2504 | 3000 | 3000 | 32.08% |  |  | OK |  |  | 60 | 46 | 6 | 86 | 64 | 3 | 4 | 1 | 3 |  | 3000
20-MV-001 | 20 | MV Power | GT generator neutral to NGR | GEN-GT | Gas turbine generator ~290 MVA, 19 kV - line terminals | NGR-GT | GT generator neutral grounding transformer cubicle | MV-1C-2-NGR | 15 kV MV-105 1/C #2 AWG Cu EPR 133% shielded, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | LOCAL | M |  | 14 | 46 | 14 | 46 | [7 empty] | 171.6 | 171.6 |  |  |  | n/a | 855.2986 | Neutral - fault current limited by NGR | 58 | 18 | 4 | 62 | 18 | 1 | 1 | 0.88 | 1 | 33 | 195
20-MV-002 | 20 | MV Power | ST generator neutral to NGR | GEN-ST | Steam turbine generator ~175 MVA, 18 kV - line terminals | NGR-ST | ST generator neutral grounding transformer cubicle | MV-1C-2-NGR | 15 kV MV-105 1/C #2 AWG Cu EPR 133% shielded, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | LOCAL | M |  | 16 | 52 | 16 | 52 | [7 empty] | 171.6 | 171.6 |  |  |  | n/a | 855.2986 | Neutral - fault current limited by NGR | 60 | 46 | 6 | 64 | 46 | 1 | 1 | 0.88 | 1 | 33 | 195
70-MV-001 | 70 | MV Power | UAT-1 to 13.8 kV main switchgear incomer | UAT-1 | Unit auxiliary transformer 1, 19/13.8 kV 45 MVA | MVS-1 | Main 13.8 kV switchboard (main electrical building) | MV-1C-1000-TPX | 15 kV MV-105 1/C 1000 kcmil Cu EPR 133% shielded, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt, triplexed set | 4 | DB-03 | M |  | 35 | 115 | 420 | 1378 | 13800 | 3 | 45000 | 1 | 1882.6639 | 1 | 1882.6639 | 602 | 2408 | 78.18% | 0.02244% | 3% | OK | 24513.8475 | Transformer secondary - 4 triplexed sets | 44 | 64 | 3 | 36 | 52 | 0.5 | -1.2 | 0.7 | 3 | 51 | 860 | 0.188
70-MV-002 | 70 | MV Power | UAT-2 to CCS 13.8 kV switchgear incomer | UAT-2 | Unit auxiliary transformer 2, 18/13.8 kV 30 MVA (feeds CCS) | MVS-CCS | CCS 13.8 kV switchboard (CCS substation) | MV-1C-750-TPX | 15 kV MV-105 1/C 750 kcmil Cu EPR 133% shielded, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt, triplexed set | 3 | TR-02 | M |  | 121 | 397 | 1089 | 3573 | 13800 | 3 | 30000 | 1 | 1255.1093 | 1 | 1255.1093 | 651.2 | 1953.6 | 64.25% | 0.07703% | 3% | OK | 14957.1226 | Transformer secondary - 3 triplexed sets | 86 | 64 | 3 | 178 | 58 | 0.5 | 5 | 0.88 | 3 | 46 | 740 | 0.21
70-MV-003 | 70 | MV Power | MVS-1 / MVS-CCS bus tie | MVS-1 | Main 13.8 kV switchboard (main electrical building) | MVS-CCS | CCS 13.8 kV switchboard (CCS substation) | MV-1C-500-TPX | 15 kV MV-105 1/C 500 kcmil Cu EPR 133% shielded, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt, triplexed set | 1 | TR-02 | M |  | 179 | 587 | 537 | 1762 | 13800 | 3 | 10000 | 1 | 418.3698 | 1 | 418.3698 | 514.8 | 514.8 | 81.27% | 0.1389% | 3% | OK | 3960.7629 |  | 36 | 52 | 0.5 | 178 | 58 | 0.5 | 5 | 0.88 | 3 | 41 | 585 | 0.256
70-MV-004 | 70 | MV Power | MVS-1 to GT LCI isolation transformer | MVS-1 | Main 13.8 kV switchboard (main electrical building) | LCI-TX | GT static starter (LCI) isolation transformer 8 MVA | MV-3C-500 | 15 kV MV-105 3/C 500 kcmil Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-01 | M |  | 85 | 279 | 85 | 279 | 13800 | 3 | 8000 | 1 | 334.6958 | 1.25 | 418.3698 | 453.2 | 453.2 | 92.31% | 0.05278% | 3% | OK | 6939.7782 |  | 36 | 52 | 0.5 | 40 | -6 | 0.5 | 5 | 0.88 | 1 | 94 | 515 | 0.256
70-MV-005 | 20 | MV Power | LCI output to GT generator (start-up) | LCI-GT | GT static starter (LCI) cubicle | GEN-GT | Gas turbine generator ~290 MVA, 19 kV - line terminals | MV-1C-500-TPX | 15 kV MV-105 1/C 500 kcmil Cu EPR 133% shielded, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt, triplexed set | 2 | TR-01 | M |  | 54 | 177 | 324 | 1063 | 6000 | 3 | 8000 | 1 | 769.8004 | 1 | 769.8004 | 514.8 | 1029.6 | 74.77% | 0.08868% | 3% | OK | 7921.5259 | Variable frequency; LCI max output voltage assumed 6 kV | 44 | -6 | 0.5 | 58 | 18 | 4 | 5 | 0.88 | 3 | 41 | 585 | 0.256
70-MV-006 | 20 | MV Power | Boiler feed pump A | MVS-1 | Main 13.8 kV switchboard (main electrical building) | M-BFP-A | HP/IP boiler feed pump A motor 3.2 MW, 13.8 kV | MV-3C-4/0 | 15 kV MV-105 3/C 4/0 AWG Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-01 | M |  | 138 | 453 | 138 | 453 | 13800 | 3 | 3200 | 0.86 | 155.6725 | 1.25 | 194.5906 | 272.8 | 272.8 | 71.33% | 0.06632% | 3% | OK | 4536.4598 | Motor: 125% FLC (NEC 430.22) | 36 | 52 | 0.5 | 86 | -9 | 0.5 | 5 | 0.88 | 1 | 76 | 310 | 0.426
70-MV-007 | 20 | MV Power | Boiler feed pump B | MVS-1 | Main 13.8 kV switchboard (main electrical building) | M-BFP-B | HP/IP boiler feed pump B motor 3.2 MW, 13.8 kV | MV-3C-4/0 | 15 kV MV-105 3/C 4/0 AWG Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-01 | M |  | 143 | 469 | 143 | 469 | 13800 | 3 | 3200 | 0.86 | 155.6725 | 1.25 | 194.5906 | 272.8 | 272.8 | 71.33% | 0.06872% | 3% | OK | 4536.4598 |  | 36 | 52 | 0.5 | 90 | -9 | 0.5 | 5 | 0.88 | 1 | 76 | 310 | 0.426
70-MV-008 | 20 | MV Power | Condensate extraction pump A | MVS-1 | Main 13.8 kV switchboard (main electrical building) | M-CEP-A | Condensate extraction pump A motor 500 kW, 13.8 kV | MV-3C-2 | 15 kV MV-105 3/C #2 AWG Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-02 | M |  | 82 | 269 | 82 | 269 | 13800 | 3 | 500 | 0.82 | 25.5104 | 1.25 | 31.8879 | 145.2 | 145.2 | 21.96% | 0.01619% | 3% | OK | 2922.4666 | #2 AWG minimum for 15 kV / fault withstand | 36 | 52 | 0.5 | 88 | 44 | 0.5 | 5 | 0.88 | 1 | 61 | 165 | 1.068
70-MV-009 | 20 | MV Power | Condensate extraction pump B | MVS-1 | Main 13.8 kV switchboard (main electrical building) | M-CEP-B | Condensate extraction pump B motor 500 kW, 13.8 kV | MV-3C-2 | 15 kV MV-105 3/C #2 AWG Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-02 | M |  | 86 | 282 | 86 | 282 | 13800 | 3 | 500 | 0.82 | 25.5104 | 1.25 | 31.8879 | 145.2 | 145.2 | 21.96% | 0.01698% | 3% | OK | 2922.4666 |  | 36 | 52 | 0.5 | 88 | 41 | 0.5 | 5 | 0.88 | 1 | 61 | 165 | 1.068
70-MV-010 | 70 | MV Power | Main LV transformer LVT-1 | MVS-1 | Main 13.8 kV switchboard (main electrical building) | LVT-1 | Main LV transformer 13.8/0.48 kV 2.5 MVA | MV-3C-1/0 | 15 kV MV-105 3/C 1/0 AWG Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | LOCAL | M |  | 15 | 49 | 15 | 49 | 13800 | 3 | 2500 | 1 | 104.5924 | 1.25 | 130.7406 | 189.2 | 189.2 | 69.1% | 0.00814% | 3% | OK | 3421.1944 |  | 36 | 52 | 0.5 | 34 | 57 | 0.5 | 1 | 0.88 | 1 | 66 | 215 | 0.716
70-MV-011 | 30 | MV Power | ACC fan transformer LVT-ACC | MVS-1 | Main 13.8 kV switchboard (main electrical building) | LVT-ACC | ACC fan transformer 13.8/0.48 kV 3 MVA | MV-3C-1/0 | 15 kV MV-105 3/C 1/0 AWG Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-02 | M |  | 151 | 495 | 151 | 495 | 13800 | 3 | 3000 | 1 | 125.5109 | 1.25 | 156.8887 | 189.2 | 189.2 | 82.92% | 0.09833% | 3% | OK | 3421.1944 |  | 36 | 52 | 0.5 | 146 | 40 | 0.5 | 5 | 0.88 | 1 | 66 | 215 | 0.716
70-MV-012 | 60 | MV Power | Gas station transformer LVT-GAS | MVS-1 | Main 13.8 kV switchboard (main electrical building) | LVT-GAS | Gas station transformer 13.8/0.48 kV 1.6 MVA | MV-3C-2 | 15 kV MV-105 3/C #2 AWG Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-03 | M |  | 109 | 358 | 109 | 358 | 13800 | 3 | 1600 | 1 | 66.9392 | 1.25 | 83.674 | 145.2 | 145.2 | 57.63% | 0.05647% | 3% | OK | 2922.4666 |  | 36 | 52 | 0.5 | -12 | 16 | 0.5 | 5 | 0.88 | 1 | 61 | 165 | 1.068
70-MV-013 | 60 | MV Power | BOG compressor motor | MVS-1 | Main 13.8 kV switchboard (main electrical building) | C-BOG | Boil-off gas compressor motor 900 kW, 13.8 kV | MV-3C-2 | 15 kV MV-105 3/C #2 AWG Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-03 | M |  | 135 | 443 | 135 | 443 | 13800 | 3 | 900 | 0.82 | 45.9186 | 1.25 | 57.3983 | 145.2 | 145.2 | 39.53% | 0.04797% | 3% | OK | 2922.4666 | Class I Div 2 - MC-HL with listed Class I fittings (NEC 501.10) | 36 | 52 | 0.5 | -45 | 25 | 0.5 | 5 | 0.88 | 1 | 61 | 165 | 1.068
70-MV-014 | 50 | MV Power | RICE black-start / island tie to MVS-1 | MVS-RICE | RICE 13.8 kV collector switchgear e-house | MVS-1 | Main 13.8 kV switchboard (main electrical building) | MV-1C-500-TPX | 15 kV MV-105 1/C 500 kcmil Cu EPR 133% shielded, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt, triplexed set | 2 | DB-02 | M |  | 88 | 289 | 528 | 1732 | 13800 | 3 | 10000 | 1 | 418.3698 | 1 | 418.3698 | 409.5 | 819 | 51.08% | 0.03415% | 3% | OK | 7921.5259 |  | 12 | 99 | 0.5 | 36 | 52 | 0.5 | -1.2 | 0.7 | 3 | 41 | 585 | 0.256
40-MV-001 | 40 | MV Power | Flue gas booster fan | MVS-CCS | CCS 13.8 kV switchboard (CCS substation) | M-BF | Flue gas booster fan motor 6.5 MW, 13.8 kV | MV-1C-500-TPX | 15 kV MV-105 1/C 500 kcmil Cu EPR 133% shielded, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt, triplexed set | 1 | TR-05 | M |  | 118 | 387 | 354 | 1161 | 13800 | 3 | 6500 | 0.86 | 316.2097 | 1.25 | 395.2621 | 514.8 | 514.8 | 76.78% | 0.06922% | 3% | OK | 3960.7629 | Across-the-line start - check voltage dip | 178 | 58 | 0.5 | 150 | -4 | 0.5 | 6 | 0.88 | 3 | 41 | 585 | 0.256
40-MV-002 | 40 | MV Power | CO2 compressor VFD line side | MVS-CCS | CCS 13.8 kV switchboard (CCS substation) | VFD-CO2 | CO2 compressor MV variable frequency drive, 13.8 kV in / out | MV-1C-750-TPX | 15 kV MV-105 1/C 750 kcmil Cu EPR 133% shielded, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt, triplexed set | 2 | TR-05 | M |  | 47 | 154 | 282 | 925 | 13800 | 3 | 14000 | 0.9 | 650.7974 | 1.25 | 813.4968 | 651.2 | 1302.4 | 62.46% | 0.02327% | 3% | OK | 9971.4151 | Input transformer integral to VFD | 178 | 58 | 0.5 | 186 | 40 | 0.5 | 6 | 0.88 | 3 | 46 | 740 | 0.21
40-MV-010 | 40 | MV Power | CO2 compressor VFD output to motor | VFD-CO2 | CO2 compressor MV variable frequency drive, 13.8 kV in / out | M-CO2C | CO2 compressor motor 14 MW, 13.8 kV (VFD) | MV-1C-750-TPX | 15 kV MV-105 1/C 750 kcmil Cu EPR 133% shielded, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt, triplexed set | 2 | LOCAL | M |  | 19 | 62 | 114 | 374 | 13800 | 3 | 14000 | 0.9 | 650.7974 | 1.25 | 813.4968 | 651.2 | 1302.4 | 62.46% | 0.009408% | 3% | OK | 9971.4151 | VFD output: shielded, symmetrical triplexed sets; confirm insulation for dv/dt with VFD vendor | 186 | 40 | 0.5 | 195 | 39 | 0.5 | 1 | 0.88 | 3 | 46 | 740 | 0.21
40-MV-003 | 40 | MV Power | Lean amine pump A | MVS-CCS | CCS 13.8 kV switchboard (CCS substation) | M-LAP-A | Lean amine pump A 800 kW, 13.8 kV | MV-3C-2 | 15 kV MV-105 3/C #2 AWG Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-05 | M |  | 78 | 256 | 78 | 256 | 13800 | 3 | 800 | 0.84 | 39.8447 | 1.25 | 49.8059 | 145.2 | 145.2 | 34.3% | 0.02405% | 3% | OK | 2922.4666 |  | 178 | 58 | 0.5 | 186 | 12 | 0.5 | 6 | 0.88 | 1 | 61 | 165 | 1.068
40-MV-004 | 40 | MV Power | Lean amine pump B | MVS-CCS | CCS 13.8 kV switchboard (CCS substation) | M-LAP-B | Lean amine pump B 800 kW, 13.8 kV | MV-3C-2 | 15 kV MV-105 3/C #2 AWG Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-05 | M |  | 75 | 246 | 75 | 246 | 13800 | 3 | 800 | 0.84 | 39.8447 | 1.25 | 49.8059 | 145.2 | 145.2 | 34.3% | 0.02313% | 3% | OK | 2922.4666 |  | 178 | 58 | 0.5 | 186 | 15 | 0.5 | 6 | 0.88 | 1 | 61 | 165 | 1.068
40-MV-005 | 40 | MV Power | Rich amine pump A | MVS-CCS | CCS 13.8 kV switchboard (CCS substation) | M-RAP-A | Rich amine pump A 700 kW, 13.8 kV | MV-3C-2 | 15 kV MV-105 3/C #2 AWG Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-05 | M |  | 69 | 226 | 69 | 226 | 13800 | 3 | 700 | 0.84 | 34.8641 | 1.25 | 43.5802 | 145.2 | 145.2 | 30.01% | 0.01862% | 3% | OK | 2922.4666 |  | 178 | 58 | 0.5 | 174 | 16 | 0.5 | 6 | 0.88 | 1 | 61 | 165 | 1.068
40-MV-006 | 40 | MV Power | Rich amine pump B | MVS-CCS | CCS 13.8 kV switchboard (CCS substation) | M-RAP-B | Rich amine pump B 700 kW, 13.8 kV | MV-3C-2 | 15 kV MV-105 3/C #2 AWG Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-05 | M |  | 66 | 217 | 66 | 217 | 13800 | 3 | 700 | 0.84 | 34.8641 | 1.25 | 43.5802 | 145.2 | 145.2 | 30.01% | 0.01781% | 3% | OK | 2922.4666 |  | 178 | 58 | 0.5 | 177 | 16 | 0.5 | 6 | 0.88 | 1 | 61 | 165 | 1.068
40-MV-007 | 40 | MV Power | DCC circulation pump A | MVS-CCS | CCS 13.8 kV switchboard (CCS substation) | M-DCC-A | Direct contact cooler circulation pump A 400 kW, 13.8 kV | MV-3C-2 | 15 kV MV-105 3/C #2 AWG Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-05 | M |  | 111 | 364 | 111 | 364 | 13800 | 3 | 400 | 0.82 | 20.4083 | 1.25 | 25.5104 | 145.2 | 145.2 | 17.57% | 0.01753% | 3% | OK | 2922.4666 |  | 178 | 58 | 0.5 | 146 | 6 | 0.5 | 6 | 0.88 | 1 | 61 | 165 | 1.068
40-MV-008 | 40 | MV Power | DCC circulation pump B | MVS-CCS | CCS 13.8 kV switchboard (CCS substation) | M-DCC-B | Direct contact cooler circulation pump B 400 kW, 13.8 kV | MV-3C-2 | 15 kV MV-105 3/C #2 AWG Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-05 | M |  | 108 | 354 | 108 | 354 | 13800 | 3 | 400 | 0.82 | 20.4083 | 1.25 | 25.5104 | 145.2 | 145.2 | 17.57% | 0.01706% | 3% | OK | 2922.4666 |  | 178 | 58 | 0.5 | 146 | 9 | 0.5 | 6 | 0.88 | 1 | 61 | 165 | 1.068
40-MV-009 | 40 | MV Power | CCS LV transformer LVT-CCS | MVS-CCS | CCS 13.8 kV switchboard (CCS substation) | LVT-CCS | CCS LV transformer 13.8/0.48 kV 2.5 MVA | MV-3C-1/0 | 15 kV MV-105 3/C 1/0 AWG Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | LOCAL | M |  | 14 | 46 | 14 | 46 | 13800 | 3 | 2500 | 1 | 104.5924 | 1.25 | 130.7406 | 189.2 | 189.2 | 69.1% | 0.007597% | 3% | OK | 3421.1944 |  | 178 | 58 | 0.5 | 182 | 60 | 0.5 | 1 | 0.88 | 1 | 66 | 215 | 0.716
50-MV-001 | 50 | MV Power | Genset 1 to collector switchgear | GEN-R01 | Gas engine genset 1 (40 ft container) 2.5 MVA, 13.8 kV - terminal box | MVS-RICE | RICE 13.8 kV collector switchgear e-house | MV-3C-2 | 15 kV MV-105 3/C #2 AWG Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-04 | M |  | 52 | 171 | 52 | 171 | 13800 | 3 | 2500 | 1 | 104.5924 | 1.15 | 120.2813 | 145.2 | 145.2 | 82.84% | 0.04209% | 3% | OK | 2922.4666 | Generator: 115% (NEC 445.13); load in kVA | 2.2 | 71.45 | 1.5 | 12 | 99 | 0.5 | 3 | 0.88 | 1 | 61 | 165 | 1.068
50-MV-002 | 50 | MV Power | Genset 2 to collector switchgear | GEN-R02 | Gas engine genset 2 (40 ft container) 2.5 MVA, 13.8 kV - terminal box | MVS-RICE | RICE 13.8 kV collector switchgear e-house | MV-3C-2 | 15 kV MV-105 3/C #2 AWG Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-04 | M |  | 47 | 154 | 47 | 154 | 13800 | 3 | 2500 | 1 | 104.5924 | 1.15 | 120.2813 | 145.2 | 145.2 | 82.84% | 0.03804% | 3% | OK | 2922.4666 | Generator: 115% (NEC 445.13); load in kVA | 2.2 | 75.65 | 1.5 | 12 | 99 | 0.5 | 3 | 0.88 | 1 | 61 | 165 | 1.068
50-MV-003 | 50 | MV Power | Genset 3 to collector switchgear | GEN-R03 | Gas engine genset 3 (40 ft container) 2.5 MVA, 13.8 kV - terminal box | MVS-RICE | RICE 13.8 kV collector switchgear e-house | MV-3C-2 | 15 kV MV-105 3/C #2 AWG Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-04 | M |  | 43 | 141 | 43 | 141 | 13800 | 3 | 2500 | 1 | 104.5924 | 1.15 | 120.2813 | 145.2 | 145.2 | 82.84% | 0.03481% | 3% | OK | 2922.4666 | Generator: 115% (NEC 445.13); load in kVA | 2.2 | 79.85 | 1.5 | 12 | 99 | 0.5 | 3 | 0.88 | 1 | 61 | 165 | 1.068
50-MV-004 | 50 | MV Power | Genset 4 to collector switchgear | GEN-R04 | Gas engine genset 4 (40 ft container) 2.5 MVA, 13.8 kV - terminal box | MVS-RICE | RICE 13.8 kV collector switchgear e-house | MV-3C-2 | 15 kV MV-105 3/C #2 AWG Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-04 | M |  | 38 | 125 | 38 | 125 | 13800 | 3 | 2500 | 1 | 104.5924 | 1.15 | 120.2813 | 145.2 | 145.2 | 82.84% | 0.03076% | 3% | OK | 2922.4666 | Generator: 115% (NEC 445.13); load in kVA | 2.2 | 84.05 | 1.5 | 12 | 99 | 0.5 | 3 | 0.88 | 1 | 61 | 165 | 1.068
50-MV-005 | 50 | MV Power | Genset 5 to collector switchgear | GEN-R05 | Gas engine genset 5 (40 ft container) 2.5 MVA, 13.8 kV - terminal box | MVS-RICE | RICE 13.8 kV collector switchgear e-house | MV-3C-2 | 15 kV MV-105 3/C #2 AWG Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-04 | M |  | 34 | 112 | 34 | 112 | 13800 | 3 | 2500 | 1 | 104.5924 | 1.15 | 120.2813 | 145.2 | 145.2 | 82.84% | 0.02752% | 3% | OK | 2922.4666 | Generator: 115% (NEC 445.13); load in kVA | 2.2 | 88.25 | 1.5 | 12 | 99 | 0.5 | 3 | 0.88 | 1 | 61 | 165 | 1.068
50-MV-006 | 50 | MV Power | Genset 6 to collector switchgear | GEN-R06 | Gas engine genset 6 (40 ft container) 2.5 MVA, 13.8 kV - terminal box | MVS-RICE | RICE 13.8 kV collector switchgear e-house | MV-3C-2 | 15 kV MV-105 3/C #2 AWG Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-04 | M |  | 29 | 95 | 29 | 95 | 13800 | 3 | 2500 | 1 | 104.5924 | 1.15 | 120.2813 | 145.2 | 145.2 | 82.84% | 0.02347% | 3% | OK | 2922.4666 | Generator: 115% (NEC 445.13); load in kVA | 2.2 | 92.45 | 1.5 | 12 | 99 | 0.5 | 3 | 0.88 | 1 | 61 | 165 | 1.068
50-MV-007 | 50 | MV Power | Genset 7 to collector switchgear | GEN-R07 | Gas engine genset 7 (40 ft container) 2.5 MVA, 13.8 kV - terminal box | MVS-RICE | RICE 13.8 kV collector switchgear e-house | MV-3C-2 | 15 kV MV-105 3/C #2 AWG Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-04 | M |  | 24 | 79 | 24 | 79 | 13800 | 3 | 2500 | 1 | 104.5924 | 1.15 | 120.2813 | 145.2 | 145.2 | 82.84% | 0.01943% | 3% | OK | 2922.4666 | Generator: 115% (NEC 445.13); load in kVA | 2.2 | 96.65 | 1.5 | 12 | 99 | 0.5 | 3 | 0.88 | 1 | 61 | 165 | 1.068
50-MV-008 | 50 | MV Power | Genset 8 to collector switchgear | GEN-R08 | Gas engine genset 8 (40 ft container) 2.5 MVA, 13.8 kV - terminal box | MVS-RICE | RICE 13.8 kV collector switchgear e-house | MV-3C-2 | 15 kV MV-105 3/C #2 AWG Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-04 | M |  | 24 | 79 | 24 | 79 | 13800 | 3 | 2500 | 1 | 104.5924 | 1.15 | 120.2813 | 145.2 | 145.2 | 82.84% | 0.01943% | 3% | OK | 2922.4666 | Generator: 115% (NEC 445.13); load in kVA | 2.2 | 100.85 | 1.5 | 12 | 99 | 0.5 | 3 | 0.88 | 1 | 61 | 165 | 1.068
50-MV-009 | 50 | MV Power | Collector switchgear to RICE step-up transformer LV | MVS-RICE | RICE 13.8 kV collector switchgear e-house | RICE-TX-LV | RICE step-up transformer 13.8/230 kV 22 MVA - LV cable box | MV-1C-750-TPX | 15 kV MV-105 1/C 750 kcmil Cu EPR 133% shielded, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt, triplexed set | 2 | LOCAL | M |  | 20 | 66 | 120 | 394 | 13800 | 3 | 22000 | 1 | 920.4135 | 1 | 920.4135 | 651.2 | 1302.4 | 70.67% | 0.01401% | 3% | OK | 9971.4151 | 2 triplexed sets | 12 | 99 | 0.5 | 14.5 | 107.5 | 2 | 1 | 0.88 | 3 | 46 | 740 | 0.21
50-MV-010 | 50 | MV Power | RICE auxiliary transformer LVT-RICE | MVS-RICE | RICE 13.8 kV collector switchgear e-house | LVT-RICE | RICE auxiliary transformer 13.8/0.48 kV 1 MVA | MV-3C-2 | 15 kV MV-105 3/C #2 AWG Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | LOCAL | M |  | 15 | 49 | 15 | 49 | 13800 | 3 | 1000 | 1 | 41.837 | 1.25 | 52.2962 | 145.2 | 145.2 | 36.02% | 0.004857% | 3% | OK | 2922.4666 |  | 12 | 99 | 0.5 | 10 | 104 | 0.5 | 1 | 0.88 | 1 | 61 | 165 | 1.068
70-BD-001 | 70 | Busduct | LVT-1 to PMCC-1 main | LVT-1 | Main LV transformer 13.8/0.48 kV 2.5 MVA | PMCC-1 | Main power / motor control centre 480 V | LVBD-4000 | 600 V busway 4000 A, Cu, 3-ph + ground, outdoor feeder | 1 | BD | M |  | 28 | 92 | 28 | 92 | 480 | 3 | 2500 | 1 | 3007.0327 | 1 | 3007.0327 | 4000 | 4000 | 75.18% |  |  | OK |  |  | 34 | 57 | 0.5 | 44 | 52 | 0.5 | 3 | 1 | 1 |  | 4000
30-BD-001 | 30 | Busduct | LVT-ACC to ACC VFD switchboard | LVT-ACC | ACC fan transformer 13.8/0.48 kV 3 MVA | MCC-ACC | ACC fan VFD switchroom 480 V | LVBD-4000 | 600 V busway 4000 A, Cu, 3-ph + ground, outdoor feeder | 1 | BD | M |  | 19 | 62 | 19 | 62 | 480 | 3 | 3000 | 1 | 3608.4392 | 1 | 3608.4392 | 4000 | 4000 | 90.21% |  |  | OK |  |  | 146 | 40 | 0.5 | 146 | 46 | 0.5 | 3 | 1 | 1 |  | 4000
60-BD-001 | 60 | Busduct | LVT-GAS to gas station MCC | LVT-GAS | Gas station transformer 13.8/0.48 kV 1.6 MVA | MCC-GAS | Gas station MCC 480 V (shelter) | LVBD-2500 | 600 V busway 2500 A, Cu, 3-ph + ground, outdoor feeder | 1 | BD | M |  | 25 | 82 | 25 | 82 | 480 | 3 | 1600 | 1 | 1924.5009 | 1 | 1924.5009 | 2500 | 2500 | 76.98% |  |  | OK |  |  | -12 | 16 | 0.5 | -20 | 12 | 0.5 | 3 | 1 | 1 |  | 2500
40-BD-001 | 40 | Busduct | LVT-CCS to PMCC-CCS | LVT-CCS | CCS LV transformer 13.8/0.48 kV 2.5 MVA | PMCC-CCS | CCS power / motor control centre 480 V | LVBD-4000 | 600 V busway 4000 A, Cu, 3-ph + ground, outdoor feeder | 1 | BD | M |  | 19 | 62 | 19 | 62 | 480 | 3 | 2500 | 1 | 3007.0327 | 1 | 3007.0327 | 4000 | 4000 | 75.18% |  |  | OK |  |  | 182 | 60 | 0.5 | 176 | 60 | 0.5 | 3 | 1 | 1 |  | 4000
50-BD-001 | 50 | Busduct | LVT-RICE to RICE MCC | LVT-RICE | RICE auxiliary transformer 13.8/0.48 kV 1 MVA | MCC-RICE | RICE auxiliary MCC 480 V | LVBD-2500 | 600 V busway 2500 A, Cu, 3-ph + ground, outdoor feeder | 1 | BD | M |  | 24 | 79 | 24 | 79 | 480 | 3 | 1000 | 1 | 1202.8131 | 1 | 1202.8131 | 2500 | 2500 | 48.11% |  |  | OK |  |  | 10 | 104 | 0.5 | 16 | 99 | 0.5 | 3 | 1 | 1 |  | 2500
70-LV-001 | 20 | LV Power | PMCC-1 to GT auxiliary MCC | PMCC-1 | Main power / motor control centre 480 V | MCC-GT | GT auxiliary MCC 480 V (in PEECC) | LV-3C-500 | 600 V 3/C 500 kcmil + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 2 | TR-01 | M |  | 85 | 279 | 170 | 558 | 480 | 3 | 350 | 1 | 420.9846 | 1.25 | 526.2307 | 334.4 | 668.8 | 78.68% | 0.8275% | 3% | OK | 6842.3888 | Load in kVA; 125% continuous (NEC 215.2) | 44 | 52 | 0.5 | 48 | -6 | 0.5 | 5 | 0.88 | 1 | 66 | 380 | 0.222
70-LV-002 | 20 | LV Power | PMCC-1 to HRSG auxiliary MCC | PMCC-1 | Main power / motor control centre 480 V | MCC-HRSG | HRSG auxiliary MCC 480 V | LV-3C-350 | 600 V 3/C 350 kcmil + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 2 | TR-01 | M |  | 123 | 404 | 246 | 807 | 480 | 3 | 250 | 1 | 300.7033 | 1.25 | 375.8791 | 272.8 | 545.6 | 68.89% | 1.052% | 3% | OK | 5103.5173 |  | 44 | 52 | 0.5 | 80 | -9 | 0.5 | 5 | 0.88 | 1 | 57 | 310 | 0.273
70-LV-003 | 20 | LV Power | PMCC-1 to ST auxiliary MCC | PMCC-1 | Main power / motor control centre 480 V | MCC-ST | ST auxiliary MCC 480 V | LV-3C-500 | 600 V 3/C 500 kcmil + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 2 | TR-02 | M |  | 89 | 292 | 178 | 584 | 480 | 3 | 300 | 1 | 360.8439 | 1.25 | 451.0549 | 334.4 | 668.8 | 67.44% | 0.7427% | 3% | OK | 6842.3888 |  | 44 | 52 | 0.5 | 88 | 30 | 0.5 | 5 | 0.88 | 1 | 66 | 380 | 0.222
70-LV-004 | 70 | LV Power | PMCC-1 to UPS-1 rectifier | PMCC-1 | Main power / motor control centre 480 V | UPS-1 | 230 V AC UPS | LV-3C-1/0 | 600 V 3/C 1/0 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | LOCAL | M |  | 12 | 39 | 12 | 39 | 480 | 3 | 80 | 1 | 96.225 | 1.25 | 120.2813 | 132 | 132 | 91.12% | 0.1641% | 3% | OK | 1075.2101 |  | 44 | 52 | 0.5 | 43 | 55 | 0.5 | 1 | 0.88 | 1 | 37 | 150 | 0.682
70-LV-005 | 70 | LV Power | PMCC-1 to 125 V DC chargers | PMCC-1 | Main power / motor control centre 480 V | DCB-1 | 125 V DC battery and chargers | LV-3C-2 | 600 V 3/C #2 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | LOCAL | M |  | 13 | 43 | 13 | 43 | 480 | 3 | 60 | 1 | 72.1688 | 1.25 | 90.211 | 101.2 | 101.2 | 89.14% | 0.2111% | 3% | OK | 754.7676 |  | 44 | 52 | 0.5 | 42 | 55 | 0.5 | 1 | 0.88 | 1 | 31 | 115 | 1.08
70-LV-006 | 10 | LV Power | PMCC-1 to switchyard relay bldg panelboard | PMCC-1 | Main power / motor control centre 480 V | SWY-RB | Switchyard relay & control building | LV-3C-4/0 | 600 V 3/C 4/0 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | DB-01 | M |  | 150 | 492 | 150 | 492 | 480 | 3 | 100 | 1 | 120.2813 | 1.25 | 150.3516 | 161 | 161 | 93.39% | 1.473% | 3% | OK | 1734.9445 | Relay bldg has its own 125 V DC battery | 44 | 52 | 0.5 | 95 | 128 | 0.5 | -1.2 | 0.7 | 1 | 47 | 230 | 0.392
70-LV-007 | 20 | LV Power | PMCC-1 to CEMS shelter | PMCC-1 | Main power / motor control centre 480 V | CEMS-SH | CEMS analyser shelter | LV-3C-6 | 600 V 3/C #6 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-02 | M |  | 168 | 551 | 168 | 551 | 480 | 3 | 20 | 1 | 24.0563 | 1.25 | 30.0703 | 57.2 | 57.2 | 52.57% | 2.153% | 3% | OK | 452.3893 |  | 44 | 52 | 0.5 | 122 | -8 | 0.5 | 5 | 0.88 | 1 | 24 | 65 | 2.557
20-LV-001 | 20 | LV Power | GT AC lube oil pump | MCC-GT | GT auxiliary MCC 480 V (in PEECC) | M-GT-LOP | GT AC lube oil pump motor 75 kW | LV-3C-4/0 | 600 V 3/C 4/0 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | LOCAL | M |  | 22 | 72 | 22 | 72 | 480 | 3 | 75 | 0.8 | 112.7637 | 1.25 | 140.9547 | 202.4 | 202.4 | 69.64% | 0.2026% | 3% | OK | 1734.9445 | Motor: 125% FLC (NEC 430.22) | 48 | -6 | 0.5 | 60 | -5 | 0.5 | 1 | 0.88 | 1 | 47 | 230 | 0.392
20-LV-002 | 20 | LV Power | GT enclosure vent fan A | MCC-GT | GT auxiliary MCC 480 V (in PEECC) | M-GT-VNT-A | GT enclosure ventilation fan A 45 kW | LV-3C-2 | 600 V 3/C #2 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | LOCAL | M |  | 36 | 118 | 36 | 118 | 480 | 3 | 45 | 0.8 | 67.6582 | 1.25 | 84.5728 | 101.2 | 101.2 | 83.57% | 0.548% | 3% | OK | 754.7676 |  | 48 | -6 | 0.5 | 52 | 6.5 | 11 | 1 | 0.88 | 1 | 31 | 115 | 1.08
20-LV-003 | 20 | LV Power | GT enclosure vent fan B | MCC-GT | GT auxiliary MCC 480 V (in PEECC) | M-GT-VNT-B | GT enclosure ventilation fan B 45 kW | LV-3C-2 | 600 V 3/C #2 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | LOCAL | M |  | 45 | 148 | 45 | 148 | 480 | 3 | 45 | 0.8 | 67.6582 | 1.25 | 84.5728 | 101.2 | 101.2 | 83.57% | 0.685% | 3% | OK | 754.7676 |  | 48 | -6 | 0.5 | 60 | 6.5 | 11 | 1 | 0.88 | 1 | 31 | 115 | 1.08
20-LV-004 | 20 | LV Power | HRSG recirculation pump | MCC-HRSG | HRSG auxiliary MCC 480 V | M-HRSG-RCP | HRSG preheater recirculation pump motor 55 kW | LV-3C-1/0 | 600 V 3/C 1/0 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | LOCAL | M |  | 31 | 102 | 31 | 102 | 480 | 3 | 55 | 0.8 | 82.6934 | 1.25 | 103.3667 | 132 | 132 | 78.31% | 0.3642% | 3% | OK | 1075.2101 |  | 80 | -9 | 0.5 | 100 | -8 | 0.5 | 1 | 0.88 | 1 | 37 | 150 | 0.682
20-LV-005 | 20 | LV Power | ST turning gear | MCC-ST | ST auxiliary MCC 480 V | M-ST-TG | ST turning gear motor 37 kW | LV-3C-2 | 600 V 3/C #2 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | LOCAL | M |  | 43 | 141 | 43 | 141 | 480 | 3 | 37 | 0.78 | 57.0565 | 1.25 | 71.3206 | 101.2 | 101.2 | 70.47% | 0.552% | 3% | OK | 754.7676 |  | 88 | 30 | 0.5 | 66 | 36 | 6 | 1 | 0.88 | 1 | 31 | 115 | 1.08
20-LV-006 | 20 | LV Power | ST AC lube oil pump | MCC-ST | ST auxiliary MCC 480 V | M-ST-LOP | ST AC lube oil pump motor 55 kW | LV-3C-1/0 | 600 V 3/C 1/0 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | LOCAL | M |  | 27 | 89 | 27 | 89 | 480 | 3 | 55 | 0.8 | 82.6934 | 1.25 | 103.3667 | 132 | 132 | 78.31% | 0.3172% | 3% | OK | 1075.2101 |  | 88 | 30 | 0.5 | 70 | 30 | 0.5 | 1 | 0.88 | 1 | 37 | 150 | 0.682
30-LV-001 | 30 | LV Power | ACC fan 01 VFD output to local disconnect | MCC-ACC | ACC fan VFD switchroom 480 V | DS-ACC-01 | ACC fan 01 local disconnect switch (in sight of motor, NEC 430.102) | LV-VFD-500 | 600/1000 V VFD 3/C 500 kcmil + 3 symmetrical G, Cu XLPE, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-06 | M |  | 86 | 282 | 86 | 282 | 480 | 3 | 150 | 0.85 | 212.2611 | 1.25 | 265.3264 | 334.4 | 334.4 | 79.34% | 0.8443% | 3% | OK | 3848.451 | Armor-X type VFD cable, symmetrical grounds | 146 | 46 | 0.5 | 108 | 32 | 20.5 | 20 | 0.88 | 1 | 70 | 380 | 0.222
30-LV-002 | 30 | LV Power | ACC fan 02 VFD output to local disconnect | MCC-ACC | ACC fan VFD switchroom 480 V | DS-ACC-02 | ACC fan 02 local disconnect switch (in sight of motor, NEC 430.102) | LV-VFD-500 | 600/1000 V VFD 3/C 500 kcmil + 3 symmetrical G, Cu XLPE, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-06 | M |  | 74 | 243 | 74 | 243 | 480 | 3 | 150 | 0.85 | 212.2611 | 1.25 | 265.3264 | 334.4 | 334.4 | 79.34% | 0.7265% | 3% | OK | 3848.451 | Armor-X type VFD cable, symmetrical grounds | 146 | 46 | 0.5 | 108 | 43 | 20.5 | 20 | 0.88 | 1 | 70 | 380 | 0.222
30-LV-003 | 30 | LV Power | ACC fan 03 VFD output to local disconnect | MCC-ACC | ACC fan VFD switchroom 480 V | DS-ACC-03 | ACC fan 03 local disconnect switch (in sight of motor, NEC 430.102) | LV-VFD-500 | 600/1000 V VFD 3/C 500 kcmil + 3 symmetrical G, Cu XLPE, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-06 | M |  | 79 | 259 | 79 | 259 | 480 | 3 | 150 | 0.85 | 212.2611 | 1.25 | 265.3264 | 334.4 | 334.4 | 79.34% | 0.7755% | 3% | OK | 3848.451 | Armor-X type VFD cable, symmetrical grounds | 146 | 46 | 0.5 | 108 | 54 | 20.5 | 20 | 0.88 | 1 | 70 | 380 | 0.222
30-LV-004 | 30 | LV Power | ACC fan 04 VFD output to local disconnect | MCC-ACC | ACC fan VFD switchroom 480 V | DS-ACC-04 | ACC fan 04 local disconnect switch (in sight of motor, NEC 430.102) | LV-VFD-500 | 600/1000 V VFD 3/C 500 kcmil + 3 symmetrical G, Cu XLPE, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-06 | M |  | 77 | 253 | 77 | 253 | 480 | 3 | 150 | 0.85 | 212.2611 | 1.25 | 265.3264 | 334.4 | 334.4 | 79.34% | 0.7559% | 3% | OK | 3848.451 | Armor-X type VFD cable, symmetrical grounds | 146 | 46 | 0.5 | 116 | 32 | 20.5 | 20 | 0.88 | 1 | 70 | 380 | 0.222
30-LV-005 | 30 | LV Power | ACC fan 05 VFD output to local disconnect | MCC-ACC | ACC fan VFD switchroom 480 V | DS-ACC-05 | ACC fan 05 local disconnect switch (in sight of motor, NEC 430.102) | LV-VFD-500 | 600/1000 V VFD 3/C 500 kcmil + 3 symmetrical G, Cu XLPE, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-06 | M |  | 65 | 213 | 65 | 213 | 480 | 3 | 150 | 0.85 | 212.2611 | 1.25 | 265.3264 | 334.4 | 334.4 | 79.34% | 0.6381% | 3% | OK | 3848.451 | Armor-X type VFD cable, symmetrical grounds | 146 | 46 | 0.5 | 116 | 43 | 20.5 | 20 | 0.88 | 1 | 70 | 380 | 0.222
30-LV-006 | 30 | LV Power | ACC fan 06 VFD output to local disconnect | MCC-ACC | ACC fan VFD switchroom 480 V | DS-ACC-06 | ACC fan 06 local disconnect switch (in sight of motor, NEC 430.102) | LV-VFD-500 | 600/1000 V VFD 3/C 500 kcmil + 3 symmetrical G, Cu XLPE, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-06 | M |  | 70 | 230 | 70 | 230 | 480 | 3 | 150 | 0.85 | 212.2611 | 1.25 | 265.3264 | 334.4 | 334.4 | 79.34% | 0.6872% | 3% | OK | 3848.451 | Armor-X type VFD cable, symmetrical grounds | 146 | 46 | 0.5 | 116 | 54 | 20.5 | 20 | 0.88 | 1 | 70 | 380 | 0.222
30-LV-007 | 30 | LV Power | ACC fan 07 VFD output to local disconnect | MCC-ACC | ACC fan VFD switchroom 480 V | DS-ACC-07 | ACC fan 07 local disconnect switch (in sight of motor, NEC 430.102) | LV-VFD-500 | 600/1000 V VFD 3/C 500 kcmil + 3 symmetrical G, Cu XLPE, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-06 | M |  | 68 | 223 | 68 | 223 | 480 | 3 | 150 | 0.85 | 212.2611 | 1.25 | 265.3264 | 334.4 | 334.4 | 79.34% | 0.6676% | 3% | OK | 3848.451 | Armor-X type VFD cable, symmetrical grounds | 146 | 46 | 0.5 | 124 | 32 | 20.5 | 20 | 0.88 | 1 | 70 | 380 | 0.222
30-LV-008 | 30 | LV Power | ACC fan 08 VFD output to local disconnect | MCC-ACC | ACC fan VFD switchroom 480 V | DS-ACC-08 | ACC fan 08 local disconnect switch (in sight of motor, NEC 430.102) | LV-VFD-500 | 600/1000 V VFD 3/C 500 kcmil + 3 symmetrical G, Cu XLPE, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-06 | M |  | 56 | 184 | 56 | 184 | 480 | 3 | 150 | 0.85 | 212.2611 | 1.25 | 265.3264 | 334.4 | 334.4 | 79.34% | 0.5498% | 3% | OK | 3848.451 | Armor-X type VFD cable, symmetrical grounds | 146 | 46 | 0.5 | 124 | 43 | 20.5 | 20 | 0.88 | 1 | 70 | 380 | 0.222
30-LV-009 | 30 | LV Power | ACC fan 09 VFD output to local disconnect | MCC-ACC | ACC fan VFD switchroom 480 V | DS-ACC-09 | ACC fan 09 local disconnect switch (in sight of motor, NEC 430.102) | LV-VFD-500 | 600/1000 V VFD 3/C 500 kcmil + 3 symmetrical G, Cu XLPE, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-06 | M |  | 61 | 200 | 61 | 200 | 480 | 3 | 150 | 0.85 | 212.2611 | 1.25 | 265.3264 | 334.4 | 334.4 | 79.34% | 0.5988% | 3% | OK | 3848.451 | Armor-X type VFD cable, symmetrical grounds | 146 | 46 | 0.5 | 124 | 54 | 20.5 | 20 | 0.88 | 1 | 70 | 380 | 0.222
30-LV-010 | 30 | LV Power | ACC fan 10 VFD output to local disconnect | MCC-ACC | ACC fan VFD switchroom 480 V | DS-ACC-10 | ACC fan 10 local disconnect switch (in sight of motor, NEC 430.102) | LV-VFD-500 | 600/1000 V VFD 3/C 500 kcmil + 3 symmetrical G, Cu XLPE, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-06 | M |  | 59 | 194 | 59 | 194 | 480 | 3 | 150 | 0.85 | 212.2611 | 1.25 | 265.3264 | 334.4 | 334.4 | 79.34% | 0.5792% | 3% | OK | 3848.451 | Armor-X type VFD cable, symmetrical grounds | 146 | 46 | 0.5 | 132 | 32 | 20.5 | 20 | 0.88 | 1 | 70 | 380 | 0.222
30-LV-011 | 30 | LV Power | ACC fan 11 VFD output to local disconnect | MCC-ACC | ACC fan VFD switchroom 480 V | DS-ACC-11 | ACC fan 11 local disconnect switch (in sight of motor, NEC 430.102) | LV-VFD-500 | 600/1000 V VFD 3/C 500 kcmil + 3 symmetrical G, Cu XLPE, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-06 | M |  | 47 | 154 | 47 | 154 | 480 | 3 | 150 | 0.85 | 212.2611 | 1.25 | 265.3264 | 334.4 | 334.4 | 79.34% | 0.4614% | 3% | OK | 3848.451 | Armor-X type VFD cable, symmetrical grounds | 146 | 46 | 0.5 | 132 | 43 | 20.5 | 20 | 0.88 | 1 | 70 | 380 | 0.222
30-LV-012 | 30 | LV Power | ACC fan 12 VFD output to local disconnect | MCC-ACC | ACC fan VFD switchroom 480 V | DS-ACC-12 | ACC fan 12 local disconnect switch (in sight of motor, NEC 430.102) | LV-VFD-500 | 600/1000 V VFD 3/C 500 kcmil + 3 symmetrical G, Cu XLPE, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-06 | M |  | 53 | 174 | 53 | 174 | 480 | 3 | 150 | 0.85 | 212.2611 | 1.25 | 265.3264 | 334.4 | 334.4 | 79.34% | 0.5203% | 3% | OK | 3848.451 | Armor-X type VFD cable, symmetrical grounds | 146 | 46 | 0.5 | 132 | 54 | 20.5 | 20 | 0.88 | 1 | 70 | 380 | 0.222
30-LV-013 | 30 | LV Power | ACC fan 13 VFD output to local disconnect | MCC-ACC | ACC fan VFD switchroom 480 V | DS-ACC-13 | ACC fan 13 local disconnect switch (in sight of motor, NEC 430.102) | LV-VFD-500 | 600/1000 V VFD 3/C 500 kcmil + 3 symmetrical G, Cu XLPE, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-06 | M |  | 50 | 164 | 50 | 164 | 480 | 3 | 150 | 0.85 | 212.2611 | 1.25 | 265.3264 | 334.4 | 334.4 | 79.34% | 0.4909% | 3% | OK | 3848.451 | Armor-X type VFD cable, symmetrical grounds | 146 | 46 | 0.5 | 140 | 32 | 20.5 | 20 | 0.88 | 1 | 70 | 380 | 0.222
30-LV-014 | 30 | LV Power | ACC fan 14 VFD output to local disconnect | MCC-ACC | ACC fan VFD switchroom 480 V | DS-ACC-14 | ACC fan 14 local disconnect switch (in sight of motor, NEC 430.102) | LV-VFD-500 | 600/1000 V VFD 3/C 500 kcmil + 3 symmetrical G, Cu XLPE, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-06 | M |  | 38 | 125 | 38 | 125 | 480 | 3 | 150 | 0.85 | 212.2611 | 1.25 | 265.3264 | 334.4 | 334.4 | 79.34% | 0.373% | 3% | OK | 3848.451 | Armor-X type VFD cable, symmetrical grounds | 146 | 46 | 0.5 | 140 | 43 | 20.5 | 20 | 0.88 | 1 | 70 | 380 | 0.222
30-LV-015 | 30 | LV Power | ACC fan 15 VFD output to local disconnect | MCC-ACC | ACC fan VFD switchroom 480 V | DS-ACC-15 | ACC fan 15 local disconnect switch (in sight of motor, NEC 430.102) | LV-VFD-500 | 600/1000 V VFD 3/C 500 kcmil + 3 symmetrical G, Cu XLPE, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-06 | M |  | 44 | 144 | 44 | 144 | 480 | 3 | 150 | 0.85 | 212.2611 | 1.25 | 265.3264 | 334.4 | 334.4 | 79.34% | 0.432% | 3% | OK | 3848.451 | Armor-X type VFD cable, symmetrical grounds | 146 | 46 | 0.5 | 140 | 54 | 20.5 | 20 | 0.88 | 1 | 70 | 380 | 0.222
30-LV-016 | 30 | LV Power | ACC fan 01 disconnect to motor (flexible final drop) | DS-ACC-01 | ACC fan 01 local disconnect switch (in sight of motor, NEC 430.102) | M-ACC-01 | ACC fan motor 01, 150 kW 480 V (VFD) | LV-MFX-2/0 | 1000 V 3/C 2/0 AWG + 3 symmetrical G, flexible tinned Cu XHHW-2, foil + braid shield, TPE jkt, Type TC-ER, NFPA 79 (Machine Flex type) | 2 | LOCAL | M | 6 | 6 | 20 | 12 | 39 | 480 | 3 | 150 | 0.85 | 212.2611 | 1.25 | 265.3264 | 154 | 308 | 86.14% | 0.07535% | 3% | OK | 2268.2299 | Machine Flex type TC-ER VFD cable for vibration; 360 deg shield termination glands | 108 | 32 | 20.5 | 104 | 32 | 20.5 | 1 | 0.88 | 1 | 38 | 175 | 0.568
30-LV-017 | 30 | LV Power | ACC fan 02 disconnect to motor (flexible final drop) | DS-ACC-02 | ACC fan 02 local disconnect switch (in sight of motor, NEC 430.102) | M-ACC-02 | ACC fan motor 02, 150 kW 480 V (VFD) | LV-MFX-2/0 | 1000 V 3/C 2/0 AWG + 3 symmetrical G, flexible tinned Cu XHHW-2, foil + braid shield, TPE jkt, Type TC-ER, NFPA 79 (Machine Flex type) | 2 | LOCAL | M | 6 | 6 | 20 | 12 | 39 | 480 | 3 | 150 | 0.85 | 212.2611 | 1.25 | 265.3264 | 154 | 308 | 86.14% | 0.07535% | 3% | OK | 2268.2299 | Machine Flex type TC-ER VFD cable for vibration; 360 deg shield termination glands | 108 | 43 | 20.5 | 104 | 43 | 20.5 | 1 | 0.88 | 1 | 38 | 175 | 0.568
30-LV-018 | 30 | LV Power | ACC fan 03 disconnect to motor (flexible final drop) | DS-ACC-03 | ACC fan 03 local disconnect switch (in sight of motor, NEC 430.102) | M-ACC-03 | ACC fan motor 03, 150 kW 480 V (VFD) | LV-MFX-2/0 | 1000 V 3/C 2/0 AWG + 3 symmetrical G, flexible tinned Cu XHHW-2, foil + braid shield, TPE jkt, Type TC-ER, NFPA 79 (Machine Flex type) | 2 | LOCAL | M | 6 | 6 | 20 | 12 | 39 | 480 | 3 | 150 | 0.85 | 212.2611 | 1.25 | 265.3264 | 154 | 308 | 86.14% | 0.07535% | 3% | OK | 2268.2299 | Machine Flex type TC-ER VFD cable for vibration; 360 deg shield termination glands | 108 | 54 | 20.5 | 104 | 54 | 20.5 | 1 | 0.88 | 1 | 38 | 175 | 0.568
30-LV-019 | 30 | LV Power | ACC fan 04 disconnect to motor (flexible final drop) | DS-ACC-04 | ACC fan 04 local disconnect switch (in sight of motor, NEC 430.102) | M-ACC-04 | ACC fan motor 04, 150 kW 480 V (VFD) | LV-MFX-2/0 | 1000 V 3/C 2/0 AWG + 3 symmetrical G, flexible tinned Cu XHHW-2, foil + braid shield, TPE jkt, Type TC-ER, NFPA 79 (Machine Flex type) | 2 | LOCAL | M | 6 | 6 | 20 | 12 | 39 | 480 | 3 | 150 | 0.85 | 212.2611 | 1.25 | 265.3264 | 154 | 308 | 86.14% | 0.07535% | 3% | OK | 2268.2299 | Machine Flex type TC-ER VFD cable for vibration; 360 deg shield termination glands | 116 | 32 | 20.5 | 112 | 32 | 20.5 | 1 | 0.88 | 1 | 38 | 175 | 0.568
30-LV-020 | 30 | LV Power | ACC fan 05 disconnect to motor (flexible final drop) | DS-ACC-05 | ACC fan 05 local disconnect switch (in sight of motor, NEC 430.102) | M-ACC-05 | ACC fan motor 05, 150 kW 480 V (VFD) | LV-MFX-2/0 | 1000 V 3/C 2/0 AWG + 3 symmetrical G, flexible tinned Cu XHHW-2, foil + braid shield, TPE jkt, Type TC-ER, NFPA 79 (Machine Flex type) | 2 | LOCAL | M | 6 | 6 | 20 | 12 | 39 | 480 | 3 | 150 | 0.85 | 212.2611 | 1.25 | 265.3264 | 154 | 308 | 86.14% | 0.07535% | 3% | OK | 2268.2299 | Machine Flex type TC-ER VFD cable for vibration; 360 deg shield termination glands | 116 | 43 | 20.5 | 112 | 43 | 20.5 | 1 | 0.88 | 1 | 38 | 175 | 0.568
30-LV-021 | 30 | LV Power | ACC fan 06 disconnect to motor (flexible final drop) | DS-ACC-06 | ACC fan 06 local disconnect switch (in sight of motor, NEC 430.102) | M-ACC-06 | ACC fan motor 06, 150 kW 480 V (VFD) | LV-MFX-2/0 | 1000 V 3/C 2/0 AWG + 3 symmetrical G, flexible tinned Cu XHHW-2, foil + braid shield, TPE jkt, Type TC-ER, NFPA 79 (Machine Flex type) | 2 | LOCAL | M | 6 | 6 | 20 | 12 | 39 | 480 | 3 | 150 | 0.85 | 212.2611 | 1.25 | 265.3264 | 154 | 308 | 86.14% | 0.07535% | 3% | OK | 2268.2299 | Machine Flex type TC-ER VFD cable for vibration; 360 deg shield termination glands | 116 | 54 | 20.5 | 112 | 54 | 20.5 | 1 | 0.88 | 1 | 38 | 175 | 0.568
30-LV-022 | 30 | LV Power | ACC fan 07 disconnect to motor (flexible final drop) | DS-ACC-07 | ACC fan 07 local disconnect switch (in sight of motor, NEC 430.102) | M-ACC-07 | ACC fan motor 07, 150 kW 480 V (VFD) | LV-MFX-2/0 | 1000 V 3/C 2/0 AWG + 3 symmetrical G, flexible tinned Cu XHHW-2, foil + braid shield, TPE jkt, Type TC-ER, NFPA 79 (Machine Flex type) | 2 | LOCAL | M | 6 | 6 | 20 | 12 | 39 | 480 | 3 | 150 | 0.85 | 212.2611 | 1.25 | 265.3264 | 154 | 308 | 86.14% | 0.07535% | 3% | OK | 2268.2299 | Machine Flex type TC-ER VFD cable for vibration; 360 deg shield termination glands | 124 | 32 | 20.5 | 120 | 32 | 20.5 | 1 | 0.88 | 1 | 38 | 175 | 0.568
30-LV-023 | 30 | LV Power | ACC fan 08 disconnect to motor (flexible final drop) | DS-ACC-08 | ACC fan 08 local disconnect switch (in sight of motor, NEC 430.102) | M-ACC-08 | ACC fan motor 08, 150 kW 480 V (VFD) | LV-MFX-2/0 | 1000 V 3/C 2/0 AWG + 3 symmetrical G, flexible tinned Cu XHHW-2, foil + braid shield, TPE jkt, Type TC-ER, NFPA 79 (Machine Flex type) | 2 | LOCAL | M | 6 | 6 | 20 | 12 | 39 | 480 | 3 | 150 | 0.85 | 212.2611 | 1.25 | 265.3264 | 154 | 308 | 86.14% | 0.07535% | 3% | OK | 2268.2299 | Machine Flex type TC-ER VFD cable for vibration; 360 deg shield termination glands | 124 | 43 | 20.5 | 120 | 43 | 20.5 | 1 | 0.88 | 1 | 38 | 175 | 0.568
30-LV-024 | 30 | LV Power | ACC fan 09 disconnect to motor (flexible final drop) | DS-ACC-09 | ACC fan 09 local disconnect switch (in sight of motor, NEC 430.102) | M-ACC-09 | ACC fan motor 09, 150 kW 480 V (VFD) | LV-MFX-2/0 | 1000 V 3/C 2/0 AWG + 3 symmetrical G, flexible tinned Cu XHHW-2, foil + braid shield, TPE jkt, Type TC-ER, NFPA 79 (Machine Flex type) | 2 | LOCAL | M | 6 | 6 | 20 | 12 | 39 | 480 | 3 | 150 | 0.85 | 212.2611 | 1.25 | 265.3264 | 154 | 308 | 86.14% | 0.07535% | 3% | OK | 2268.2299 | Machine Flex type TC-ER VFD cable for vibration; 360 deg shield termination glands | 124 | 54 | 20.5 | 120 | 54 | 20.5 | 1 | 0.88 | 1 | 38 | 175 | 0.568
30-LV-025 | 30 | LV Power | ACC fan 10 disconnect to motor (flexible final drop) | DS-ACC-10 | ACC fan 10 local disconnect switch (in sight of motor, NEC 430.102) | M-ACC-10 | ACC fan motor 10, 150 kW 480 V (VFD) | LV-MFX-2/0 | 1000 V 3/C 2/0 AWG + 3 symmetrical G, flexible tinned Cu XHHW-2, foil + braid shield, TPE jkt, Type TC-ER, NFPA 79 (Machine Flex type) | 2 | LOCAL | M | 6 | 6 | 20 | 12 | 39 | 480 | 3 | 150 | 0.85 | 212.2611 | 1.25 | 265.3264 | 154 | 308 | 86.14% | 0.07535% | 3% | OK | 2268.2299 | Machine Flex type TC-ER VFD cable for vibration; 360 deg shield termination glands | 132 | 32 | 20.5 | 128 | 32 | 20.5 | 1 | 0.88 | 1 | 38 | 175 | 0.568
30-LV-026 | 30 | LV Power | ACC fan 11 disconnect to motor (flexible final drop) | DS-ACC-11 | ACC fan 11 local disconnect switch (in sight of motor, NEC 430.102) | M-ACC-11 | ACC fan motor 11, 150 kW 480 V (VFD) | LV-MFX-2/0 | 1000 V 3/C 2/0 AWG + 3 symmetrical G, flexible tinned Cu XHHW-2, foil + braid shield, TPE jkt, Type TC-ER, NFPA 79 (Machine Flex type) | 2 | LOCAL | M | 6 | 6 | 20 | 12 | 39 | 480 | 3 | 150 | 0.85 | 212.2611 | 1.25 | 265.3264 | 154 | 308 | 86.14% | 0.07535% | 3% | OK | 2268.2299 | Machine Flex type TC-ER VFD cable for vibration; 360 deg shield termination glands | 132 | 43 | 20.5 | 128 | 43 | 20.5 | 1 | 0.88 | 1 | 38 | 175 | 0.568
30-LV-027 | 30 | LV Power | ACC fan 12 disconnect to motor (flexible final drop) | DS-ACC-12 | ACC fan 12 local disconnect switch (in sight of motor, NEC 430.102) | M-ACC-12 | ACC fan motor 12, 150 kW 480 V (VFD) | LV-MFX-2/0 | 1000 V 3/C 2/0 AWG + 3 symmetrical G, flexible tinned Cu XHHW-2, foil + braid shield, TPE jkt, Type TC-ER, NFPA 79 (Machine Flex type) | 2 | LOCAL | M | 6 | 6 | 20 | 12 | 39 | 480 | 3 | 150 | 0.85 | 212.2611 | 1.25 | 265.3264 | 154 | 308 | 86.14% | 0.07535% | 3% | OK | 2268.2299 | Machine Flex type TC-ER VFD cable for vibration; 360 deg shield termination glands | 132 | 54 | 20.5 | 128 | 54 | 20.5 | 1 | 0.88 | 1 | 38 | 175 | 0.568
30-LV-028 | 30 | LV Power | ACC fan 13 disconnect to motor (flexible final drop) | DS-ACC-13 | ACC fan 13 local disconnect switch (in sight of motor, NEC 430.102) | M-ACC-13 | ACC fan motor 13, 150 kW 480 V (VFD) | LV-MFX-2/0 | 1000 V 3/C 2/0 AWG + 3 symmetrical G, flexible tinned Cu XHHW-2, foil + braid shield, TPE jkt, Type TC-ER, NFPA 79 (Machine Flex type) | 2 | LOCAL | M | 6 | 6 | 20 | 12 | 39 | 480 | 3 | 150 | 0.85 | 212.2611 | 1.25 | 265.3264 | 154 | 308 | 86.14% | 0.07535% | 3% | OK | 2268.2299 | Machine Flex type TC-ER VFD cable for vibration; 360 deg shield termination glands | 140 | 32 | 20.5 | 136 | 32 | 20.5 | 1 | 0.88 | 1 | 38 | 175 | 0.568
30-LV-029 | 30 | LV Power | ACC fan 14 disconnect to motor (flexible final drop) | DS-ACC-14 | ACC fan 14 local disconnect switch (in sight of motor, NEC 430.102) | M-ACC-14 | ACC fan motor 14, 150 kW 480 V (VFD) | LV-MFX-2/0 | 1000 V 3/C 2/0 AWG + 3 symmetrical G, flexible tinned Cu XHHW-2, foil + braid shield, TPE jkt, Type TC-ER, NFPA 79 (Machine Flex type) | 2 | LOCAL | M | 6 | 6 | 20 | 12 | 39 | 480 | 3 | 150 | 0.85 | 212.2611 | 1.25 | 265.3264 | 154 | 308 | 86.14% | 0.07535% | 3% | OK | 2268.2299 | Machine Flex type TC-ER VFD cable for vibration; 360 deg shield termination glands | 140 | 43 | 20.5 | 136 | 43 | 20.5 | 1 | 0.88 | 1 | 38 | 175 | 0.568
30-LV-030 | 30 | LV Power | ACC fan 15 disconnect to motor (flexible final drop) | DS-ACC-15 | ACC fan 15 local disconnect switch (in sight of motor, NEC 430.102) | M-ACC-15 | ACC fan motor 15, 150 kW 480 V (VFD) | LV-MFX-2/0 | 1000 V 3/C 2/0 AWG + 3 symmetrical G, flexible tinned Cu XHHW-2, foil + braid shield, TPE jkt, Type TC-ER, NFPA 79 (Machine Flex type) | 2 | LOCAL | M | 6 | 6 | 20 | 12 | 39 | 480 | 3 | 150 | 0.85 | 212.2611 | 1.25 | 265.3264 | 154 | 308 | 86.14% | 0.07535% | 3% | OK | 2268.2299 | Machine Flex type TC-ER VFD cable for vibration; 360 deg shield termination glands | 140 | 54 | 20.5 | 136 | 54 | 20.5 | 1 | 0.88 | 1 | 38 | 175 | 0.568
40-LV-001 | 40 | LV Power | Reboiler condensate pump A | PMCC-CCS | CCS power / motor control centre 480 V | M-RBC-A | Reboiler condensate pump A 110 kW, 480 V | LV-3C-350 | 600 V 3/C 350 kcmil + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-05 | M |  | 85 | 279 | 85 | 279 | 480 | 3 | 110 | 0.82 | 161.353 | 1.25 | 201.6912 | 272.8 | 272.8 | 73.93% | 0.78% | 3% | OK | 2551.7586 |  | 176 | 60 | 0.5 | 200 | 24 | 0.5 | 6 | 0.88 | 1 | 57 | 310 | 0.273
40-LV-002 | 40 | LV Power | CO2 dehydration package | PMCC-CCS | CCS power / motor control centre 480 V | PKG-DEH | CO2 dehydration package (TEG) 250 kVA | LV-3C-350 | 600 V 3/C 350 kcmil + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 2 | TR-05 | M |  | 83 | 272 | 166 | 545 | 480 | 3 | 250 | 1 | 300.7033 | 1.25 | 375.8791 | 272.8 | 545.6 | 68.89% | 0.7098% | 3% | OK | 5103.5173 | Load in kVA | 176 | 60 | 0.5 | 214 | 39 | 0.5 | 6 | 0.88 | 1 | 57 | 310 | 0.273
40-LV-003 | 40 | LV Power | CO2 fiscal meter skid | PMCC-CCS | CCS power / motor control centre 480 V | FC-CO2 | CO2 export fiscal meter skid / flow computer | LV-3C-10 | 600 V 3/C #10 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-05 | M |  | 114 | 374 | 114 | 374 | 480 | 3 | 15 | 1 | 18.0422 | 1.25 | 22.5527 | 30.8 | 30.8 | 73.22% | 2.679% | 3% | OK | 314.1593 |  | 176 | 60 | 0.5 | 242 | 39 | 1 | 6 | 0.88 | 1 | 20 | 35 | 6.251
50-LV-001 | 50 | LV Power | Genset 1 auxiliaries | MCC-RICE | RICE auxiliary MCC 480 V | AUX-R01 | Genset 1 auxiliary panel (radiator fans, pre-lube, jacket heater) | LV-3C-1/0 | 600 V 3/C 1/0 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-04 | M |  | 64 | 210 | 64 | 210 | 480 | 3 | 75 | 1 | 90.211 | 1.25 | 112.7637 | 132 | 132 | 85.43% | 0.8203% | 3% | OK | 1075.2101 | Load in kVA | 16 | 99 | 0.5 | -4 | 71.45 | 1 | 3 | 0.88 | 1 | 37 | 150 | 0.682
50-LV-002 | 50 | LV Power | Genset 2 auxiliaries | MCC-RICE | RICE auxiliary MCC 480 V | AUX-R02 | Genset 2 auxiliary panel (radiator fans, pre-lube, jacket heater) | LV-3C-1/0 | 600 V 3/C 1/0 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-04 | M |  | 59 | 194 | 59 | 194 | 480 | 3 | 75 | 1 | 90.211 | 1.25 | 112.7637 | 132 | 132 | 85.43% | 0.7562% | 3% | OK | 1075.2101 | Load in kVA | 16 | 99 | 0.5 | -4 | 75.65 | 1 | 3 | 0.88 | 1 | 37 | 150 | 0.682
50-LV-003 | 50 | LV Power | Genset 3 auxiliaries | MCC-RICE | RICE auxiliary MCC 480 V | AUX-R03 | Genset 3 auxiliary panel (radiator fans, pre-lube, jacket heater) | LV-3C-1/0 | 600 V 3/C 1/0 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-04 | M |  | 55 | 180 | 55 | 180 | 480 | 3 | 75 | 1 | 90.211 | 1.25 | 112.7637 | 132 | 132 | 85.43% | 0.705% | 3% | OK | 1075.2101 | Load in kVA | 16 | 99 | 0.5 | -4 | 79.85 | 1 | 3 | 0.88 | 1 | 37 | 150 | 0.682
50-LV-004 | 50 | LV Power | Genset 4 auxiliaries | MCC-RICE | RICE auxiliary MCC 480 V | AUX-R04 | Genset 4 auxiliary panel (radiator fans, pre-lube, jacket heater) | LV-3C-1/0 | 600 V 3/C 1/0 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-04 | M |  | 50 | 164 | 50 | 164 | 480 | 3 | 75 | 1 | 90.211 | 1.25 | 112.7637 | 132 | 132 | 85.43% | 0.6409% | 3% | OK | 1075.2101 | Load in kVA | 16 | 99 | 0.5 | -4 | 84.05 | 1 | 3 | 0.88 | 1 | 37 | 150 | 0.682
50-LV-005 | 50 | LV Power | Genset 5 auxiliaries | MCC-RICE | RICE auxiliary MCC 480 V | AUX-R05 | Genset 5 auxiliary panel (radiator fans, pre-lube, jacket heater) | LV-3C-1/0 | 600 V 3/C 1/0 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-04 | M |  | 45 | 148 | 45 | 148 | 480 | 3 | 75 | 1 | 90.211 | 1.25 | 112.7637 | 132 | 132 | 85.43% | 0.5768% | 3% | OK | 1075.2101 | Load in kVA | 16 | 99 | 0.5 | -4 | 88.25 | 1 | 3 | 0.88 | 1 | 37 | 150 | 0.682
50-LV-006 | 50 | LV Power | Genset 6 auxiliaries | MCC-RICE | RICE auxiliary MCC 480 V | AUX-R06 | Genset 6 auxiliary panel (radiator fans, pre-lube, jacket heater) | LV-3C-1/0 | 600 V 3/C 1/0 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-04 | M |  | 41 | 135 | 41 | 135 | 480 | 3 | 75 | 1 | 90.211 | 1.25 | 112.7637 | 132 | 132 | 85.43% | 0.5255% | 3% | OK | 1075.2101 | Load in kVA | 16 | 99 | 0.5 | -4 | 92.45 | 1 | 3 | 0.88 | 1 | 37 | 150 | 0.682
50-LV-007 | 50 | LV Power | Genset 7 auxiliaries | MCC-RICE | RICE auxiliary MCC 480 V | AUX-R07 | Genset 7 auxiliary panel (radiator fans, pre-lube, jacket heater) | LV-3C-1/0 | 600 V 3/C 1/0 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-04 | M |  | 36 | 118 | 36 | 118 | 480 | 3 | 75 | 1 | 90.211 | 1.25 | 112.7637 | 132 | 132 | 85.43% | 0.4614% | 3% | OK | 1075.2101 | Load in kVA | 16 | 99 | 0.5 | -4 | 96.65 | 1 | 3 | 0.88 | 1 | 37 | 150 | 0.682
50-LV-008 | 50 | LV Power | Genset 8 auxiliaries | MCC-RICE | RICE auxiliary MCC 480 V | AUX-R08 | Genset 8 auxiliary panel (radiator fans, pre-lube, jacket heater) | LV-3C-1/0 | 600 V 3/C 1/0 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-04 | M |  | 35 | 115 | 35 | 115 | 480 | 3 | 75 | 1 | 90.211 | 1.25 | 112.7637 | 132 | 132 | 85.43% | 0.4486% | 3% | OK | 1075.2101 | Load in kVA | 16 | 99 | 0.5 | -4 | 100.85 | 1 | 3 | 0.88 | 1 | 37 | 150 | 0.682
60-LV-001 | 60 | LV Power | Fuel gas electric heater H-101 | MCC-GAS | Gas station MCC 480 V (shelter) | H-101 | Fuel gas electric heater 400 kW | LV-3C-500 | 600 V 3/C 500 kcmil + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 2 | TR-07 | M |  | 41 | 135 | 82 | 269 | 480 | 3 | 400 | 0.98 | 490.9441 | 1.25 | 613.6801 | 334.4 | 668.8 | 91.76% | 0.4655% | 3% | OK | 6842.3888 | Class I Div 2 - MC-HL with listed Class I fittings (NEC 501.10) | -20 | 12 | 0.5 | 2 | 7 | 1.5 | 3 | 0.88 | 1 | 66 | 380 | 0.222
60-LV-002 | 60 | LV Power | LNG in-tank pump 1 | MCC-GAS | Gas station MCC 480 V (shelter) | M-LNG-P1 | LNG in-tank send-out pump 1, 250 kW 480 V (top penetration) | LV-3C-500 | 600 V 3/C 500 kcmil + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 2 | TR-07 | M |  | 79 | 259 | 158 | 518 | 480 | 3 | 250 | 0.84 | 357.9801 | 1.25 | 447.4751 | 334.4 | 668.8 | 66.91% | 0.654% | 3% | OK | 6842.3888 | Class I Div 1 at tank roof - MC-HL with listed Class I fittings (NEC 501.10) | -20 | 12 | 0.5 | -60 | 10 | 24 | 3 | 0.88 | 1 | 66 | 380 | 0.222
60-LV-003 | 60 | LV Power | LNG in-tank pump 2 | MCC-GAS | Gas station MCC 480 V (shelter) | M-LNG-P2 | LNG in-tank send-out pump 2, 250 kW 480 V (top penetration) | LV-3C-500 | 600 V 3/C 500 kcmil + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 2 | TR-07 | M |  | 74 | 243 | 148 | 486 | 480 | 3 | 250 | 0.84 | 357.9801 | 1.25 | 447.4751 | 334.4 | 668.8 | 66.91% | 0.6126% | 3% | OK | 6842.3888 | Class I Div 1 at tank roof - MC-HL with listed Class I fittings (NEC 501.10) | -20 | 12 | 0.5 | -58 | 12 | 24 | 3 | 0.88 | 1 | 66 | 380 | 0.222
60-LV-004 | 60 | LV Power | LNG area heat tracing / lighting panel | MCC-GAS | Gas station MCC 480 V (shelter) | HTP-LNG | Heat tracing / lighting panel - LNG area | LV-3C-2 | 600 V 3/C #2 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-07 | M |  | 45 | 148 | 45 | 148 | 480 | 3 | 60 | 1 | 72.1688 | 1.25 | 90.211 | 101.2 | 101.2 | 89.14% | 0.7307% | 3% | OK | 754.7676 |  | -20 | 12 | 0.5 | -42 | 4 | 0.5 | 3 | 0.88 | 1 | 31 | 115 | 1.08
60-LV-005 | 60 | LV Power | Inlet ESD valve hydraulic power unit | MCC-GAS | Gas station MCC 480 V (shelter) | XV-001 | Station inlet ESD valve (electro-hydraulic actuator) | LV-3C-10 | 600 V 3/C #10 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-07 | M |  | 17 | 56 | 17 | 56 | 480 | 3 | 3 | 0.8 | 4.5105 | 1.25 | 5.6382 | 30.8 | 30.8 | 18.31% | 0.09986% | 3% | OK | 314.1593 | Class I Div 2 - MC-HL with listed Class I fittings (NEC 501.10) | -20 | 12 | 0.5 | -24 | 10 | 4 | 3 | 0.88 | 1 | 20 | 35 | 6.251
60-LV-006 | 60 | LV Power | Gas chromatograph supply (120 V) | MCC-GAS | Gas station MCC 480 V (shelter) | AT-GC | Gas chromatograph (shelter) | LV-2C-10 | 600 V 2/C #10 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | LOCAL | M |  | 10 | 33 | 10 | 33 | 120 | 1 | 2 | 1 | 16.6667 | 1.25 | 20.8333 | 30.8 | 30.8 | 67.64% | 1.13% | 3% | OK | 254.469 |  | -20 | 12 | 0.5 | -22 | 12 | 0.5 | 1 | 0.88 | 1 | 18 | 35 | 8.137
70-DC-001 | 20 | DC Power | GT DC emergency lube oil pump | DCB-1 | 125 V DC battery and chargers | M-GT-ELOP | GT DC emergency lube oil pump motor 15 kW | LV-1C-500 | 600 V 1/C 500 kcmil Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt (+/- pair) | 1 | TR-01 | M |  | 103 | 338 | 206 | 676 | 125 | DC | 15 | 1 | 120 | 1.25 | 150 | 409.2 | 409.2 | 36.66% | 1.671% | 3% | OK | 1815.8406 | Circuit integrity (CI) cable to be considered | 42 | 55 | 0.5 | 61 | -5 | 0.5 | 5 | 0.88 | 2 | 34 | 465 | 0.169
70-DC-002 | 20 | DC Power | ST DC emergency lube oil pump | DCB-1 | 125 V DC battery and chargers | M-ST-ELOP | ST DC emergency lube oil pump motor 22 kW | LV-1C-500 | 600 V 1/C 500 kcmil Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt (+/- pair) | 1 | TR-02 | M |  | 77 | 253 | 154 | 505 | 125 | DC | 22 | 1 | 176 | 1.25 | 220 | 409.2 | 409.2 | 53.76% | 1.832% | 3% | OK | 1815.8406 | Circuit integrity (CI) cable to be considered | 42 | 55 | 0.5 | 72 | 30 | 0.5 | 5 | 0.88 | 2 | 34 | 465 | 0.169
70-DC-003 | 70 | DC Power | 125 V DC trip / closing supply to MVS-1 | DCB-1 | 125 V DC battery and chargers | MVS-1 | Main 13.8 kV switchboard (main electrical building) | LV-2C-10 | 600 V 2/C #10 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | LOCAL | M |  | 17 | 56 | 17 | 56 | 125 | DC | 2 | 1 | 16 | 1.25 | 20 | 30.8 | 30.8 | 64.94% | 1.771% | 3% | OK | 254.469 |  | 42 | 55 | 0.5 | 36 | 52 | 0.5 | 1 | 0.88 | 1 | 18 | 35 | 8.137
70-DC-004 | 20 | DC Power | 125 V DC to GT control / PEECC | DCB-1 | 125 V DC battery and chargers | GTCP | GT control panel (in PEECC) | LV-2C-2 | 600 V 2/C #2 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-01 | M |  | 88 | 289 | 88 | 289 | 125 | DC | 3 | 1 | 24 | 1.25 | 30 | 101.2 | 101.2 | 29.64% | 2.151% | 3% | OK | 615.7522 |  | 42 | 55 | 0.5 | 46 | -6 | 0.5 | 5 | 0.88 | 1 | 28 | 115 | 1.273
70-UP-001 | 70 | DC Power | UPS to DCS servers / CCR (208 V 1-ph) | UPS-1 | 230 V AC UPS | DCS-CCR | DCS servers / central control room | LV-2C-2 | 600 V 2/C #2 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | LOCAL | M |  | 11 | 36 | 11 | 36 | 208 | 1 | 10 | 1 | 48.0769 | 1.25 | 60.0962 | 101.2 | 101.2 | 59.38% | 0.3237% | 3% | OK | 615.7522 |  | 43 | 55 | 0.5 | 40 | 55 | 0.5 | 1 | 0.88 | 1 | 28 | 115 | 1.273
70-UP-002 | 20 | DC Power | UPS to GT control panel (208 V 1-ph) | UPS-1 | 230 V AC UPS | GTCP | GT control panel (in PEECC) | LV-2C-2 | 600 V 2/C #2 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-01 | M |  | 87 | 285 | 87 | 285 | 208 | 1 | 5 | 1 | 24.0385 | 1.25 | 30.0481 | 101.2 | 101.2 | 29.69% | 1.28% | 3% | OK | 615.7522 |  | 43 | 55 | 0.5 | 46 | -6 | 0.5 | 5 | 0.88 | 1 | 28 | 115 | 1.273
70-UP-003 | 20 | DC Power | UPS to ST control panel (208 V 1-ph) | UPS-1 | 230 V AC UPS | TCP-ST | ST control panel | LV-2C-2 | 600 V 2/C #2 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-02 | M |  | 79 | 259 | 79 | 259 | 208 | 1 | 5 | 1 | 24.0385 | 1.25 | 30.0481 | 101.2 | 101.2 | 29.69% | 1.162% | 3% | OK | 615.7522 |  | 43 | 55 | 0.5 | 85 | 40 | 0.5 | 5 | 0.88 | 1 | 28 | 115 | 1.273
70-UP-004 | 20 | DC Power | UPS to power block RIO (208 V 1-ph) | UPS-1 | 230 V AC UPS | RIO-PB | DCS remote I/O cabinet - power block | LV-2C-6 | 600 V 2/C #6 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-01 | M |  | 80 | 262 | 80 | 262 | 208 | 1 | 3 | 1 | 14.4231 | 1.25 | 18.0288 | 57.2 | 57.2 | 31.52% | 1.787% | 3% | OK | 380.1327 |  | 43 | 55 | 0.5 | 68 | 22 | 0.5 | 5 | 0.88 | 1 | 22 | 65 | 3.222
70-UP-005 | 40 | DC Power | UPS to CCS RIO (208 V 1-ph) | UPS-1 | 230 V AC UPS | RIO-CCS | DCS remote I/O cabinet - CCS | LV-2C-2 | 600 V 2/C #2 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-02 | M |  | 164 | 538 | 164 | 538 | 208 | 1 | 5 | 1 | 24.0385 | 1.25 | 30.0481 | 101.2 | 101.2 | 29.69% | 2.413% | 3% | OK | 615.7522 |  | 43 | 55 | 0.5 | 174 | 58 | 0.5 | 5 | 0.88 | 1 | 28 | 115 | 1.273
70-UP-006 | 60 | DC Power | UPS to gas station RIO / flow computer (208 V 1-ph) | UPS-1 | 230 V AC UPS | RIO-GAS | DCS remote I/O cabinet - gas station (shelter) | LV-2C-2 | 600 V 2/C #2 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-03 | M |  | 131 | 430 | 131 | 430 | 208 | 1 | 3 | 1 | 14.4231 | 1.25 | 18.0288 | 101.2 | 101.2 | 17.82% | 1.156% | 3% | OK | 615.7522 |  | 43 | 55 | 0.5 | -18 | 12 | 0.5 | 5 | 0.88 | 1 | 28 | 115 | 1.273
10-CT-001 | 10 | Control | Bay 1 breaker / disconnect switch control & status | SWY-B1 | 230 kV bay 1 - RICE transformer bay (gantry dead-end) | SWY-RB | Switchyard relay & control building | CTL-25C-14 | 600 V 25/C #14 AWG Cu XHHW-2 control, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 2 | TR-08 | M |  | 116 | 381 | 232 | 761 | [12 empty] | n/a | 1145.1105 |  | 20 | 137.5 | 12.5 | 95 | 128 | 0.5 | -0.8 | 0.88 | 1 | 27
10-CT-002 | 10 | Control | Bay 1 CT / CCVT secondaries | SWY-B1 | 230 kV bay 1 - RICE transformer bay (gantry dead-end) | SWY-RB | Switchyard relay & control building | CTL-12C-10 | 600 V 12/C #10 AWG Cu XHHW-2 control (CT circuits), Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 2 | TR-08 | M |  | 116 | 381 | 232 | 761 | [12 empty] | n/a | 1145.1105 | Check CT burden | 20 | 137.5 | 12.5 | 95 | 128 | 0.5 | -0.8 | 0.88 | 1 | 27
10-CT-003 | 10 | Control | Bay 2 breaker / disconnect switch control & status | SWY-B2 | 230 kV bay 2 - bus coupler (gantry dead-end) | SWY-RB | Switchyard relay & control building | CTL-25C-14 | 600 V 25/C #14 AWG Cu XHHW-2 control, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 2 | TR-08 | M |  | 94 | 308 | 188 | 617 | [12 empty] | n/a | 1145.1105 |  | 40 | 137.5 | 12.5 | 95 | 128 | 0.5 | -0.8 | 0.88 | 1 | 27
10-CT-004 | 10 | Control | Bay 2 CT / CCVT secondaries | SWY-B2 | 230 kV bay 2 - bus coupler (gantry dead-end) | SWY-RB | Switchyard relay & control building | CTL-12C-10 | 600 V 12/C #10 AWG Cu XHHW-2 control (CT circuits), Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 2 | TR-08 | M |  | 94 | 308 | 188 | 617 | [12 empty] | n/a | 1145.1105 | Check CT burden | 40 | 137.5 | 12.5 | 95 | 128 | 0.5 | -0.8 | 0.88 | 1 | 27
10-CT-005 | 10 | Control | Bay 3 breaker / disconnect switch control & status | SWY-B3 | 230 kV bay 3 - GT generator bay (gantry dead-end) | SWY-RB | Switchyard relay & control building | CTL-25C-14 | 600 V 25/C #14 AWG Cu XHHW-2 control, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 2 | TR-08 | M |  | 72 | 236 | 144 | 472 | [12 empty] | n/a | 1145.1105 |  | 60 | 137.5 | 12.5 | 95 | 128 | 0.5 | -0.8 | 0.88 | 1 | 27
10-CT-006 | 10 | Control | Bay 3 CT / CCVT secondaries | SWY-B3 | 230 kV bay 3 - GT generator bay (gantry dead-end) | SWY-RB | Switchyard relay & control building | CTL-12C-10 | 600 V 12/C #10 AWG Cu XHHW-2 control (CT circuits), Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 2 | TR-08 | M |  | 72 | 236 | 144 | 472 | [12 empty] | n/a | 1145.1105 | Check CT burden | 60 | 137.5 | 12.5 | 95 | 128 | 0.5 | -0.8 | 0.88 | 1 | 27
10-CT-007 | 10 | Control | Bay 4 breaker / disconnect switch control & status | SWY-B4 | 230 kV bay 4 - ST generator bay / line exit (gantry dead-end) | SWY-RB | Switchyard relay & control building | CTL-25C-14 | 600 V 25/C #14 AWG Cu XHHW-2 control, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 2 | TR-08 | M |  | 50 | 164 | 100 | 328 | [12 empty] | n/a | 1145.1105 |  | 80 | 137.5 | 12.5 | 95 | 128 | 0.5 | -0.8 | 0.88 | 1 | 27
10-CT-008 | 10 | Control | Bay 4 CT / CCVT secondaries | SWY-B4 | 230 kV bay 4 - ST generator bay / line exit (gantry dead-end) | SWY-RB | Switchyard relay & control building | CTL-12C-10 | 600 V 12/C #10 AWG Cu XHHW-2 control (CT circuits), Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 2 | TR-08 | M |  | 50 | 164 | 100 | 328 | [12 empty] | n/a | 1145.1105 | Check CT burden | 80 | 137.5 | 12.5 | 95 | 128 | 0.5 | -0.8 | 0.88 | 1 | 27
20-CT-001 | 20 | Control | GSU-GT protection: CTs, sudden pressure, WTI/OTI, LTC | GSU-GT-LV | GT step-up transformer - LV bushings / marshalling box | GPP | Generator & transformer protection panels | CTL-12C-10 | 600 V 12/C #10 AWG Cu XHHW-2 control (CT circuits), Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 2 | DB-03 | M |  | 38 | 125 | 76 | 249 | [12 empty] | n/a | 1145.1105 |  | 54 | 60 | 4.5 | 38 | 55 | 0.5 | -1.2 | 0.7 | 1 | 27
20-CT-002 | 20 | Control | GSU-GT alarms / cooling control | GSU-GT-LV | GT step-up transformer - LV bushings / marshalling box | GPP | Generator & transformer protection panels | CTL-25C-14 | 600 V 25/C #14 AWG Cu XHHW-2 control, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | DB-03 | M |  | 38 | 125 | 38 | 125 | [12 empty] | n/a | 572.5553 |  | 54 | 60 | 4.5 | 38 | 55 | 0.5 | -1.2 | 0.7 | 1 | 27
20-CT-003 | 20 | Control | GSU-ST protection: CTs, sudden pressure, WTI/OTI, LTC | GSU-ST-LV | ST step-up transformer - LV bushings / marshalling box | GPP | Generator & transformer protection panels | CTL-12C-10 | 600 V 12/C #10 AWG Cu XHHW-2 control (CT circuits), Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 2 | DB-03 | M |  | 60 | 197 | 120 | 394 | [12 empty] | n/a | 1145.1105 |  | 74 | 60 | 4.5 | 38 | 55 | 0.5 | -1.2 | 0.7 | 1 | 27
20-CT-004 | 20 | Control | GSU-ST alarms / cooling control | GSU-ST-LV | ST step-up transformer - LV bushings / marshalling box | GPP | Generator & transformer protection panels | CTL-25C-14 | 600 V 25/C #14 AWG Cu XHHW-2 control, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | DB-03 | M |  | 60 | 197 | 60 | 197 | [12 empty] | n/a | 572.5553 |  | 74 | 60 | 4.5 | 38 | 55 | 0.5 | -1.2 | 0.7 | 1 | 27
20-CT-005 | 20 | Control | UAT-1 protection & alarms | UAT-1 | Unit auxiliary transformer 1, 19/13.8 kV 45 MVA | GPP | Generator & transformer protection panels | CTL-12C-10 | 600 V 12/C #10 AWG Cu XHHW-2 control (CT circuits), Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | DB-03 | M |  | 29 | 95 | 29 | 95 | [12 empty] | n/a | 572.5553 |  | 44 | 64 | 3 | 38 | 55 | 0.5 | -1.2 | 0.7 | 1 | 27
20-CT-006 | 20 | Control | UAT-2 protection & alarms | UAT-2 | Unit auxiliary transformer 2, 18/13.8 kV 30 MVA (feeds CCS) | GPP | Generator & transformer protection panels | CTL-12C-10 | 600 V 12/C #10 AWG Cu XHHW-2 control (CT circuits), Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | DB-03 | M |  | 76 | 249 | 76 | 249 | [12 empty] | n/a | 572.5553 |  | 86 | 64 | 3 | 38 | 55 | 0.5 | -1.2 | 0.7 | 1 | 27
20-CT-007 | 20 | Control | GT generator CT / VT secondaries | GEN-GT | Gas turbine generator ~290 MVA, 19 kV - line terminals | GPP | Generator & transformer protection panels | CTL-12C-10 | 600 V 12/C #10 AWG Cu XHHW-2 control (CT circuits), Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 2 | TR-01 | M |  | 75 | 246 | 150 | 492 | [12 empty] | n/a | 1145.1105 |  | 58 | 18 | 4 | 38 | 55 | 0.5 | 5 | 0.88 | 1 | 27
20-CT-008 | 20 | Control | ST generator CT / VT secondaries | GEN-ST | Steam turbine generator ~175 MVA, 18 kV - line terminals | GPP | Generator & transformer protection panels | CTL-12C-10 | 600 V 12/C #10 AWG Cu XHHW-2 control (CT circuits), Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 2 | TR-02 | M |  | 47 | 154 | 94 | 308 | [12 empty] | n/a | 1145.1105 |  | 60 | 46 | 6 | 38 | 55 | 0.5 | 5 | 0.88 | 1 | 27
50-CT-001 | 50 | Control | RICE transformer protection & alarms | RICE-TX-LV | RICE step-up transformer 13.8/230 kV 22 MVA - LV cable box | RPC | RICE plant controller | CTL-12C-10 | 600 V 12/C #10 AWG Cu XHHW-2 control (CT circuits), Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | LOCAL | M |  | 25 | 82 | 25 | 82 | [12 empty] | n/a | 572.5553 |  | 14.5 | 107.5 | 2 | 8 | 99 | 0.5 | 1 | 0.88 | 1 | 27
70-CT-001 | 70 | Control | MVS-1 hardwired interface to DCS | MVS-1 | Main 13.8 kV switchboard (main electrical building) | DCS-CCR | DCS servers / central control room | CTL-25C-14 | 600 V 25/C #14 AWG Cu XHHW-2 control, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 4 | LOCAL | M |  | 15 | 49 | 60 | 197 | [12 empty] | n/a | 2290.221 |  | 36 | 52 | 0.5 | 40 | 55 | 0.5 | 1 | 0.88 | 1 | 27
20-CT-009 | 20 | Control | GT control to GT aux MCC | GTCP | GT control panel (in PEECC) | MCC-GT | GT auxiliary MCC 480 V (in PEECC) | CTL-25C-14 | 600 V 25/C #14 AWG Cu XHHW-2 control, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 3 | LOCAL | M |  | 10 | 33 | 30 | 98 | [12 empty] | n/a | 1717.6658 |  | 46 | -6 | 0.5 | 48 | -6 | 0.5 | 1 | 0.88 | 1 | 27
20-CT-010 | 20 | Control | GT control to LCI | GTCP | GT control panel (in PEECC) | LCI-GT | GT static starter (LCI) cubicle | CTL-25C-14 | 600 V 25/C #14 AWG Cu XHHW-2 control, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | LOCAL | M |  | 10 | 33 | 10 | 33 | [12 empty] | n/a | 572.5553 |  | 46 | -6 | 0.5 | 44 | -6 | 0.5 | 1 | 0.88 | 1 | 27
60-CT-001 | 60 | Control | Inlet ESD valve solenoids and limit switches | XV-001 | Station inlet ESD valve (electro-hydraulic actuator) | RIO-GAS | DCS remote I/O cabinet - gas station (shelter) | CTL-7C-12 | 600 V 7/C #12 AWG Cu XHHW-2 control, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-07 | M |  | 19 | 62 | 19 | 62 | [12 empty] | n/a | 283.5287 | Class I Div 2 - MC-HL with listed Class I fittings (NEC 501.10) | -24 | 10 | 4 | -18 | 12 | 0.5 | 3 | 0.88 | 1 | 19
40-CT-001 | 40 | Control | CO2 compressor UCP to VFD / CCS switchgear | UCP-CO2 | CO2 compressor unit control panel | MVS-CCS | CCS 13.8 kV switchboard (CCS substation) | CTL-25C-14 | 600 V 25/C #14 AWG Cu XHHW-2 control, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 2 | TR-05 | M |  | 60 | 197 | 120 | 394 | [12 empty] | n/a | 1145.1105 |  | 192 | 34 | 0.5 | 178 | 58 | 0.5 | 6 | 0.88 | 1 | 27
10-FO-001 | 10 | Fibre Optic | Switchyard relay bldg to DCS / SCADA | SWY-RB | Switchyard relay & control building | DCS-CCR | DCS servers / central control room | FO-48SM | 48-fiber single-mode OFCR, interlocked Al armor | 2 | DB-01 | M |  | 151 | 495 | 302 | 991 | [12 empty] | n/a | 692.7212 | Diverse routes recommended | 95 | 128 | 0.5 | 40 | 55 | 0.5 | -1.2 | 0.7 | 1 | 21
10-FO-002 | 10 | Fibre Optic | Generator protection intertrip to switchyard | GPP | Generator & transformer protection panels | SWY-RB | Switchyard relay & control building | FO-24SM | 24-fiber single-mode OFCR, interlocked Al armor | 2 | DB-01 | M |  | 153 | 502 | 306 | 1004 | [12 empty] | n/a | 567.0575 |  | 38 | 55 | 0.5 | 95 | 128 | 0.5 | -1.2 | 0.7 | 1 | 19
20-FO-001 | 20 | Fibre Optic | GT control to DCS | GTCP | GT control panel (in PEECC) | DCS-CCR | DCS servers / central control room | FO-24SM | 24-fiber single-mode OFCR, interlocked Al armor | 2 | TR-01 | M |  | 90 | 295 | 180 | 591 | [12 empty] | n/a | 567.0575 | Redundant pair | 46 | -6 | 0.5 | 40 | 55 | 0.5 | 5 | 0.88 | 1 | 19
20-FO-002 | 20 | Fibre Optic | ST control to DCS | TCP-ST | ST control panel | DCS-CCR | DCS servers / central control room | FO-24SM | 24-fiber single-mode OFCR, interlocked Al armor | 2 | TR-02 | M |  | 82 | 269 | 164 | 538 | [12 empty] | n/a | 567.0575 | Redundant pair | 85 | 40 | 0.5 | 40 | 55 | 0.5 | 5 | 0.88 | 1 | 19
20-FO-003 | 20 | Fibre Optic | Power block RIO to DCS | RIO-PB | DCS remote I/O cabinet - power block | DCS-CCR | DCS servers / central control room | FO-24SM | 24-fiber single-mode OFCR, interlocked Al armor | 2 | TR-01 | M |  | 83 | 272 | 166 | 545 | [12 empty] | n/a | 567.0575 | Redundant pair | 68 | 22 | 0.5 | 40 | 55 | 0.5 | 5 | 0.88 | 1 | 19
20-FO-004 | 20 | Fibre Optic | CEMS shelter to DCS | CEMS-SH | CEMS analyser shelter | DCS-CCR | DCS servers / central control room | FO-24SM | 24-fiber single-mode OFCR, interlocked Al armor | 1 | TR-02 | M |  | 176 | 577 | 176 | 577 | [12 empty] | n/a | 283.5287 |  | 122 | -8 | 0.5 | 40 | 55 | 0.5 | 5 | 0.88 | 1 | 19
30-FO-001 | 30 | Fibre Optic | ACC VFD switchroom to DCS | MCC-ACC | ACC fan VFD switchroom 480 V | DCS-CCR | DCS servers / central control room | FO-24SM | 24-fiber single-mode OFCR, interlocked Al armor | 1 | TR-02 | M |  | 143 | 469 | 143 | 469 | [12 empty] | n/a | 283.5287 |  | 146 | 46 | 0.5 | 40 | 55 | 0.5 | 5 | 0.88 | 1 | 19
40-FO-001 | 40 | Fibre Optic | CCS RIO to DCS | RIO-CCS | DCS remote I/O cabinet - CCS | DCS-CCR | DCS servers / central control room | FO-48SM | 48-fiber single-mode OFCR, interlocked Al armor | 2 | TR-02 | M |  | 167 | 548 | 334 | 1096 | [12 empty] | n/a | 692.7212 | Redundant pair | 174 | 58 | 0.5 | 40 | 55 | 0.5 | 5 | 0.88 | 1 | 21
40-FO-002 | 40 | Fibre Optic | CO2 compressor UCP to CCS RIO | UCP-CO2 | CO2 compressor unit control panel | RIO-CCS | DCS remote I/O cabinet - CCS | FO-24SM | 24-fiber single-mode OFCR, interlocked Al armor | 1 | TR-05 | M |  | 65 | 213 | 65 | 213 | [12 empty] | n/a | 283.5287 |  | 192 | 34 | 0.5 | 174 | 58 | 0.5 | 6 | 0.88 | 1 | 19
50-FO-001 | 50 | Fibre Optic | RICE plant controller to DCS | RPC | RICE plant controller | DCS-CCR | DCS servers / central control room | FO-24SM | 24-fiber single-mode OFCR, interlocked Al armor | 2 | DB-02 | M |  | 94 | 308 | 188 | 617 | [12 empty] | n/a | 567.0575 | Redundant pair | 8 | 99 | 0.5 | 40 | 55 | 0.5 | -1.2 | 0.7 | 1 | 19
60-FO-001 | 60 | Fibre Optic | Gas station RIO to DCS | RIO-GAS | DCS remote I/O cabinet - gas station (shelter) | DCS-CCR | DCS servers / central control room | FO-24SM | 24-fiber single-mode OFCR, interlocked Al armor | 2 | TR-03 | M |  | 127 | 417 | 254 | 833 | [12 empty] | n/a | 567.0575 | Redundant pair | -18 | 12 | 0.5 | 40 | 55 | 0.5 | 5 | 0.88 | 1 | 19
50-CT-002 | 50 | Control | Genset 1 control / sync / protection to RPC | GEN-R01 | Gas engine genset 1 (40 ft container) 2.5 MVA, 13.8 kV - terminal box | RPC | RICE plant controller | CTL-25C-14 | 600 V 25/C #14 AWG Cu XHHW-2 control, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-04 | M |  | 48 | 157 | 48 | 157 | [12 empty] | n/a | 572.5553 | Plus genset LAN on fiber by vendor | 2.2 | 71.45 | 1.5 | 8 | 99 | 0.5 | 3 | 0.88 | 1 | 27
50-CT-003 | 50 | Control | Genset 2 control / sync / protection to RPC | GEN-R02 | Gas engine genset 2 (40 ft container) 2.5 MVA, 13.8 kV - terminal box | RPC | RICE plant controller | CTL-25C-14 | 600 V 25/C #14 AWG Cu XHHW-2 control, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-04 | M |  | 43 | 141 | 43 | 141 | [12 empty] | n/a | 572.5553 | Plus genset LAN on fiber by vendor | 2.2 | 75.65 | 1.5 | 8 | 99 | 0.5 | 3 | 0.88 | 1 | 27
50-CT-004 | 50 | Control | Genset 3 control / sync / protection to RPC | GEN-R03 | Gas engine genset 3 (40 ft container) 2.5 MVA, 13.8 kV - terminal box | RPC | RICE plant controller | CTL-25C-14 | 600 V 25/C #14 AWG Cu XHHW-2 control, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-04 | M |  | 38 | 125 | 38 | 125 | [12 empty] | n/a | 572.5553 | Plus genset LAN on fiber by vendor | 2.2 | 79.85 | 1.5 | 8 | 99 | 0.5 | 3 | 0.88 | 1 | 27
50-CT-005 | 50 | Control | Genset 4 control / sync / protection to RPC | GEN-R04 | Gas engine genset 4 (40 ft container) 2.5 MVA, 13.8 kV - terminal box | RPC | RICE plant controller | CTL-25C-14 | 600 V 25/C #14 AWG Cu XHHW-2 control, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-04 | M |  | 34 | 112 | 34 | 112 | [12 empty] | n/a | 572.5553 | Plus genset LAN on fiber by vendor | 2.2 | 84.05 | 1.5 | 8 | 99 | 0.5 | 3 | 0.88 | 1 | 27
50-CT-006 | 50 | Control | Genset 5 control / sync / protection to RPC | GEN-R05 | Gas engine genset 5 (40 ft container) 2.5 MVA, 13.8 kV - terminal box | RPC | RICE plant controller | CTL-25C-14 | 600 V 25/C #14 AWG Cu XHHW-2 control, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-04 | M |  | 29 | 95 | 29 | 95 | [12 empty] | n/a | 572.5553 | Plus genset LAN on fiber by vendor | 2.2 | 88.25 | 1.5 | 8 | 99 | 0.5 | 3 | 0.88 | 1 | 27
50-CT-007 | 50 | Control | Genset 6 control / sync / protection to RPC | GEN-R06 | Gas engine genset 6 (40 ft container) 2.5 MVA, 13.8 kV - terminal box | RPC | RICE plant controller | CTL-25C-14 | 600 V 25/C #14 AWG Cu XHHW-2 control, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-04 | M |  | 24 | 79 | 24 | 79 | [12 empty] | n/a | 572.5553 | Plus genset LAN on fiber by vendor | 2.2 | 92.45 | 1.5 | 8 | 99 | 0.5 | 3 | 0.88 | 1 | 27
50-CT-008 | 50 | Control | Genset 7 control / sync / protection to RPC | GEN-R07 | Gas engine genset 7 (40 ft container) 2.5 MVA, 13.8 kV - terminal box | RPC | RICE plant controller | CTL-25C-14 | 600 V 25/C #14 AWG Cu XHHW-2 control, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-04 | M |  | 20 | 66 | 20 | 66 | [12 empty] | n/a | 572.5553 | Plus genset LAN on fiber by vendor | 2.2 | 96.65 | 1.5 | 8 | 99 | 0.5 | 3 | 0.88 | 1 | 27
50-CT-009 | 50 | Control | Genset 8 control / sync / protection to RPC | GEN-R08 | Gas engine genset 8 (40 ft container) 2.5 MVA, 13.8 kV - terminal box | RPC | RICE plant controller | CTL-25C-14 | 600 V 25/C #14 AWG Cu XHHW-2 control, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | 1 | TR-04 | M |  | 19 | 62 | 19 | 62 | [12 empty] | n/a | 572.5553 | Plus genset LAN on fiber by vendor | 2.2 | 100.85 | 1.5 | 8 | 99 | 0.5 | 3 | 0.88 | 1 | 27
60-IN-001 | 60 | Instrument | Ultrasonic meter A to flow computer | FT-101A | Ultrasonic gas meter run A | FC-GAS | Fiscal gas flow computer / metering panel (shelter) | INS-2TSP-16 | 300 V 2 TSP #16 AWG, PLTC/ITC-HL, CCW armor, PVC jkt (IS blue) | 1 | TR-07 | M |  | 37 | 121 | 37 | 121 | [12 empty] | n/a | 201.0619 | Custody transfer; intrinsically safe | -7.25 | -3 | 2.2 | -17 | 12 | 0.5 | 3 | 0.88 | 1 | 16
60-IN-002 | 60 | Instrument | Ultrasonic meter B to flow computer | FT-101B | Ultrasonic gas meter run B | FC-GAS | Fiscal gas flow computer / metering panel (shelter) | INS-2TSP-16 | 300 V 2 TSP #16 AWG, PLTC/ITC-HL, CCW armor, PVC jkt (IS blue) | 1 | TR-07 | M |  | 34 | 112 | 34 | 112 | [12 empty] | n/a | 201.0619 | Custody transfer; intrinsically safe | -7.25 | 0 | 2.2 | -17 | 12 | 0.5 | 3 | 0.88 | 1 | 16
60-IN-003 | 60 | Instrument | Ultrasonic meter C to flow computer | FT-101C | Ultrasonic gas meter run C (spare / check) | FC-GAS | Fiscal gas flow computer / metering panel (shelter) | INS-2TSP-16 | 300 V 2 TSP #16 AWG, PLTC/ITC-HL, CCW armor, PVC jkt (IS blue) | 1 | TR-07 | M |  | 31 | 102 | 31 | 102 | [12 empty] | n/a | 201.0619 | Custody transfer; intrinsically safe | -7.25 | 3 | 2.2 | -17 | 12 | 0.5 | 3 | 0.88 | 1 | 16
60-IN-004 | 60 | Instrument | Gas chromatograph to flow computer (Modbus) | AT-GC | Gas chromatograph (shelter) | FC-GAS | Fiscal gas flow computer / metering panel (shelter) | INS-RS485 | 300 V 1 TSP #22 AWG 120 ohm RS-485, ITC-HL, CCW armor | 1 | LOCAL | M |  | 13 | 43 | 13 | 43 | [12 empty] | n/a | 113.0973 |  | -22 | 12 | 0.5 | -17 | 12 | 0.5 | 1 | 0.88 | 1 | 12
60-IN-005 | 60 | Instrument | Flow computer to gas station RIO (Modbus) | FC-GAS | Fiscal gas flow computer / metering panel (shelter) | RIO-GAS | DCS remote I/O cabinet - gas station (shelter) | INS-RS485 | 300 V 1 TSP #22 AWG 120 ohm RS-485, ITC-HL, CCW armor | 1 | LOCAL | M |  | 9 | 30 | 9 | 30 | [12 empty] | n/a | 113.0973 |  | -17 | 12 | 0.5 | -18 | 12 | 0.5 | 1 | 0.88 | 1 | 12
60-IN-006 | 60 | Instrument | Gas station JB (PT/TT/DPT) to RIO | JB-GAS | Gas station instrument junction box | RIO-GAS | DCS remote I/O cabinet - gas station (shelter) | INS-24TSP-18 | 300 V 24 TSP #18 AWG indiv. + overall shield, PLTC/ITC-HL, CCW armor | 1 | TR-07 | M |  | 25 | 82 | 25 | 82 | [12 empty] | n/a | 1134.1149 | Intrinsically safe | -10 | 8 | 0.5 | -18 | 12 | 0.5 | 3 | 0.88 | 1 | 38
60-IN-007 | 60 | Instrument | Pressure regulator position / PT to JB | PCV-101 | Pressure reducing / regulating valve skid | JB-GAS | Gas station instrument junction box | INS-1TSP-16 | 300 V 1 TSP #16 AWG, PLTC/ITC-HL, CCW armor, PVC jkt (IS blue) | 2 | TR-07 | M |  | 30 | 98 | 60 | 197 | [12 empty] | n/a | 265.4646 | Intrinsically safe | 1.5 | 1.5 | 2.5 | -10 | 8 | 0.5 | 3 | 0.88 | 1 | 13
60-IN-008 | 60 | Instrument | LNG tank gauging to RIO | LT-LNG | LNG tank level / temperature gauging head | RIO-GAS | DCS remote I/O cabinet - gas station (shelter) | INS-12TSP-18 | 300 V 12 TSP #18 AWG indiv. + overall shield, PLTC/ITC-HL, CCW armor | 1 | TR-07 | M |  | 98 | 322 | 98 | 322 | [12 empty] | n/a | 706.8583 |  | -60 | -6 | 24 | -18 | 12 | 0.5 | 3 | 0.88 | 1 | 30
60-IN-009 | 60 | Instrument | LNG area JB to RIO | JB-LNG | LNG area instrument junction box | RIO-GAS | DCS remote I/O cabinet - gas station (shelter) | INS-24TSP-18 | 300 V 24 TSP #18 AWG indiv. + overall shield, PLTC/ITC-HL, CCW armor | 1 | TR-07 | M |  | 45 | 148 | 45 | 148 | [12 empty] | n/a | 1134.1149 | Intrinsically safe | -44 | 8 | 0.5 | -18 | 12 | 0.5 | 3 | 0.88 | 1 | 38
20-IN-001 | 20 | Instrument | GT exhaust thermocouples to GT control | JB-GT-TC | GT exhaust thermocouple junction box | GTCP | GT control panel (in PEECC) | INS-TC-12P-KX | 300 V 12 pair #16 AWG type KX thermocouple extension, ITC-HL, CCW armor | 2 | TR-01 | M |  | 50 | 164 | 100 | 328 | [12 empty] | n/a | 1413.7167 |  | 72 | 2 | 6 | 46 | -6 | 0.5 | 5 | 0.88 | 1 | 30
20-IN-002 | 20 | Instrument | HRSG drum JB to power block RIO | JB-HRSG-01 | HRSG drum platform instrument junction box | RIO-PB | DCS remote I/O cabinet - power block | INS-24TSP-18 | 300 V 24 TSP #18 AWG indiv. + overall shield, PLTC/ITC-HL, CCW armor | 2 | TR-01 | M |  | 102 | 335 | 204 | 669 | [12 empty] | n/a | 2268.2299 |  | 97 | -6 | 30 | 68 | 22 | 0.5 | 5 | 0.88 | 1 | 38
20-IN-003 | 20 | Instrument | CEMS probe to analyser shelter | AE-STK | CEMS probe at stack sample port | CEMS-SH | CEMS analyser shelter | INS-2TSP-16 | 300 V 2 TSP #16 AWG, PLTC/ITC-HL, CCW armor, PVC jkt (IS blue) | 1 | LOCAL | M |  | 64 | 210 | 64 | 210 | [12 empty] | n/a | 201.0619 | Heated sample line by vendor | 117 | -0.5 | 40 | 122 | -8 | 0.5 | 1 | 0.88 | 1 | 16
30-IN-001 | 30 | Instrument | ACC JB to power block RIO | JB-ACC | ACC instrument junction box | RIO-PB | DCS remote I/O cabinet - power block | INS-24TSP-18 | 300 V 24 TSP #18 AWG indiv. + overall shield, PLTC/ITC-HL, CCW armor | 1 | TR-02 | M |  | 107 | 351 | 107 | 351 | [12 empty] | n/a | 1134.1149 |  | 142 | 30 | 0.5 | 68 | 22 | 0.5 | 5 | 0.88 | 1 | 38
40-IN-001 | 40 | Instrument | Absorber JB to CCS RIO | JB-ABS-01 | Absorber instrument junction box (mid-height) | RIO-CCS | DCS remote I/O cabinet - CCS | INS-24TSP-18 | 300 V 24 TSP #18 AWG indiv. + overall shield, PLTC/ITC-HL, CCW armor | 2 | TR-05 | M |  | 110 | 361 | 220 | 722 | [12 empty] | n/a | 2268.2299 |  | 170 | -2.5 | 30 | 174 | 58 | 0.5 | 6 | 0.88 | 1 | 38
40-IN-002 | 40 | Instrument | Stripper JB to CCS RIO | JB-STR-01 | Stripper instrument junction box | RIO-CCS | DCS remote I/O cabinet - CCS | INS-24TSP-18 | 300 V 24 TSP #18 AWG indiv. + overall shield, PLTC/ITC-HL, CCW armor | 1 | TR-05 | M |  | 92 | 302 | 92 | 302 | [12 empty] | n/a | 1134.1149 |  | 190 | 15.5 | 20 | 174 | 58 | 0.5 | 6 | 0.88 | 1 | 38
40-IN-003 | 40 | Instrument | CO2 fiscal meter to CCS RIO (Modbus) | FC-CO2 | CO2 export fiscal meter skid / flow computer | RIO-CCS | DCS remote I/O cabinet - CCS | INS-RS485 | 300 V 1 TSP #22 AWG 120 ohm RS-485, ITC-HL, CCW armor | 1 | TR-05 | M |  | 114 | 374 | 114 | 374 | [12 empty] | n/a | 113.0973 |  | 242 | 39 | 1 | 174 | 58 | 0.5 | 6 | 0.88 | 1 | 12
70-FG-001 | 60 | Instrument | F&G loop: gas station / LNG detectors | FGP-1 | Fire & gas panel | JB-GAS | Gas station instrument junction box | INS-12TSP-18 | 300 V 12 TSP #18 AWG indiv. + overall shield, PLTC/ITC-HL, CCW armor | 1 | TR-03 | M |  | 123 | 404 | 123 | 404 | [12 empty] | n/a | 706.8583 | Circuit integrity (CI) rated | 39 | 55.5 | 0.5 | -10 | 8 | 0.5 | 5 | 0.88 | 1 | 30
70-FG-002 | 20 | Instrument | F&G loop: GT enclosure detectors | FGP-1 | Fire & gas panel | JB-FG-GT | F&G junction box - GT enclosure | INS-12TSP-18 | 300 V 12 TSP #18 AWG indiv. + overall shield, PLTC/ITC-HL, CCW armor | 1 | TR-01 | M |  | 103 | 338 | 103 | 338 | [12 empty] | n/a | 706.8583 | Circuit integrity (CI) rated | 39 | 55.5 | 0.5 | 60 | -3 | 1 | 5 | 0.88 | 1 | 30
70-FG-003 | 40 | Instrument | F&G loop: CCS area detectors | FGP-1 | Fire & gas panel | JB-FG-CCS | F&G junction box - CCS area | INS-12TSP-18 | 300 V 12 TSP #18 AWG indiv. + overall shield, PLTC/ITC-HL, CCW armor | 1 | TR-02 | M |  | 226 | 741 | 226 | 741 | [12 empty] | n/a | 706.8583 | Circuit integrity (CI) rated | 39 | 55.5 | 0.5 | 172 | -3 | 1 | 5 | 0.88 | 1 | 30
20-EG-001 | 20 | Earthing | Power block main ground grid (mesh) | EG-PB | Power block main earth grid (nearest riser) | EG-PB | Power block main earth grid (nearest riser) | EG-CU-4/0 | Bare stranded Cu 4/0 AWG ground grid conductor (buried) | 1 | EG | M | 1800 | 1800 | 5906 | 1800 | 5906 | [12 empty] | n/a | 138.9291 | Length estimate - confirm by IEEE 80 study | 75 | 20 | -0.8 | 75 | 20 | -0.8 | -0.8 |  | 1 | 13.3
10-EG-001 | 10 | Earthing | Switchyard ground grid (mesh) | EG-SWY | Switchyard earth grid (nearest riser) | EG-SWY | Switchyard earth grid (nearest riser) | EG-CU-4/0 | Bare stranded Cu 4/0 AWG ground grid conductor (buried) | 1 | EG | M | 2400 | 2400 | 7874 | 2400 | 7874 | [12 empty] | n/a | 138.9291 | Length estimate - confirm by IEEE 80 study | 50 | 137.5 | -0.8 | 50 | 137.5 | -0.8 | -0.8 |  | 1 | 13.3
40-EG-001 | 40 | Earthing | CCS area ground grid (mesh) | EG-CCS | CCS area earth grid (nearest riser) | EG-CCS | CCS area earth grid (nearest riser) | EG-CU-4/0 | Bare stranded Cu 4/0 AWG ground grid conductor (buried) | 1 | EG | M | 1200 | 1200 | 3937 | 1200 | 3937 | [12 empty] | n/a | 138.9291 | Length estimate | 190 | 25 | -0.8 | 190 | 25 | -0.8 | -0.8 |  | 1 | 13.3
60-EG-001 | 60 | Earthing | Gas / LNG area ground grid (mesh) | EG-GAS | Gas / LNG area earth grid (nearest riser) | EG-GAS | Gas / LNG area earth grid (nearest riser) | EG-CU-4/0 | Bare stranded Cu 4/0 AWG ground grid conductor (buried) | 1 | EG | M | 900 | 900 | 2953 | 900 | 2953 | [12 empty] | n/a | 138.9291 | Length estimate | -30 | 5 | -0.8 | -30 | 5 | -0.8 | -0.8 |  | 1 | 13.3
50-EG-001 | 50 | Earthing | RICE area ground grid (mesh) | EG-RICE | RICE area earth grid (nearest riser) | EG-RICE | RICE area earth grid (nearest riser) | EG-CU-4/0 | Bare stranded Cu 4/0 AWG ground grid conductor (buried) | 1 | EG | M | 600 | 600 | 1969 | 600 | 1969 | [12 empty] | n/a | 138.9291 | Length estimate | -4 | 85 | -0.8 | -4 | 85 | -0.8 | -0.8 |  | 1 | 13.3
10-EG-002 | 10 | Earthing | Interconnection power block grid - switchyard grid | EG-PB | Power block main earth grid (nearest riser) | EG-SWY | Switchyard earth grid (nearest riser) | EG-CU-4/0 | Bare stranded Cu 4/0 AWG ground grid conductor (buried) | 2 | EG | M |  | 163 | 535 | 326 | 1070 | [12 empty] | n/a | 277.8582 | Two diverse connections | 75 | 20 | -0.8 | 50 | 137.5 | -0.8 | -0.8 |  | 1 | 13.3
50-EG-002 | 50 | Earthing | Interconnection power block grid - RICE grid | EG-PB | Power block main earth grid (nearest riser) | EG-RICE | RICE area earth grid (nearest riser) | EG-CU-4/0 | Bare stranded Cu 4/0 AWG ground grid conductor (buried) | 2 | EG | M |  | 165 | 541 | 330 | 1083 | [12 empty] | n/a | 277.8582 |  | 75 | 20 | -0.8 | -4 | 85 | -0.8 | -0.8 |  | 1 | 13.3
40-EG-002 | 40 | Earthing | Interconnection power block grid - CCS grid | EG-PB | Power block main earth grid (nearest riser) | EG-CCS | CCS area earth grid (nearest riser) | EG-CU-4/0 | Bare stranded Cu 4/0 AWG ground grid conductor (buried) | 2 | EG | M |  | 138 | 453 | 276 | 906 | [12 empty] | n/a | 277.8582 |  | 75 | 20 | -0.8 | 190 | 25 | -0.8 | -0.8 |  | 1 | 13.3
60-EG-002 | 60 | Earthing | Interconnection power block grid - gas/LNG grid | EG-PB | Power block main earth grid (nearest riser) | EG-GAS | Gas / LNG area earth grid (nearest riser) | EG-CU-4/0 | Bare stranded Cu 4/0 AWG ground grid conductor (buried) | 2 | EG | M |  | 138 | 453 | 276 | 906 | [12 empty] | n/a | 277.8582 | Insulating joints on gas pipe - check cathodic protection | 75 | 20 | -0.8 | -30 | 5 | -0.8 | -0.8 |  | 1 | 13.3
20-EG-002 | 20 | Earthing | GSU-GT tank and neutral bonds | GSU-GT-LV | GT step-up transformer - LV bushings / marshalling box | EG-PB | Power block main earth grid (nearest riser) | EB-CU-2/0 | Green insulated Cu 2/0 AWG bonding jumper | 4 | EG | M | 15 | 15 | 49 | 60 | 197 | [12 empty] | n/a | 706.8583 |  | 54 | 60 | 4.5 | 75 | 20 | -0.8 | -0.8 |  | 1 | 15
20-EG-003 | 20 | Earthing | GSU-ST tank and neutral bonds | GSU-ST-LV | ST step-up transformer - LV bushings / marshalling box | EG-PB | Power block main earth grid (nearest riser) | EB-CU-2/0 | Green insulated Cu 2/0 AWG bonding jumper | 4 | EG | M | 15 | 15 | 49 | 60 | 197 | [12 empty] | n/a | 706.8583 |  | 74 | 60 | 4.5 | 75 | 20 | -0.8 | -0.8 |  | 1 | 15
20-EG-004 | 20 | Earthing | Stack lightning down conductors | STK | HRSG stack (lightning down conductor) | EG-PB | Power block main earth grid (nearest riser) | EG-CU-4/0 | Bare stranded Cu 4/0 AWG ground grid conductor (buried) | 2 | EG | M | 70 | 70 | 230 | 140 | 459 | [12 empty] | n/a | 277.8582 |  | 117 | 3 | 55 | 75 | 20 | -0.8 | -0.8 |  | 1 | 13.3
40-EG-003 | 40 | Earthing | Absorber column bonds | C-ABS | Absorber column shell (lightning / bonding) | EG-CCS | CCS area earth grid (nearest riser) | EB-CU-2/0 | Green insulated Cu 2/0 AWG bonding jumper | 2 | EG | M | 10 | 10 | 33 | 20 | 66 | [12 empty] | n/a | 353.4292 |  | 170 | 6 | 0 | 190 | 25 | -0.8 | -0.8 |  | 1 | 15
60-EG-003 | 60 | Earthing | LNG tank bonds | TK-LNG | LNG full-containment tank (bonding) | EG-GAS | Gas / LNG area earth grid (nearest riser) | EB-CU-2/0 | Green insulated Cu 2/0 AWG bonding jumper | 4 | EG | M | 20 | 20 | 66 | 80 | 262 | [12 empty] | n/a | 706.8583 |  | -60 | 10 | 0 | -30 | 5 | -0.8 | -0.8 |  | 1 | 15
Note on O2: M: (¦dX¦+¦dY¦+rises to raceway elevation) x (1+slack) + 2 x termination allowance. D: 3D span x (1+sag). Override (col N) wins if filled.
Note on W2: 3-ph: P/(sqrt3 x V x PFxEff). 1-ph / DC: P/(V x PFxEff). For kVA loads PF=1.
Note on X2: 1.25 motors (NEC 430.22) and continuous loads (NEC 210.19/215.2); 1.15 generators (NEC 445.13); 1.00 transformer secondaries / busway / OHL.
Note on AC2: mV/A/m x (running I / runs) x L / 1000 / V. mV/A/m from NEC Ch.9 Table 9 (AC, 0.85 PF) or Table 8 (DC loop).

## Raceways
Raceway ID | Description | Type | Elevation (m) | Width (mm) | Usable depth (mm) | Tiers | Max fill | Correction factor | Capacity (mm2) | Cable area used (mm2) | Fill (% of max) | Check
OHL | Overhead strung conductors (switchyard / line) | Overhead | [5 empty] | 1 |  | 28254.5968 |  | n/a
IPB-GT | Isolated phase bus route GT generator -> GSU / UAT-1 | Busduct | 4 |  |  |  |  | 1 |  | 0 |  | n/a
IPB-ST | Isolated phase bus route ST generator -> GSU / UAT-2 | Busduct | 4 |  |  |  |  | 1 |  | 0 |  | n/a
BD | LV busduct, transformer to switchboard (local) | Busduct | 3 |  |  |  |  | 1 |  | 0 |  | n/a
TR-01 | Ladder tray: main electrical bldg -> GT / HRSG (40,50 -> 40,20 -> 46,20) | Tray | 5 | 900 | 100 | 4 | 40% | 0.88 | 144000 | 45975.6377 | 31.93% | OK
TR-02 | Ladder tray: main electrical bldg -> ACC -> CCS (46,53 -> 140,53 -> 140,64 -> 180,64 -> 180,40) | Tray | 5 | 900 | 100 | 4 | 40% | 0.88 | 144000 | 43339.0561 | 30.1% | OK
TR-03 | Ladder tray: main electrical bldg -> gas station / LNG (40,50 -> -4,50 -> -4,14) | Tray | 5 | 900 | 100 | 3 | 40% | 0.88 | 108000 | 7734.6011 | 7.162% | OK
TR-04 | Ladder tray: RICE gensets -> collector e-house (4,70 -> 4,104 -> 12,104) | Tray | 3 | 1000 | 100 | 3 | 40% | 0.88 | 120000 | 36561.8553 | 30.47% | OK
TR-05 | Ladder tray: CCS internal (substation -> absorber / stripper / compressor) | Tray | 6 | 900 | 100 | 4 | 40% | 0.88 | 144000 | 44380.494 | 30.82% | OK
TR-06 | Ladder tray: ACC VFD room -> fan deck, 2 risers (east / west) x 600 mm, single layer for 500 kcmil (NEC 392.22) | Tray | 20 | 600 | 100 | 4 | 40% | 0.88 | 96000 | 57726.765 | 60.13% | OK
TR-07 | Ladder tray: gas station / LNG local | Tray | 3 | 600 | 100 | 3 | 40% | 0.88 | 72000 | 25723.3606 | 35.73% | OK
TR-08 | Concrete cable trench: switchyard bays -> relay building | Trench | -0.8 | 1000 | 600 | 1 | 40% | 0.88 | 240000 | 9160.8842 | 3.817% | OK
DB-01 | Duct bank: main electrical bldg / transformer yard -> switchyard relay bldg | Duct bank | -1.2 | 1200 | 600 | 1 | 30% | 0.7 | 216000 | 2994.7232 | 1.386% | OK
DB-02 | Duct bank: RICE e-house -> main electrical bldg | Duct bank | -1.2 | 900 | 600 | 1 | 30% | 0.7 | 162000 | 8488.5833 | 5.24% | OK
DB-03 | Duct bank: UAT-1 -> main 13.8 kV switchgear | Duct bank | -1.2 | 1200 | 600 | 1 | 30% | 0.7 | 216000 | 29094.2896 | 13.47% | OK
LOCAL | Local tray / conduit within a building or package | Local | 1 |  |  |  |  | 0.88 |  | 80126.3206 |  | n/a
EG | Buried earth grid / bonding | Buried | -0.8 | [6 empty] | 4557.9404 |  | n/a

## BOQ Summary
BILL OF QUANTITIES - CABLES, CONDUCTORS AND BUSWAY
Cable Type | Description | Category | No. of circuits | Schedule length (m) | Incl. wastage (m) | Incl. wastage (ft) | Reel length (m) | No. of reels | Mass (t)
ACSR-DRAKE | ACSR 795 kcmil 'Drake' 26/7, 1 per phase | HV Overhead | 3 | 546 | 574 | 1883 | 2000 | 1 | 0.93447
ACSR-DRAKE-2B | ACSR 795 kcmil 'Drake' 26/7, twin bundle per phase | HV Overhead | 6 | 1602 | 1683 | 5522 | 2000 | 1 | 2.7399
SW-7/16-EHS | Shield wire 7/16" EHS galvanized steel | HV Overhead | 1 | 124 | 131 | 430 | 3000 | 1 | 0.077945
OPGW-24 | OPGW 24-fiber shield wire | HV Overhead | 1 | 200 | 210 | 689 | 4000 | 1 | 0.1302
IPB-10K | Isolated phase bus 24 kV, 10 kA (per phase metre) | Busduct | 1 | 174 | 183 | 600 |  |  | 29.28
IPB-7K | Isolated phase bus 24 kV, 7 kA (per phase metre) | Busduct | 1 | 120 | 126 | 413 |  |  | 15.12
IPB-3K | Isolated phase tap bus 24 kV, 3 kA (per phase metre) | Busduct | 2 | 396 | 416 | 1365 |  |  | 29.12
LVBD-4000 | 600 V busway 4000 A, Cu, 3-ph + ground, outdoor feeder | Busduct | 3 | 66 | 70 | 230 |  |  | 3.15
LVBD-2500 | 600 V busway 2500 A, Cu, 3-ph + ground, outdoor feeder | Busduct | 2 | 49 | 52 | 171 |  |  | 1.56
MV-1C-2-NGR | 15 kV MV-105 1/C #2 AWG Cu EPR 133% shielded, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | MV Power | 2 | 30 | 32 | 105 | 300 | 1 | 0.0512
MV-3C-2 | 15 kV MV-105 3/C #2 AWG Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | MV Power | 19 | 1225 | 1287 | 4222 | 300 | 5 | 5.148
MV-3C-1/0 | 15 kV MV-105 3/C 1/0 AWG Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | MV Power | 3 | 180 | 189 | 620 | 300 | 1 | 1.0017
MV-3C-4/0 | 15 kV MV-105 3/C 4/0 AWG Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | MV Power | 2 | 281 | 296 | 971 | 300 | 1 | 2.368
MV-3C-500 | 15 kV MV-105 3/C 500 kcmil Cu EPR 133% shielded + GC, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | MV Power | 1 | 85 | 90 | 295 | 300 | 1 | 1.395
MV-1C-500-TPX | 15 kV MV-105 1/C 500 kcmil Cu EPR 133% shielded, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt, triplexed set | MV Power | 4 | 1743 | 1831 | 6007 | 300 | 7 | 8.0564
MV-1C-750-TPX | 15 kV MV-105 1/C 750 kcmil Cu EPR 133% shielded, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt, triplexed set | MV Power | 4 | 1605 | 1686 | 5531 | 300 | 6 | 10.4532
MV-1C-1000-TPX | 15 kV MV-105 1/C 1000 kcmil Cu EPR 133% shielded, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt, triplexed set | MV Power | 1 | 420 | 441 | 1447 | 300 | 2 | 3.4839
LV-3C-10 | 600 V 3/C #10 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | LV Power | 2 | 131 | 138 | 453 | 600 | 1 | 0.0828
LV-3C-6 | 600 V 3/C #6 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | LV Power | 1 | 168 | 177 | 581 | 600 | 1 | 0.16815
LV-3C-2 | 600 V 3/C #2 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | LV Power | 5 | 182 | 192 | 630 | 600 | 1 | 0.3456
LV-3C-1/0 | 600 V 3/C 1/0 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | LV Power | 11 | 455 | 478 | 1568 | 300 | 2 | 1.2428
LV-3C-4/0 | 600 V 3/C 4/0 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | LV Power | 2 | 172 | 181 | 594 | 300 | 1 | 0.8326
LV-3C-350 | 600 V 3/C 350 kcmil + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | LV Power | 3 | 497 | 522 | 1713 | 300 | 2 | 3.7584
LV-3C-500 | 600 V 3/C 500 kcmil + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | LV Power | 5 | 736 | 773 | 2536 | 300 | 3 | 7.5754
LV-VFD-500 | 600/1000 V VFD 3/C 500 kcmil + 3 symmetrical G, Cu XLPE, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | LV Power | 15 | 927 | 974 | 3196 | 300 | 4 | 10.714
LV-MFX-2/0 | 1000 V 3/C 2/0 AWG + 3 symmetrical G, flexible tinned Cu XHHW-2, foil + braid shield, TPE jkt, Type TC-ER, NFPA 79 (Machine Flex type) | LV Power | 15 | 180 | 189 | 620 | 300 | 1 | 0.4914
LV-2C-10 | 600 V 2/C #10 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | DC Power | 2 | 27 | 29 | 95 | 600 | 1 | 0.0145
LV-2C-6 | 600 V 2/C #6 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | DC Power | 1 | 80 | 84 | 276 | 600 | 1 | 0.0672
LV-2C-2 | 600 V 2/C #2 AWG + G Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | DC Power | 6 | 560 | 588 | 1929 | 600 | 1 | 0.8232
LV-1C-500 | 600 V 1/C 500 kcmil Cu XHHW-2, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt (+/- pair) | DC Power | 2 | 360 | 378 | 1240 | 300 | 2 | 1.2474
CTL-7C-12 | 600 V 7/C #12 AWG Cu XHHW-2 control, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | Control | 1 | 19 | 20 | 66 | 600 | 1 | 0.012
CTL-12C-14 | 600 V 12/C #14 AWG Cu XHHW-2 control, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | Control | 0 | 0 | 0 | 0 | 600 |  | 0
CTL-25C-14 | 600 V 25/C #14 AWG Cu XHHW-2 control, Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | Control | 18 | 1237 | 1299 | 4262 | 600 | 3 | 1.4289
CTL-12C-10 | 600 V 12/C #10 AWG Cu XHHW-2 control (CT circuits), Type MC-HL, CCW Al armor (Armor-X type), PVC jkt | Control | 11 | 1234 | 1296 | 4252 | 600 | 3 | 1.5552
INS-1TSP-16 | 300 V 1 TSP #16 AWG, PLTC/ITC-HL, CCW armor, PVC jkt (IS blue) | Instrument | 1 | 60 | 63 | 207 | 600 | 1 | 0.01575
INS-2TSP-16 | 300 V 2 TSP #16 AWG, PLTC/ITC-HL, CCW armor, PVC jkt (IS blue) | Instrument | 4 | 166 | 175 | 574 | 600 | 1 | 0.06125
INS-12TSP-18 | 300 V 12 TSP #18 AWG indiv. + overall shield, PLTC/ITC-HL, CCW armor | Instrument | 4 | 550 | 578 | 1896 | 600 | 1 | 0.5202
INS-24TSP-18 | 300 V 24 TSP #18 AWG indiv. + overall shield, PLTC/ITC-HL, CCW armor | Instrument | 6 | 693 | 728 | 2388 | 600 | 2 | 1.0192
INS-TC-12P-KX | 300 V 12 pair #16 AWG type KX thermocouple extension, ITC-HL, CCW armor | Instrument | 1 | 100 | 105 | 344 | 600 | 1 | 0.084
INS-RS485 | 300 V 1 TSP #22 AWG 120 ohm RS-485, ITC-HL, CCW armor | Instrument | 3 | 136 | 143 | 469 | 600 | 1 | 0.0286
FO-24SM | 24-fiber single-mode OFCR, interlocked Al armor | Fibre Optic | 9 | 1642 | 1725 | 5659 | 2000 | 1 | 0.5175
FO-48SM | 48-fiber single-mode OFCR, interlocked Al armor | Fibre Optic | 2 | 636 | 668 | 2192 | 2000 | 1 | 0.24048
EG-CU-4/0 | Bare stranded Cu 4/0 AWG ground grid conductor (buried) | Earthing | 10 | 8248 | 8661 | 28415 | 300 | 29 | 8.4012
EB-CU-2/0 | Green insulated Cu 2/0 AWG bonding jumper | Earthing | 4 | 220 | 231 | 758 | 300 | 1 | 0.14322
TOTAL |  |  | 200 | [5 empty] | 155.4609
IPB lengths are per phase metre (3 per run); LV busway per metre; OHL lengths are conductor metres; triplexed MV sets count each 1/C cable.
SUMMARY BY SYSTEM
System | No. of circuits | Conductor length (m) | Conductor length (ft) | Circuits OK | Circuits CHECK | Max loading | Max volt drop
HV Overhead | 11 | 2472 | 8110 | 9 | 0 | 80.88%
Busduct | 9 | 805 | 2641 | 9 | 0 | 90.21%
MV Power | 36 | 5569 | 18271 | 34 | 0 | 92.31% | 0.1389%
LV Power | 60 | 3458 | 11345 | 60 | 0 | 93.39% | 2.679%
DC Power | 10 | 1017 | 3337 | 10 | 0 | 64.94% | 2.413%
Control | 30 | 2490 | 8169 | 0 | 0
Instrument | 19 | 1705 | 5594 | 0 | 0
Fibre Optic | 11 | 2278 | 7474 | 0 | 0
Earthing | 14 | 8468 | 27782 | 0 | 0
TOTAL | 200 |  |  | 122 | 0

## References
PUBLIC REFERENCE DOCUMENTS
These public documents were identified as references for typical plant arrangements. They were NOT opened or transcribed for this schedule: equipment positions come from the 3D model and ratings are representative values. Cable product pages are cited as examples of the MC-HL / CCW armor construction; sizes, ODs and masses in 'Cable Types' are typical values - confirm against the selected manufacturer's data sheets. Replace with project data before use.
Topic | Document | URL
CCPP + LNG + gas metering | Shannon Technology & Energy Park power plant - list of planning drawings (incl. gas metering / regulating enclosures) | https://www.pleanala.ie/publicaccess/EIAR-NIS/319566/Shannon%20Technology%20and%20Energy%20Park%20(STEP)%20Power%20Plant/02_Planning%20Drawings/SLNG_PP_List%20of%20Planning_Drawings.pdf
CCPP layout | Shannon - Combined Cycle Power Plant general arrangement | https://www.pleanala.ie/publicaccess/EIAR-NIS/311233/Drawings/Structures/198291-1GSU-G2001.pdf
CCPP layout | Tees CCPP - indicative generating station sheet 1 | https://infrastructure.planninginspectorate.gov.uk/wp-content/ipc/uploads/projects/EN010082/EN010082-000370-4.5%20-%20Tees%20CCPP%20-%20Indicative%20Generating%20Station%20Sheet%201%20-%20Rev%202.pdf
CCPP layout | ESC Brooke County CCGT air permit application (conceptual layout, App. A) | https://dep.wv.gov/daq/Documents/December%202016%20Applications/033-00264_APPL_R14-0036.pdf
CCS | Bechtel / Panda Sherman NGCC carbon capture FEED final report (OSTI) | https://www.osti.gov/servlets/purl/1836563
CCS | NETL - EPRI CalCapture (Elk Hills) NGCC CCS FEED | https://netl.doe.gov/sites/default/files/netl-file/21CMOG_CCUS_Bhown.pdf
CCS | NETL - Calpine Deer Park CCS FEED | https://netl.doe.gov/sites/default/files/netl-file/23CM_PSCC28_Herman.pdf
Gas metering | Adams County CO - regulator station site plan submittal | https://adcogov.org/sites/default/files/2024-05/RCU2024-00010-submittal1.pdf
RICE | KYMEA Energy Center (4 x Wartsila 18V50SG) - KY PSC case 2024-00290 | https://psc.ky.gov/pscecf/2024-00290/tosterloh@sturgillturner.com/10042024124833/07_Attachment_E_-_Public_Meeting_Information.pdf
RICE | We Energies Paris RICE generation project | https://www.we-energies.com/company/paris-generation-project
Switchyard / SLD | PJM facilities study - 1,100 MW combined cycle interconnection (one-lines) | https://www.pjm.com/pjmfiles/pub/planning/project-queues/facilities/b03_fac.pdf
Cable product | Southwire SPEC 45352 - 600 V XLPE XHHW-2 Armor-X (MC-HL) power cable with ground | https://cabletechsupport.southwire.com/tile/26/spec/45352/?country=US
Cable product | Southwire SPEC 45227 - 600 V XLPE XHHW-2 Armor-X (MC-HL) control cable with ground | https://www.southwire.com/wire-cable/armored-power-cable/cu-600v-xlpe-xhhw-2-armor-x-pvc-control-cable-with-ground/p/55061899
Cable product | Southwire SPEC 45302 - 600/1000 V Armor-X VFD cable | https://www.southwire.com/wire-cable/armored-power-cable/cu-600-1000v-xlpe-insulation-armor-x-sup-sup-thermoplastic-lszh-tp-jacket-xhhw-2-vfd-cable-ct-rated-sunlight-resistant-for-direct-burial-silicone-free/p/67267399
Cable product | Southwire SPEC 45443 - Machine Flex TC-ER 1000 V flexible VFD cable, 3 symmetrical grounds | https://cabletechsupport.southwire.com/tile/1/spec/45443/?country=US
Cable product | Southwire SPEC 45442 - reduced diameter flexible VFD cable, Type TC-ER | https://www.southwire.com/wire-cable/power-control/cu-600v-xlpe-insulation-shielded-tpe-jacket-xhhw-2-reduced-diameter-flexible-variable-frequency-drive-vfd-/p/SPEC45442
Switchyard / SLD | SPP GEN-2008-006 facility study - 2-on-1 CCGT, 138 kV one-lines | https://opsportal.spp.org/documents/studies/files/2008_Generation_Studies/GEN-2008-006FS.pdf